## Slide 1
Combined Cycle Plant Survey Response Summary
Operations Analysis
November 17, 2020

## Slide 2: Introduction
At approximately 6:02am on March 16, 2020, around 584.5 MW of load tripped causing ERCOT's frequency to reach as high as 60.109 Hz
During the PDCWG discussion of this event, it was brought to ERCOT’s attention that some Combined Cycle Plants (CCP) transition into Temperature Control Mode when near their HSL and have limitations in their ability to provide PFR to high frequency events
A survey was sent out CCP owners to understand the design capabilities of these resources during various operating conditions
  42 RFIs sent out for 68 CCPs
  Currently missing responses for two CCPs

## Slide 3: Operating Conditions
Operating Conditions Set 1
  The Power Augmentation (PA) technology is not active and Gas Turbines (GT) are operating at maximum capability
  The PA technology is actively augmenting output (NFRC is non-zero) and Gas Turbines (GT) are operating somewhere in the middle of their operating capability
  The PA technology is actively augmenting output (NFRC is zero or close to zero) and Gas Turbines (GT) are operating at maximum capability
Operating Conditions Set 2
  Gas Turbines (GT) are operating somewhere in the middle of their operating capability
  Gas Turbines (GT) are operating at maximum capability

## Slide 4: Operating Conditions Set 1
Resources have Power Augmentation Technologies

## Slide 5: Will the Resource transition into an Operating Mode other than Droop/MW/Speed Control?
Power Augmentation Control Mode
  PA Technology that increases firing temperature
Chart: 
| N/A | No | Base Load Control Mode | Exhaust Temperature Control Mode | Power Augmentation Control Mode | Temperature Control Mode
Count | 2 | 17 | 4 | 4 | 4 | 33

## Slide 6: Any Limitations or Delays of PFR to High Frequency Events?
Of the 8 captured in the dynamic model, all transitioned into Temperature Control mode
Of the 21 not captured in the dynamic model, 2 transitioned into an Exhaust Temperature Control Mode and 19 to Temperature Control mode
Chart: 
| N/A | No | Captured In ERCOT Dynamic Model | Not Captured in Dynamic Model
Count | 2 | 33 | 8 | 21

## Slide 7: Will the Resource transition into an Operating Mode other than Droop/MW/Speed Control?
27 of the 64 resources are not designed to operate in this condition
Reserve Capacity Mode
  Resource will stay in MW control during high frequency events
Chart: 
| N/A | No | Not Applicable | Reserve Capacity Mode (GT) | Power Augmentation Control Mode (GT) | Temperature Control Mode (GT)
Count | 2 | 25 | 27 | 2 | 4 | 4
Notes: CCPs generally identified that Power Augmentation is used after GTs are operating at max power output.
When in Reserve Capacity Mode, the resource will generally be in MW control but may transition to Exhaust control mode if the low frequency event is large enough

## Slide 8: Any Limitations or Delays of PFR to High Frequency Events?
Two resources identified that their dynamic models includes the control loop for when the resource enters and exits Temperature Control Mode (i.e. the reason for why limitations exist)
Chart: 
| N/A | No | Not Applicable | Yes & Captured in Dynamic Model
Count | 2 | 33 | 27 | 2

## Slide 9: Will the Resource transition into an Operating Mode other than Droop/MW/Speed Control?
Operating modes entered will mostly be independent of whether the resource has PA Technology enabled or disabled
Chart: 
| N/A | No | Base Load Control Mode | Exhaust Temperature Control Mode | Power Augmentation Control Mode | Temperature Control Mode
Count | 2 | 17 | 4 | 4 | 4 | 34
Notes: One new resource identified as entering Temperature Control Mode when it enables wet compression

## Slide 10: Any Limitations or Delays of PFR to High Frequency Events?
Limitations in PFR to High Frequency events will be seen for resources that need to disable PA Technology before changing control mode
8 Resource Captured Limitations in Model
  All 8 enter Temperature Control Mode
26 Resources do not capture limitations in model
  21 enter Temperature Control Mode, 2 enter Exhaust Temperature Control Mode, and 2 will be limited if response pushes resource below 90% of HSL
Chart: 
| N/A | No | Captured in Dynamic Model | Not Captured in Dynamic Model
Count | 2 | 27 | 8 | 26

## Slide 11: Operating Conditions Set 2
Resources do not have Power Augmentation Technologies

## Slide 12: Operating Condition: GTs Operating Somewhere in the Middle of Range
Chart: 
| N/A | No
Count | 2 | 5
One resource identified it would enable Outlet Temperature Correction (OTC) once the generator breaker is closed
  OTC monitors difference between actual exhaust temperature and exhaust temperature limit
Chart: 
| N/A | No | Yes
 | 2 | 4 | 1
Notes:   OTC monitors difference between actual exhaust temperature and exhaust temperature limit and a difference of 0 would enable temperature control mode

## Slide 13: GTs Operating at Maximum Capability
Resources did not identify any impact to PFR to high frequency events
Chart: 
| N/A | Not Applicable | Outlet Temperature Control Mode | Exhaust Temperature Control Mode
Count | 2 | 2 | 1 | 2
Chart: 
| Not Applicable | No | N/A
Count | 1 | 4 | 2

## Slide 14: Notable Feedback/Comments

## Slide 15: Feedback and Comments
“A limit to the load reduction should be considered to prevent frequency swings.”
“Combined Cycle Units should not be scored for high frequency events when they are within 2% of their temperature limit (HSL-NFRC)”
“…power augmentation through wet compression is only available when the ambient temperature is above 65F, the GT is at base-load, and requires 45 minutes notice to start the skid. Wet compression is typically run during peak summer demand periods.”
“…the amount of load drop required for the response may drop load enough to turn off systems such as the duct burners or wet compression. If wet compression turns off, the unit would experience a runback to reduce load to avoid over-firing of the unit which may reduce load more than required for the frequency event.”

## Slide 16: Questions?