## Slide 1
ERCOT Frequency Control Report
October 2020
ERCOT
Operations Planning
PDCWG | November 17th, 2020

## Slide 2: Summary of October 2020
CPS1: 170.56%
Current CPS1 12-Month Rolling Average: 171.95%
5 BAAL Exceedances
5 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2019 BAAL-003 FRM Performance: -811.14
2020 RMS1 Statistics
  Mean: 16.07 mHz
  Min: 12.25 mHz
  Max: 22.6 mHz
Energy Statistics
  Total Energy: 31,210,036 MWh
  Wind Energy: 7,264,919 MWh
  Percent Energy from Wind: 23.28%
  Solar Energy: 682,932 MWh
  Percent Energy from Solar: 2.19%
Minimum System Inertia
  Mean: 189,099 MW*s
  Max: 242,576 MW*s on Oct 10th
  Min: 147,889 MW*s on Oct 26th
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Oct-20 CPS1 (%): 170.56
Notes: Outliers:
1. 66.87% @ 10/10/2020 16:00
  Unit Trip:
  Loss of approximately 694 MW of generation @16:45.
  1150 MW of RRS deployed.
97.11% @ 10/22/2020 22:00
  Expected Gen Dev:
  Expected gen dev remains negative for a third of the hour.
  Large exp. Gen. dev of -1910 @ 22:22 mostly due to thermal units.
  Several large units deviating due to configuration changes.
  Wind/Solar Ramp: Wind and solar are fairly steady.
  Regulation: Regulation up exhausted during the period of negative expected gen. dev.
  Manual SCED Rest: A manual SCED reset at 22:17 due to frequency drag and reg up fully deployed.
86.36% @ 10/29/2020 17:00
  Unit Trip:
  Loss of approximately 130 MW of generation @17:17.
  Expected Gen Dev: Expected gen dev is negative for most of the hour.
  Large exp. Gen. dev of -1283 MW @ 17:25 mostly due to thermal units runback.
  Wind/Solar Ramp:
  Solar consistently ramps down throughout the hour from 3016 MW to 1572 MW.
  Wind consistently ramps down throughout the hour from 7538 MW to 6270 MW.
  Manual SCED Rest: Multiple manual SCED resets due to unit trip, runback and consistent wind/solar down ramps.
4. 75.66% @ 10/30/2020 17:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1390 MW @ 17:52 mostly due to solar and thermal units
  Wind/Solar Ramp:
  A 616MW Solar down-ramp within a 15 minute period at the end of the hour.
  Regulation: Regulation up exhausted for over half of the hour
  Manual SCED Rest: A manual SCED reset at 17:50 due to solar down ramp and reg up fully deployed.
5. 98.72% @ 10/31/2020 15:00
  Expected Gen Dev:
  Large exp. Gen. dev of -916 MW @ 15:29 mostly due to thermal and a few solar units
  A thermal unit running back to off from 580MW and all reg up deployed.
  Wind/Solar Ramp:
  A 337 MW Solar down-ramp within a 10 minute period @ 15:26.
  Manual SCED Rest: A manual SCED reset at 15:27 due to a thermal unit runback and reg up fully deployed.

## Slide 5: BAAL Exceedances & Violations
There was 5 BAAL exceedances in Oct

## Slide 6: 15-Minute Average CPS1%
Oct-20 CPS1 (%): 170.56

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 171.95%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.07 mHz
  Min: 12.25 mHz
  Max: 22.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2019 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 31,210,036 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,264,919 MWh

## Slide 23: % Energy from Wind Generation
Notes: 23.28%

## Slide 24: Total Energy From Solar Generation
Notes: 682,932 MWh

## Slide 25: % Energy from Solar Generation
Notes: 2.19%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 147,889 MW*s on 9/27/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 189,099
Max: 242,576 on Oct 10th
Min: 147,889 on Oct 26th

## Slide 28: Questions?
Thank you!