## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
December 3rd, 2020

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs & IMFR
    2 FMEs in the month of October
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 11/17/2020
  ERCOT Summary of RFI – combined cycle unit frequency response for high frequency events
  NPRR 1040 – Compliance Metrics for Ancillary Service Supply Responsibility
  Request Indefinite Deferral/Tabling: OBDRR25 - Procedure for Calculating RRS Limits for Units (OBD), capture concepts for limits on Energy Storage Resources
  ERCOT Reports and FME Discussion

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs in October
  10/13/2020 17:13:40
    Loss of 473 MW
    Interconnection Frequency Response: 1006 MW/0.1 Hz
    9 of 40 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 40 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  10/19/2020 14:30:46
    Loss of 628 MW
    Interconnection Frequency Response: 961 MW/0.1 Hz
    7 of 40 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 40 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1106.25 MW/0.1Hz
Frequency Response Obligation (FRO): 425 MW/0.1 Hz

## Slide 7: Frequency Control Report
October 2020

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy
Notes: 32,735,862 MWh

## Slide 13: ERCOT Total Energy from Wind Generation
Notes: 5,026,960 MWh

## Slide 14: ERCOT % Energy from Wind Generation
Notes: 15.36%

## Slide 15: ERCOT Total Energy from Solar Generation
Notes: 782,376 MWh

## Slide 16: ERCOT % Energy from Solar Generation
Notes: 2.39%

## Slide 17
Questions?