## Slide 1
Intra-Hour Wind Forecast Accuracy Updates
(November 2020)
WMWG
Operations Analysis
Dec. 7, 2020

## Slide 2: Current GTBD Parameters
GTBD Component Tuning events:
  No tuning events this month
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 – 10:00 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 – 1:15 PM – Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – 1:10 PM – K5 changed from 0.4 to 0.5, Max Integral ACE feedback changed from 160 to 200, PWRR Threshold changed from 25 to 30
6/17/20 – 10 AM - PWRR Calculation method changed from Direct to Interpolated
9/1/20 – 11 AM - Max Integral ACE Feedback changed from 200 to 250
9/3/20 – 3 PM - Max Integral ACE Feedback changed from 250 to 300
9/4/20 – 3 PM - Max Integral ACE Feedback changed from 300 to 250

## Slide 3: Projected Wind Ramp Rate (PWRR) Error
Performance Metric | SCED PWRR (11/1 – 11/31) | Persistence Ramp* (11/1 – 11/31)
Monthly MAE (MW) | 66 | 90
Monthly MAE when 5-Min. Wind Ramp > 100 MW | 100 | 175
* Persistence Ramp assumes using a 0 MW wind ramp in PWRR