## Slide 1
2021 Long-Term Load Forecast
Calvin Opheim
Load Forecasting & Analysis
SAWG
December 18, 2020

## Slide 2: Agenda
Data Used in Model Development
Growth Driver
Creating Weather Zone Load Forecasts
Creating the ERCOT System Load Forecast
ERCOT System Load Forecast

## Slide 3: Agenda - continued
Rooftop PV Forecast
Forecast Adjustments
Assumptions and Challenges
Weather Zone Forecast Summary
Questions

## Slide 4
Data Used in Model Development

## Slide 5: Weather Zones
2 or 3 Weather Stations in each Weather Zone

## Slide 6: Load Models
Unique Model for
  Each Weather Zone
    Each Temperature Group
      Hot
      Medium
      Cold

## Slide 7: Input Data
Hourly Models
From January 2015 through August 2020
  Recent Snapshot
    Appliance Stock
    Energy Efficiency
    Demand Response
    Price Responsive Load

## Slide 8: Input Data
Weather
  Temperature, Temperature Squared, and Temperature Cubed
  Cooling Degree Days and Heating Degree Days
  Cloud Cover
  Wind Speed
  Dew Point

## Slide 9: Input Data
Calendar
  Month
  Day of the Week
  Holidays
  Hour
  Interact Hour with Day of the Week

## Slide 10: Input Data
Variable Interactions
  Interact a Weather Variable with a Calendar Variable
    Temperature with Hour
    Dew Point with Hour
  Interact multiple Weather Variables with a Calendar Variable
    Temperature with Dew Point and Hour

## Slide 11
Growth Driver

## Slide 12: Premise Forecast
Unique Model for
  Each Weather Zone
    Each Premise Class
      Residential
      Commercial
      Industrial
Monthly Models

## Slide 13: Input Data
From January 2015 through August 2020
Economic Measures
  Population
  Non-Farm Employment
  Housing Stock
  Error Correction Term

## Slide 14: Challenges
Chart: Far West Historical Premise Counts
Premise Counts increased significantly via opt-in

## Slide 15: Challenges
Chart: West Historical Premise Counts
Premise Counts increased significantly via opt-in

## Slide 16: Growth Driver for Far West and West
Economic Measures from Moody’s Base Scenario
  Population
  Non-Farm Employment
  Housing Stock

## Slide 17
Creating Weather Zone Load Forecasts

## Slide 18: Example - Coast
Coast 2021 Gross Summer Peak Forecasts Based on Historical Weather Years
Sort from high to low
Year | Month | Day | Hour | Forecast (MW) | Rank
2021 | 8 | 14 | 17 | 21,157 | 1
2021 | 8 | 8 | 16 | 20,532 | 2
2021 | 8 | 8 | 17 | 20,431 | 3
2021 | 8 | 14 | 16 | 20,411 | 4
2021 | 8 | 13 | 17 | 20,401 | 5

## Slide 19: Example - Coast
Year | Month | Day | Hour | Forecast (MW) | Rank
2021 | 8 | 14 | 17 | 21,157 | 1
2021 | 8 | 8 | 16 | 20,532 | 2
2021 | 8 | 8 | 17 | 20,431 | 3
2021 | 8 | 14 | 16 | 20,411 | 4
2021 | 8 | 13 | 17 | 20,401 | 5
Sort from high to low
Rank | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
1 | 21,157 | 21,103 | 21,600 | 21,091 | 21,968 | 21,539 | 22,344 | 22,793 | 21,628 | 21,167 | 22,157 | 21,745 | 21,049 | 21,289 | 22,044
2 | 20,532 | 20,936 | 21,472 | 20,728 | 21,374 | 21,425 | 22,312 | 21,321 | 21,281 | 21,131 | 22,091 | 21,452 | 21,029 | 21,231 | 21,973
3 | 20,431 | 20,864 | 21,426 | 20,716 | 21,311 | 21,258 | 22,287 | 21,261 | 21,251 | 21,089 | 21,659 | 21,391 | 20,847 | 21,151 | 21,922
4 | 20,411 | 20,583 | 21,374 | 20,627 | 21,254 | 21,257 | 22,170 | 21,197 | 21,213 | 20,993 | 21,615 | 21,367 | 20,810 | 21,105 | 21,909
5 | 20,401 | 20,546 | 21,316 | 20,617 | 21,199 | 21,204 | 22,119 | 21,169 | 21,202 | 20,990 | 21,570 | 21,301 | 20,807 | 21,072 | 21,892
Coast 2021 Gross Summer Peak Forecasts Based on Historical Weather Years

## Slide 20: Example - Coast
Chart: Coast 2021 Gross Summer Peak Forecasts
| 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
 | 21156.859 | 21103.2311 | 21599.5646 | 21091.0795 | 21968.4196 | 21538.7117 | 22344.0941 | 22792.6537 | 21628.4006 | 21167.3344 | 22156.8108 | 21744.8692 | 21049.4984 | 21289.064 | 22044.4537

## Slide 21: Example - Coast
Coast 2021 Gross Summer Forecasts Based on Historical Weather Years
Rank | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | Average
1 | 21,157 | 21,103 | 21,600 | 21,091 | 21,968 | 21,539 | 22,344 | 22,793 | 21,628 | 21,167 | 22,157 | 21,745 | 21,049 | 21,289 | 22,044 | 21,645
2 | 20,532 | 20,936 | 21,472 | 20,728 | 21,374 | 21,425 | 22,312 | 21,321 | 21,281 | 21,131 | 22,091 | 21,452 | 21,029 | 21,231 | 21,973 | 21,353
3 | 20,431 | 20,864 | 21,426 | 20,716 | 21,311 | 21,258 | 22,287 | 21,261 | 21,251 | 21,089 | 21,659 | 21,391 | 20,847 | 21,151 | 21,922 | 21,258
4 | 20,411 | 20,583 | 21,374 | 20,627 | 21,254 | 21,257 | 22,170 | 21,197 | 21,213 | 20,993 | 21,615 | 21,367 | 20,810 | 21,105 | 21,909 | 21,192
5 | 20,401 | 20,546 | 21,316 | 20,617 | 21,199 | 21,204 | 22,119 | 21,169 | 21,202 | 20,990 | 21,570 | 21,301 | 20,807 | 21,072 | 21,892 | 21,160

## Slide 22: Example - Coast
Chart: Coast 2021 Gross Summer Peak Forecasts
| 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | Highest | Lowest | Average
 | 21156.859 | 21103.2311 | 21599.5646 | 21091.0795 | 21968.4196 | 21538.7117 | 22344.0941 | 22792.6537 | 21628.4006 | 21167.3344 | 22156.8108 | 21744.8692 | 21049.4984 | 21289.064 | 22044.4537 | 22792.6537 | 21049.4984 | 21645.003

## Slide 23: Creating Weather Zone Load Forecasts
Summary
For every weather zone
For every forecasted year (2021-2030)
Forecasted values are ranked from high to low for each month
The average is calculated for each rank
This is the gross normal weather load forecast
Does not include impacts of the rooftop PV forecast

## Slide 24
Creating the ERCOT System Load Forecast

## Slide 25: Creating the ERCOT System Forecast - Example
Coast 2008 Summer Actual Load
For every weather zone, retrieve the actual load values from calendar year 2008
Sort the values from high to low
Sort from high to low
Historical Year | Month | Day | Hour | Rank | Coast Actual Load (MW)
2008 | 8 | 1 | 17 | 1 | 17,623
2008 | 8 | 1 | 16 | 2 | 17,478
2008 | 8 | 1 | 18 | 3 | 17,463
2008 | 8 | 8 | 17 | 4 | 17,222
2008 | 8 | 8 | 18 | 5 | 17,184

## Slide 26: Creating the ERCOT System Forecast - Example
Coast 2021 Gross Forecast Based on 2008 Calendar
Assign the average forecast values by rank (from slide 22) to the same rank based on the actual load from 2008
Month | Day | Hour | Rank | Coast 2021 Gross Forecast (MW)
8 | 1 | 17 | 1 | 21,645
8 | 1 | 16 | 2 | 21,353
8 | 1 | 18 | 3 | 21,258
8 | 8 | 17 | 4 | 21,192
8 | 8 | 18 | 5 | 21,160

## Slide 27: Creating the ERCOT System Forecast - Example
Month | Day | Hour | Rank | Coast 2021 Gross Forecast (MW)
8 | 1 | 17 | 1 | 21,645
8 | 1 | 16 | 2 | 21,353
8 | 1 | 18 | 3 | 21,258
8 | 8 | 17 | 4 | 21,192
8 | 8 | 18 | 5 | 21,160
Forecast Year | Month | Day | Hour | Coast | East | Fwest | Ncent | North | Scent | South | West
2021 | 8 | 4 | 17 | 20,880 | 2,726 | 4,850 | 26,055 | 1,898 | 12,957 | 5,808 | 2,069
2021 | 8 | 1 | 17 | 21,645 | 2,811 | 4,818 | 25,263 | 1,850 | 12,202 | 5,756 | 1,896
2021 | 8 | 4 | 18 | 20,628 | 2,751 | 4,835 | 25,630 | 1,867 | 12,688 | 5,698 | 2,003
2021 | 8 | 4 | 16 | 20,792 | 2,742 | 4,804 | 25,568 | 1,860 | 12,527 | 5,773 | 1,998
2021 | 8 | 7 | 17 | 21,064 | 2,734 | 4,736 | 25,151 | 1,800 | 12,407 | 5,938 | 1,944

## Slide 28: Creating the ERCOT System Forecast - Example
Forecast Year | Month | Day | Hour | Coast | East | Fwest | Ncent | North | Scent | South | West | ERCOT
2021 | 8 | 4 | 17 | 20,880 | 2,726 | 4,850 | 26,055 | 1,898 | 12,957 | 5,808 | 2,069 | 77,244
2021 | 8 | 1 | 17 | 21,645 | 2,811 | 4,818 | 25,263 | 1,850 | 12,202 | 5,756 | 1,896 | 76,242
2021 | 8 | 4 | 18 | 20,628 | 2,751 | 4,835 | 25,630 | 1,867 | 12,688 | 5,698 | 2,003 | 76,101
2021 | 8 | 4 | 16 | 20,792 | 2,742 | 4,804 | 25,568 | 1,860 | 12,527 | 5,773 | 1,998 | 76,066
2021 | 8 | 7 | 17 | 21,064 | 2,734 | 4,736 | 25,151 | 1,800 | 12,407 | 5,938 | 1,944 | 75,772
ERCOT Gross Forecast (MW) Based on 2008 Calendar
Month | Day | Hour | Rank | Coast 2021 Gross Forecast (MW)
8 | 1 | 17 | 1 | 21,645
8 | 1 | 16 | 2 | 21,353
8 | 1 | 18 | 3 | 21,258
8 | 8 | 17 | 4 | 21,192
8 | 8 | 18 | 5 | 21,160

## Slide 29: ERCOT Forecast
Summary
Forecasts for each Weather Zone are mapped into a Historical Calendar by Rank
2008 Historical Calendar was selected
  Evaluated 2007 through 2018
  2008 had the least amount of diversity between Weather Zone peaks and ERCOT peak

## Slide 30: Historical Coincident Factors Scenario Forecasts
Chart: ERCOT Gross Summer Peak Forecasts
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2008 Coincident Factors | 77243.6379 | 78855.2515 | 80280.2923 | 81266.818 | 82057.6381 | 82838.0592 | 83615.9218 | 84361.6918 | 85094.6733 | 85820.1422
Average Coincident Factors | 76439.7685 | 78053.371 | 79480.1144 | 80467.673 | 81259.1399 | 82039.1634 | 82815.1477 | 83561.2641 | 84294.8864 | 85020.6819
Minimum Coincident Factors | 75248.5873 | 76863.9742 | 78292.5508 | 79282.3239 | 80075.2899 | 80855.1039 | 81631.6783 | 82378.0142 | 83110.9968 | 83837.11

## Slide 31
ERCOT System Load Forecast

## Slide 32: ERCOT Gross Summer Peak Demand Forecast
Chart: Year
| 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 56068.0162 | 60029.6626 | 58483.7006 | 60212.6796 | 62202.8028 | 62114.7508 | 62102.9637 | 63407.1899 | 65713.4485 | 68317.6698 | 66557.7818 | 67252.9949 | 66464.0643 | 69620.4076 | 71092.6092 | 69496.2398 | 73308.1534 | 74665.5795 | 74327.8368
Forecast | 77243.6379 | 78855.2515 | 80280.2923 | 81266.818 | 82057.6381 | 82838.0592 | 83615.9218 | 84361.6918 | 85094.6733 | 85820.1422

## Slide 33: ERCOT Gross Summer Peak Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167 | 89814.0662
2021 LTLF | 77243.6379 | 78855.2515 | 80280.2923 | 81266.818 | 82057.6381 | 82838.0592 | 83615.9218 | 84361.6918 | 85094.6733 | 85820.1422

## Slide 34: ERCOT Annual Energy Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 411250.124 | 424830.7607 | 437920.9466 | 449969.4074 | 458262.8869 | 467416.1431 | 476372.8197 | 486219.7609 | 493415.2383 | 501621.5583
2021 LTLF | 405842.0308 | 419616.1297 | 434006.1603 | 444425.8147 | 450675.8648 | 457853.9767 | 464902.5388 | 472950.0009 | 478510.2935 | 485142.9766

## Slide 35: ERCOT Annual Energy Forecast
Chart: Year
| 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 279880.5312 | 284375.2214 | 288387.3917 | 298454.3809 | 304979.6733 | 306592.3592 | 310856.8551 | 307388.6171 | 318292.4722 | 333992.2576 | 325010.9182 | 331740.3591 | 340140.816 | 347496.4293 | 351371.5138 | 357260.0082 | 376235.4109 | 383845.0491 | 382248.4728
Forecast | 405842.0308 | 419616.1297 | 434006.1603 | 444425.8147 | 450675.8648 | 457853.9767 | 464902.5388 | 472950.0009 | 478510.2935 | 485142.9766
December forecasted

## Slide 36
Rooftop PV Forecast

## Slide 37: Rooftop PV Forecast
This is the first year that a rooftop PV forecast was created
A forecast was created for residential ESIIDs using the load profile assignment for each weather zone
Total installed capacity was approximately 700 MW as of August, 2020
Forecast is for the total installed capacity to increase to approximately 2,100 MW by August, 2030
The assumed capacity factor at the time of the summer peak is 46%
The gross forecast minus the rooftop PV forecast results in the net forecast

## Slide 38: Rooftop PV Forecast - Approach
Chart: 8/14/2020
Residential with PV | 2.9942 | 2.6935 | 2.4703 | 2.2983 | 2.1521 | 2.0565 | 1.9853 | 1.761 | 1.3747 | 1.1335 | 1.0157 | 1.0241 | 1.0743 | 1.1352 | 1.3006 | 1.6109 | 2.1439 | 2.959 | 3.8669 | 4.4444 | 4.4532 | 4.187 | 3.8375 | 3.4472
Residential w/o PV | 2.5546 | 2.312 | 2.1167 | 1.967 | 1.8451 | 1.7715 | 1.7159 | 1.683 | 1.8042 | 2.0797 | 2.4253 | 2.8112 | 3.1796 | 3.4784 | 3.7016 | 3.8438 | 3.9578 | 4.0215 | 3.9767 | 3.7849 | 3.5967 | 3.4168 | 3.1551 | 2.8741

## Slide 39: Rooftop PV Forecast - Approach
Chart: 7/13/2020
Residential with PV | 3.045 | 2.7254 | 2.4901 | 2.3148 | 2.191 | 2.0879 | 1.9991 | 1.6896 | 1.3786 | 1.1611 | 1.0361 | 0.99524 | 1.0453 | 1.1463 | 1.3413 | 1.7372 | 2.2433 | 2.9341 | 3.7715 | 4.3613 | 4.5007 | 4.3102 | 3.9344 | 3.492
Residential w/o PV | 2.5828 | 2.3242 | 2.1298 | 1.9887 | 1.887 | 1.8112 | 1.7316 | 1.712 | 1.8416 | 2.1213 | 2.4966 | 2.9128 | 3.3117 | 3.6154 | 3.7997 | 3.9155 | 4.0091 | 4.0876 | 4.0813 | 3.9235 | 3.6902 | 3.5337 | 3.2518 | 2.9205

## Slide 40: Rooftop PV Forecast - Approach
Data from ERCOT’s monthly peak day in July (7/13/2020) and August (8/14/2020) was used
Calculate the total hourly demands for residential ESIIDs with PV
Calculate the total hourly demands for residential ESIIDs without PV
Divide the total hour demand values by the number of ESIIDs (result is an average use per ESIID with and without PV)
Divide the average use per ESIID with PV by the average use per ESIID without PV for each hour (call this the PV hourly factors)
Multiply the PV hourly factors by the forecasted number of PV Premises

## Slide 41: Rooftop PV Forecast - Approach
Use the PV hourly factor for hour 17 to create the PV Summer Peak forecast
Subtract out the current contribution of PV (as of August, 2020)
Assume no PV output at the time of the winter peak which is typically 8 a.m.
Assume the same PV hourly factor for residential and business ESIIDs
This is a work in progress. More analysis will be performed in 2021.

## Slide 42: Rooftop PV Forecast
Chart: Rooftop PV Forecast (MW) at Time of Summer Peak
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Rooftop PV Forecast (MW) | 100 | 190 | 280 | 359.3751 | 425.9655 | 483.9269 | 540.0378 | 579.8566 | 613.369 | 641.5196

## Slide 43: Observations
Residential ESIIDs with PV have greater average usage per hour than ESIIDs without PV during the early morning and evening hours
Some studies suggest that customers with PV tend to use more energy
To compensate for this, should the shapes be unitized?

## Slide 44
Forecast Adjustments

## Slide 45: Load Forecast Adjustments
Lubbock added to North Forecast from 2021 on
  Based on Lubbock’s Peak Forecast of its growth
“Fiber Services in Lubbock, TX.” About NTS, NTS Communications, Inc., 2018, www.ntscom.com/aboutnts/primary-locations/lubbock-tx.

## Slide 46: Load Forecast Adjustments
Rayburn added to East Forecast from 2021 on
  Based on Rayburn’s Actual Seasonal Peaks in 2019
“RCEC.” PROJECTS>OFFICE>RCEC, Alliance Architects, 2019, www.alliancearch.com/projects/office/rcec/.

## Slide 47: Load Forecast Adjustments
Adjustments added for Large Industrial Facilities
  Coast
    425 – 650 MW phased in over time
  South
    75 – 930 MW phased in over time
  South Central
    24 – 480 MW phased in over time

## Slide 48
Assumptions and Challenges

## Slide 49: Assumptions
Inherent Levels from the Input Data of
  Appliance Stock and Energy Efficiency
  Demand Response
  4 CP Impact
  Behind-the-Meter DG (non rooftop solar)
  Price Responsive Load
  Electric Vehicles (significant impact on future forecasts)

## Slide 50: Challenges
Weather Volatility
Economic Uncertainty
Policy Impacts

## Slide 51
Weather Zone Forecast Summary

## Slide 52: Coast Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 19321.0084 | 18410.6379 | 18770.1669 | 18578.0722 | 19928.7248 | 19826.1816 | 20100.7586 | 20269.849 | 21256.1152 | 20904.8591
Forecast | 21645.003 | 21938.0589 | 22229.7592 | 22446.9686 | 22634.7961 | 22829.8089 | 23020.0229 | 23208.2339 | 23397.7648 | 23585.6714
90th Percentile | 22523.5179 | 22815.6269 | 23108.228 | 23326.6428 | 23514.6901 | 23709.6759 | 23899.9784 | 24088.2053 | 24277.7187 | 24465.6994

## Slide 53: East Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 2570.0318 | 2420.8076 | 2379.3416 | 2324.9016 | 2463.9556 | 2493.8287 | 2415.8767 | 2620.839 | 2554.0154 | 2871.3338
Forecast | 2811.1295 | 2850.4577 | 2895.0741 | 2940.2025 | 2983.7356 | 3026.0158 | 3066.4813 | 3105.4974 | 3143.6681 | 3180.8921
90th Percentile | 2911.4086 | 2950.8705 | 2995.487 | 3040.5818 | 3084.1484 | 3126.3618 | 3166.7269 | 3205.7431 | 3243.9137 | 3281.0708

## Slide 54: Far West Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 2102.6526 | 2172.2454 | 2278.6712 | 2688.0037 | 2811.8407 | 2908.9704 | 3164.1864 | 3655.0145 | 4307.5529 | 4438.8515
Forecast | 4906.6779 | 5076.1968 | 5268.9138 | 5445.1702 | 5620.8737 | 5786.239 | 5961.2135 | 6121.658 | 6278.162 | 6437.8852
90th Percentile | 5418.4604 | 5645.4777 | 5883.8791 | 6114.0631 | 6349.6165 | 6581.7335 | 6817.8841 | 7058.579 | 7300.0126 | 7543.9874

## Slide 55: North Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 1563.7511 | 1559.0797 | 1483.4728 | 1407.7908 | 1451.5364 | 1440.1835 | 1393.5089 | 1521.8453 | 1476.3299 | 1420.1554
Forecast | 1898.4366 | 1899.71 | 1900.9445 | 1902.2566 | 1903.6715 | 1905.1033 | 1906.6127 | 1908.2046 | 1909.9297 | 1911.6886
90th Percentile | 1990.0491 | 1991.3169 | 1992.5493 | 1993.8677 | 1995.2771 | 1996.7017 | 1998.2122 | 1999.8087 | 2001.5266 | 2003.28
Lubbock added 2021

## Slide 56: North Central Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 25626.4845 | 24747.9427 | 24420.6897 | 23445.6124 | 24580.6459 | 25282.3165 | 24313.2101 | 26499.241 | 25493.7914 | 25510.2523
Forecast | 26055.0508 | 26259.1483 | 26491.4919 | 26725.003 | 26950.9231 | 27171.2119 | 27382.68 | 27586.688 | 27781.5963 | 27970.4187
90th Percentile | 27222.35 | 27425.707 | 27657.8095 | 27891.4412 | 28117.5507 | 28338.0289 | 28549.7037 | 28754.0217 | 28949.1022 | 29138.0451

## Slide 57: South Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 5297.9871 | 5240.6816 | 5206.7333 | 5352.2159 | 5455.4528 | 5786.8259 | 5845.2837 | 6176.1064 | 6039.7135 | 5850.2163
Forecast | 6033.4244 | 6671.656 | 6994.3821 | 7207.6277 | 7262.5987 | 7320.1017 | 7375.4901 | 7430.3624 | 7485.9654 | 7541.1585
90th Percentile | 6168.9759 | 6806.6361 | 7130.0709 | 7344.5951 | 7400.0695 | 7457.5569 | 7513.1533 | 7567.9981 | 7623.5571 | 7678.8224

## Slide 58: South Central Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 11734.5525 | 11641.4929 | 11432.8102 | 11452.2257 | 12032.5532 | 12344.8416 | 11970.2041 | 12886.8971 | 12784.8579 | 13010.9607
Forecast | 12957.1489 | 13194.2747 | 13510.7538 | 13586.5491 | 13658.4228 | 13727.8556 | 13794.75 | 13859.4174 | 13921.195 | 13980.7334
90th Percentile | 13669.1038 | 13905.9755 | 14222.425 | 14298.3108 | 14370.2402 | 14439.7531 | 14506.6718 | 14571.4506 | 14633.296 | 14692.8918

## Slide 59: West Gross Summer NCP Forecasts
Chart: Year
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Actual | 1853.8705 | 1849.1276 | 1862.3039 | 1852.9276 | 1883.889 | 1899.0862 | 1901.9406 | 2083.5791 | 2117.3991 | 2058.4193
Forecast | 2069.2454 | 2097.1693 | 2122.4426 | 2149.2467 | 2177.936 | 2207.1731 | 2239.222 | 2273.293 | 2309.4024 | 2346.7846
90th Percentile | 2159.551 | 2187.4669 | 2212.6999 | 2239.4557 | 2268.0241 | 2297.3902 | 2329.4632 | 2363.4456 | 2399.4825 | 2436.897

## Slide 60: Coast Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 21862.9327 | 22206.0532 | 22521.2584 | 22829.4103 | 23134.3416 | 23437.9834 | 23738.678 | 24030.3715 | 24314.4167 | 24593.3095
2021 LTLF | 21645.003 | 21938.0589 | 22229.7592 | 22446.9686 | 22634.7961 | 22829.8089 | 23020.0229 | 23208.2339 | 23397.7648 | 23585.6714

## Slide 61: East Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 2762.0251 | 2788.8114 | 2807.4572 | 2825.3976 | 2841.7367 | 2858.7823 | 2876.7427 | 2893.2117 | 2909.4943 | 2924.7997
2021 LTLF | 2811.1295 | 2850.4577 | 2895.0741 | 2940.2025 | 2983.7356 | 3026.0158 | 3066.4813 | 3105.4974 | 3143.6681 | 3180.8921

## Slide 62: Far West Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 5301.0839 | 5553.5078 | 5798.4962 | 6035.8231 | 6265.351 | 6490.5893 | 6707.2612 | 6915.4144 | 7113.6241 | 7307.4251
2021 LTLF | 4942.5517 | 5168.674 | 5394.7964 | 5615.5349 | 5830.8895 | 6046.2441 | 6248.1391 | 6441.9582 | 6635.7774 | 6816.1369

## Slide 63: North Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 1911.867 | 1915.6207 | 1919.5077 | 1923.5744 | 1927.6019 | 1931.5135 | 1935.5169 | 1939.7093 | 1944.1927 | 1948.7281
2021 LTLF | 1898.4366 | 1899.71 | 1900.9445 | 1902.2566 | 1903.6715 | 1905.1033 | 1906.6127 | 1908.2046 | 1909.9297 | 1911.6886

## Slide 64: North Central Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 26302.7895 | 26620.8614 | 26965.1683 | 27309.9794 | 27647.9747 | 27978.173 | 28295.7904 | 28599.965 | 28889.8294 | 29173.4717
2021 LTLF | 26055.0508 | 26259.1483 | 26491.4919 | 26725.003 | 26950.9231 | 27171.2119 | 27382.68 | 27586.688 | 27781.5963 | 27970.4187

## Slide 65: South Central Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 13049.5296 | 13206.4219 | 13375.9936 | 13544.3559 | 13706.9474 | 13864.4515 | 14016.3099 | 14162.2411 | 14301.2948 | 14436.7272
2021 LTLF | 12957.1489 | 13194.2747 | 13510.7538 | 13586.5491 | 13658.4228 | 13727.8556 | 13794.75 | 13859.4174 | 13921.195 | 13980.7334

## Slide 66: South Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 6080.2976 | 6734.2223 | 7069.7895 | 7322.2065 | 7424.6283 | 7526.4044 | 7626.8603 | 7723.8234 | 7818.2021 | 7911.152
2021 LTLF | 6033.4244 | 6671.656 | 6994.3821 | 7216.7695 | 7441.2791 | 7592.5093 | 7744.943 | 7893.1735 | 8041.8162 | 8191.0078

## Slide 67: West Gross Summer NCP Forecast
Chart: Year
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
2020 LTLF | 2153.2677 | 2207.6373 | 2262.9268 | 2319.2258 | 2373.0337 | 2424.6495 | 2478.5355 | 2534.1704 | 2591.4849 | 2650.2106
2021 LTLF | 2069.2454 | 2125.8456 | 2180.7766 | 2234.3747 | 2291.5684 | 2351.4377 | 2415.4879 | 2484.3042 | 2556.4652 | 2632.4725

## Slide 68: Questions?