| NOGRR Number | 979 | NPRR Title | Incorporate State Estimator Standards and Telemetry Standards into Protocols |
| --- | --- | --- | --- |

| Date | January 4, 2021 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | David L. Mercado; Bill Valagura |
| E-mail Address | David.Mercado@centerpointenergy.com; Bill.Valagura@calpine.com |
| Company | CenterPoint Energy Houston Electric, LLC; Calpine Corporation |
| Phone Number | (713) 207-2125; (832) 753-3546 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU); Independent Generator |

Comments

CenterPoint Energy Houston Electric, LLC (CenterPoint Energy) and Calpine Corporation (Calpine) appreciate the opportunity to provide joint comments on top of the 7/30/20 Calpine comments.  The revised language in paragraph (5) of Section 3.10.5, TSP Responsibilities, seeks to bolster communication and reasonable notice, if practicable, of Transmission Service Providers (TSPs) telemetry changes when the TSP has previously approved the Qualified Scheduling Entity’s (QSE’s) use of the TSP’s telemetry for a Generation Resource’s Bulk Electric System protection scheme or for generation control.  This will allow the QSE to take actions necessary to ensure that the protection scheme is not impaired and/or the generation control system is not degraded.

A minor clarification is also made to paragraph (5)(c) of Section 3.10.7.5.10, ERCOT Request for Redundant Telemetry.

Market Rules Notes

Please note the baseline Protocol language in the following section(s) has been updated to reflect the incorporation of the following NPRR(s) into the Protocols:

- NPRR957 – RTF-4 Definition of Energy Storage Resource and Related Registration and Telemetry Requirements (effective 1/1/20)

  - Section 3.10.7.5.2

Please note the following NPRRs also propose revisions to the following sections:

- NPRR1005, Clarify Definition of Point of Interconnection (POI) and Add Definition Point of Interconnection Bus (POIB)

  - Section 3.10.7.5.2

Revised Cover Page Language

| Nodal Protocol Sections Requiring Revision | 2.1, Definitions 2.2, Acronyms and Abbreviations 3.10.5, TSP Responsibilities 3.10.6, Resource Entity Responsibilities 3.10.7.5, Telemetry Standards 3.10.7.5.1, Continuous Telemetry of the Status of Breakers and Switches 3.10.7.5.2, Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows 3.10.7.5.3, Required Telemetry of Voltage and Power Flow (new) 3.10.7.5.4, General Telemetry Performance Criteria (new) 3.10.7.5.5, Supplemental Telemetry Performance Criteria (new) 3.10.7.5.6, TSP/QSE Telemetry Restoration (new) 3.10.7.5.7, Calibration, Quality Checking and Testing (new) 3.10.7.5.8, Inter-Control Center Communications Protocol (ICCP) Links (new) 3.10.7.5.8.1, Data Quality Codes (new) 3.10.7.5.8.2, Reliability of ICCP Associations (new) 3.10.7.5.9, ERCOT Requests for Telemetry (new) 3.10.7.5.10, ERCOT Request for Redundant Telemetry (new) 3.10.9, State Estimator Standards 3.10.9.1, Considerations for State Estimator Standards 3.10.9.2, Telemetry and State Estimator Performance Monitoring 3.10.9.2, State Estimator Data (new) 3.10.9.3, Telemetry Status and Analog Measurements Data (new) 3.10.9.4, State Estimator Performance Requirements (new) 3.10.9.5, ERCOT Directives (new) |
| --- | --- |

Revised Proposed Protocol Language

## 2.1	DEFINITIONS

State Estimator

A computational algorithm that uses Real-Time inputs from the network’s Supervisory Control and Data Acquisition (SCADA) system that measure the network’s electrical parameters, including its topology, voltage, power flows, etc., to estimate electrical parameters (such as line flows and Electrical Bus voltages and Loads) in the ERCOT Transmission Grid.  The State Estimator’s output is a description of the network and all of the values (topology, voltage, power flow, etc.) to describe each Electrical Bus and line included in the system model.

State Estimator  Bus

An electrical node of common voltage at a substation that consists of one or more Electrical Buses tied together with closed breakers or switches.

## 2.2	ACRONYMS AND ABBREVIATIONS

3.10.5	TSP Responsibilities

(1)	Each TSP shall design, implement, operate, and maintain its systems to meet the requirements of Section 3.10.7.5, Telemetry Requirements, for measurements facilitating the observability of the Electrical Buses used for Security-Constrained Economic Dispatch (SCED).  However, there is no obligation to re-construct or retrofit already existing installations except as shown to be needed in order to comply with Section 3.10.7.5 and Section 3.10.9, State Estimator Requirements.

(2)	TSPs shall add telemetry to equipment it owns or directly operates and controls at ERCOT’s request to maintain observability and redundancy requirements as specified herein, and under Section 3.10.7.5.  ERCOT shall request such additions when a lack of data telemetry has caused, or can be demonstrated to result in, inaccuracies between Real-Time measurements and modeling outcomes that could result in incorrect LMP prices or potential reliability problems.

(3)	Each TSP shall provide to ERCOT planned construction information, including Certificate of Convenience and Necessity (CCN) application milestone dates if applicable, all of which shall be updated according to a schedule established by ERCOT.

(4)	Each TSP shall provide to ERCOT project status updates of Transmission Facilities that are part of an Reliability Must-Run (RMR) or Must Run Alternative (MRA) exit strategy corresponding to a specific RMR or MRA Agreement that has not been terminated, which shall be updated by the first Business Day of each month, noting any acceleration or delay in planned completion date.

(5)	A QSE must receive approval from a TSP prior to using the TSP’s telemetry as part of a Generation Resource’s Bulk Electric System protection scheme or for generation control.  If a TSP has approved a QSE’s use of the TSP’s telemetry, the TSP shall inform the QSE of any telemetry changes with reasonable notice prior to the change or where prior notice is not possible as soon as reasonably practicable thereafter, including discontinuation of the TSP’s provision of such telemetry, and the timeline for the changes.

[NPRR857: Replace Section 3.10.5 above with the following upon system implementation:] - 3.10.5 TSP and DCTO Responsibilities (1) Each TSP and DCTO shall design, implement, operate, and maintain its systems to meet the requirements of Section 3.10.7.5, Telemetry Requirements, for measurements facilitating the observability of the Electrical Buses used for Security-Constrained Economic Dispatch (SCED). However, there is no obligation to re-construct or retrofit already existing installations except as shown to be needed in order to comply with Section 3.10.7.5 and Section 3.10.9, State Estimator Requirements. (2) Each TSP and DCTO shall add telemetry to equipment it owns or directly operates and controls at ERCOT’s request to maintain observability and redundancy requirements as specified herein, and under Section 3.10.7.5. ERCOT shall request such additions when a lack of data telemetry has caused, or can be demonstrated to result in, inaccuracies between Real-Time measurements and modeling outcomes that could result in incorrect LMP prices or potential reliability problems. (3) Each TSP and DCTO shall provide to ERCOT planned construction information, including Certificate of Convenience and Necessity (CCN) application milestone dates if applicable, all of which shall be updated according to a schedule established by ERCOT. (4) Each TSP shall provide to ERCOT project status updates of Transmission Facilities that are part of an Reliability Must-Run (RMR) or Must Run Alternative (MRA) exit strategy corresponding to a specific RMR or MRA Agreement that has not been terminated, which shall be updated by the first Business Day of each month, noting any acceleration or delay in planned completion date. (5) A QSE must receive approval from a TSP prior to using the TSP’s telemetry as part of a Generation Resource’s Bulk Electric System protection scheme or for generation control. If a TSP has approved a QSE’s use of the TSP’s telemetry, the TSP shall inform the QSE of any telemetry changes with reasonable notice prior to the change or where prior notice is not possible as soon as reasonably practicable thereafter, including discontinuation of the TSP’s provision of such telemetry, and the timeline for the changes.

3.10.6	QSE and Resource Entity Responsibilities

(1)	Resource Entities shall provide Resource Registration data pursuant to Planning Guide Section 6.8.2, Resource Registration Process, to ERCOT and to TSPs upon request.  The Resource Registration data will contain information describing each Generation Resource, SOG, and Load Resource that it represents under Section 3.10.7.2, Modeling of Resources and Transmission Loads.

(2)	QSEs shall ensure availability of telemetry to generation and transmission equipment its Resource Entity owns  at ERCOT’s request to maintain observability and redundancy requirements as specified herein, and under Section 3.10.7.5.  ERCOT shall request such additions when a lack of data telemetry has caused, or can be demonstrated to result in, inaccuracies between Real-Time measurements and modeling outcomes that could result in incorrect LMP prices or potential reliability problems.

3.10.7.5	Telemetry Requirements

(1)	The telemetry provided to ERCOT necessary to support the State Estimator must meet the requirements set forth in Section 3.10.9, State Estimator Requirements.

(2)	The telemetry provided to ERCOT by each TSP and QSE must be updated at a ten second or less scan rate and be provided to ERCOT at the same rate.  Each TSP and QSE shall install appropriate condition detection capability to notify ERCOT of potentially incorrect data from loss of communication or scan function.  Condition codes must accompany the data to indicate its quality and whether the data has been measured within the scan rate requirement.  Also, ERCOT shall analyze data received for possible loss of updates.  Similarly, ERCOT shall provide condition detection capability on loss of telemetry links with the TSP and QSE.  ERCOT shall represent data condition codes from each TSP and QSE in a consistent manner for all applicable ERCOT applications.

[NPRR857: Replace paragraph (3) above with the following upon system implementation:] (2) The telemetry provided to ERCOT by each TSP, QSE, or DCTO must be updated at a ten second or less scan rate and be provided to ERCOT at the same rate. Each TSP, DCTO, and QSE shall install appropriate condition detection capability to notify ERCOT of potentially incorrect data from loss of communication or scan function. Condition codes must accompany the data to indicate its quality and whether the data has been measured within the scan rate requirement. Also, ERCOT shall analyze data received for possible loss of updates. Similarly, ERCOT shall provide condition detection capability on loss of telemetry links with the TSP, DCTO, and QSE. ERCOT shall represent data condition codes from each TSP, DCTO, and QSE in a consistent manner for all applicable ERCOT applications.

(3)	Each TSP and QSE shall use fully redundant Inter-Control Center Communications Protocol (ICCP) links  between its control center systems and ERCOT systems such that any single element of the communication system can fail and:

(a)	For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and

(b)	For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT’s control centers with updates of all data continuing at a 30 second or less scan rate.

[NPRR857: Replace paragraph (4) above with the following upon system implementation:] (3) Each TSP, DCTO, and QSE shall use fully redundant Inter-Control Center Communications Protocol (ICCP) links between its control center systems and ERCOT systems such that any single element of the communication system can fail and: (a) For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and (b) For all other failures, complete information must continue to flow between the TSP’s, DCTO’s, QSE’s, and ERCOT’s control centers with updates of all data continuing at a 30 second or less scan rate.

(4)	When ERCOT identifies a reliability concern, a deficiency in system observability, or a deficiency in measurement to support the representation of Model Loads, and that concern or deficiency is not due to any inadequacy of the State Estimator program, additional telemetry may be requested as described in Section 3.10.7.5.9, ERCOT Requests for Telemetry.

[NPRR857: Replace paragraph (4) above with the following upon system implementation:] (4) When ERCOT identifies a reliability concern, a deficiency in system observability, or a deficiency in measurement to support the representation of Model Loads, and that concern or deficiency is not due to any inadequacy of the State Estimator program, additional telemetry may be requested as described in Section 3.10.7.5.9, ERCOT Requests for Telemetry.

3.10.7.5.1	Continuous Telemetry of the Status of Breakers and Switches

(1)	Each TSP and QSE shall be responsible for providing telemetry, as described in this subsection, to ERCOT on the status of all breakers and switches it owns or its Resource owns, respectively,  used to switch any Transmission Element or Load modeled by ERCOT.

(2)	Each TSP and QSE is not required to install telemetry on individual breakers and switches it owns or its Resource Entity owns, respectively,  where the telemetered status shown to ERCOT is current and free from ambiguous changes in state caused by the TSP or Resource Entity switching operations and TSP or Resource Entity personnel.

(3)	Each TSP, Resource Entity, or QSE shall update the status of any breaker or switch it owns or is responsible for through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute.

(4)	If in the sole opinion of ERCOT, the manual updates of the TSP or QSE have been unsuccessful in maintaining the accuracy required to support State Estimator performance to a TAC-approved predefined standard as described in Section 3.10.9, ERCOT may request that the TSP or QSE install complete telemetry from the breaker or switch it owns or its Resource Entity owns, respectively,  to the TSP or QSE, and then to ERCOT.

(a)	In making the determination to request installation of additional telemetry from a breaker or switch, ERCOT shall consider the economic implications of inaccurate representation of Model Loads in LMP results versus the cost to remedy.

(b)	If the TSP or QSE disputes the request for additional telemetry on individual breakers and switches it owns or its Resource Entity owns, respectively, it may appeal the request pursuant to Section 3.10.7.5.9, ERCOT Requests for Telemetry.

[NPRR857: Replace paragraphs (1) through (4) above with the following upon system implementation:] (1) Each TSP, DCTO, and QSE shall provide telemetry, as described in this subsection, to ERCOT on the status of all breakers and switches it owns or its Resource Entity owns, respectively used to switch any Transmission Element or Load modeled by ERCOT. (2) Each TSP, DCTO, and QSE is not required to install telemetry on individual breakers and switches it owns or its Resource Entity owns, respectively, where the telemetered status shown to ERCOT is current and free from ambiguous changes in state caused by the TSP, DCTO, or QSE switching operations and TSP, DCTO, or QSE personnel. (3) Each TSP, DCTO, and QSE shall update the status of any breaker or switch it owns or its Resource Entity owns, respectively, through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute. (4) If in the sole opinion of ERCOT, the manual updates of the TSP, DCTO, or QSE have been unsuccessful in maintaining the accuracy required to support State Estimator performance to a TAC-approved predefined standard as described in Section 3.10.9, ERCOT may request that the TSP, DCTO, or QSE install complete telemetry from the breaker or switch it owns or its Resource Entity owns, respectively, to the TSP, DCTO, or QSE, and then to ERCOT. (a) In making the determination to request installation of additional telemetry from a breaker or switch, ERCOT shall consider the economic implications of inaccurate representation of Model Loads in LMP results versus the cost to remedy. (b) If the TSP or associated QSE disputes the request for additional telemetry it owns or its Resource Entity owns, respectively, it may appeal the request pursuant to Section 3.10.7.5.9, ERCOT Requests for Telemetry.

(5)	ERCOT shall measure TSP and QSE performance in providing accurate data that do not include ambiguous changes in state and shall report the performance metrics on the Market Information System (MIS) Secure Area on a monthly basis.

[NPRR857: Replace paragraph (5) above with the following upon system implementation:] (5) ERCOT shall measure TSP, DCTO, and QSE performance in providing accurate data that do not include ambiguous changes in state and shall report the performance metrics on the Market Information System (MIS) Secure Area on a monthly basis.

(6)	Unless there is an Emergency Condition, TSPs and QSEs must obtain approval from ERCOT to purposely open a breaker or switch unless that breaker or switch is shown in a Planned Outage in the Outage Scheduler, or the device will return to its previous state within 60 minutes, or the device is a generator output circuit breaker.  Also, TSPs and QSEs must obtain approval from ERCOT before closing any breaker or switch, except in response to a Forced Outage, or an emergency, or the device will return to its previous state within 60 minutes, or the device is a generator output circuit breaker.

[NPRR857: Replace paragraph (6) above with the following upon system implementation:] (6) Unless there is an Emergency Condition, TSPs, DCTOs, and QSEs must obtain approval from ERCOT to purposely open a breaker or switch unless that breaker or switch is shown in a Planned Outage in the Outage Scheduler, or the device will return to its previous state within 60 minutes, or the device is a generator output circuit breaker. Also, TSPs, DCTOs, and QSEs must obtain approval from ERCOT before closing any breaker or switch, except in response to a Forced Outage, or an emergency, or the device will return to its previous state within 60 minutes, or the device is a generator output circuit breaker.

(7)	ERCOT shall monitor the data condition codes of all breakers and switches showing loss of communication or scan function in the Network Operations Model.  When the telemetry of breakers and switches is lost, ERCOT shall use the last known state of the device for security analysis as updated by the Outage Scheduler and through verbal communication with the TSP or QSE.  ERCOT’s systems must identify probable errors in switch or breaker status and ERCOT shall act to resolve or correct such errors in a timely manner as described in Section 6, Adjustment Period and Real-Time Operations.

[NPRR857: Replace paragraph (7) above with the following upon system implementation:] (7) ERCOT shall monitor the data condition codes of all breakers and switches showing loss of communication or scan function in the Network Operations Model. When the telemetry of breakers and switches is lost, ERCOT shall use the last known state of the device for security analysis as updated by the Outage Scheduler and through verbal communication with the TSP, DCTO, or QSE. ERCOT’s systems must identify probable errors in switch or breaker status and ERCOT shall act to resolve or correct such errors in a timely manner as described in Section 6, Adjustment Period and Real-Time Operations.

(8)	ERCOT shall establish a system that provides alarms to ERCOT Operators when there is a change in status of any monitored transmission breaker or switch, and an indication of whether the device change of status was planned in the Outage Scheduler.  ERCOT Operators shall monitor any changes in status not only for reliability of operations, but also for accuracy and impact on the operation of the SCED functions and subsequent potential for calculation of inaccurate LMPs.

(9)	Each QSE that represents a Split Generation Resource, with metering according to Section 3.8, Special Considerations for Split Generation Meters, Combined Cycle Generation Resources, Quick Start Generation Resources, Hydro Generation Resources, and Limited Duration Resources, shall provide ERCOT with telemetry of the actual generator breakers and switches continuously providing ERCOT with the status of the individual Split Generation Resource.

3.10.7.5.2	Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows

(1)	Each TSP and QSE shall provide telemetry of voltages, flows, and Loads on any modeled Transmission Element it owns or its Resource Entity owns, respectively, to the extent such may be required to estimate all transmission Load withdrawals and generation injections to and from the ERCOT Transmission Grid using the State Estimator and as needed to meet the State Estimator requirements set forth in Section 3.10.9 with consideration given to the economic implications of inaccurate LMP results versus the cost to remedy.

[NPRR857: Replace paragraph (1) above with the following upon system implementation:] (1) Each TSP, DCTO, and QSE shall provide telemetry of voltages, flows, and Loads on any modeled Transmission Element it owns or its Resource Entity owns, respectively, to the extent such may be required to estimate all transmission Load withdrawals and generation injections to and from the ERCOT Transmission Grid using the State Estimator and as needed to meet the State EstimatorState Estimator requirements set forth in Section 3.10.9 with consideration given to the economic implications of inaccurate LMP results versus the cost to remedy.

(2)	Each QSE that represents a Split Generation Resource, with metering according to Section 3.8, Special Considerations for Split Generation Meters, Combined Cycle Generation Resources, Quick Start Generation Resources, Hydro Generation Resources, Limited Duration Resources and Energy Storage Resources, shall provide ERCOT with telemetry of the actual equivalent generator injection of its Split Generation Resource and the Master QSE shall provide telemetry in accordance with Section 6.5.5.2, Operational Data Requirements, on a total Generation Resource basis.  ERCOT shall calculate the sum of each QSE’s telemetry on a Split Generation Resource and compare the sum to the telemetry for the total Generation Resource.  ERCOT shall notify each QSE representing a Split Generation Resource of any errors in telemetry detected by the State Estimator.

(3)	Each TSP and QSE shall provide telemetered measurements at a periodicity of 10 seconds on modeled Transmission Elements it owns or its Resource Entity owns, respectively, to ensure State Estimator observability of any monitored voltage and power flow between their associated transmission breakers to the extent such can be shown to be needed to meet the State Estimator requirements set forth in Section 3.10.9.  On monitored non-Load substations, ERCOT may request additional telemetry in accordance with Section 3.10.7.5.10.

[NPRR857: Replace paragraph (3) above with the following upon system implementation:] (3) Each TSP, DCTO, and QSE shall provide telemetered measurements at a periodicity of ten seconds on modeled Transmission Elements it owns or its Resource Entity owns, respectively, to ensure State Estimator observability of any monitored voltage and power flow between their associated transmission breakers to the extent such can be shown to be needed to meet the State Estimator requirements set forth in Section 3.10.9. On monitored non-Load substations, ERCOT may request additional telemetry in accordance with Section 3.10.7.5.10.

(4)	The accuracy of the State Estimator is critical to successful market operations.  For this reason it is a critical objective for ERCOT to maintain reasonable and accurate results of the State Estimator.  ERCOT shall use all reasonable efforts to achieve that objective, including the provision of legitimate constraints used in calculating LMPs.

(5)	Each TSP, QSE and ERCOT shall develop a continuously operated program to maintain telemetry of all Transmission Element measurements to provide accurate State Estimator results as outlined in Section 3.10.9.  For any location where there is a connection of multiple, measured, Transmission Elements, ERCOT shall have an automated process to detect and notify ERCOT System operators if the residual sum of all telemetered measurements is more than:

(a)	Five percent of the largest line Normal Rating at the State Estimator Bus; or

(b)	Five MW, whichever is greater.

If a location chronically fails this test, ERCOT shall notify the applicable TSP or QSE and suggest actions that the TSP or QSE could take to correct the failure.  Within 30 days, the TSP or QSE shall take the actions necessary to correct the failure or provide ERCOT with a detailed plan with a projected time frame to correct the failure.  ERCOT shall post a notice on the MIS Secure Area of any State Estimator Buses not meeting the State Estimator requirements set forth in Section 3.10.9, including a list of all measurements and the residual errors on a monthly basis.

[NPRR857: Replace paragraph (5) above with the following upon system implementation:] (5) Each TSP, DCTO, QSE, and ERCOT shall develop a continuously operated program to maintain telemetry of all Transmission Element measurements to provide accurate State Estimator results as outlined in Section 3.10.9. For any location where there is a connection of multiple, measured, Transmission Elements, ERCOT shall have an automated process to detect and notify ERCOT System operators if the residual sum of all telemetered measurements is more than: (a) Five percent of the largest line Normal Rating at the State Estimator Bus; or (b) Five MW, whichever is greater. If a location chronically fails this test, ERCOT shall notify the applicable TSP, DCTO, or QSE and suggest actions that the TSP, DCTO, or QSE could take to correct the failure. Within 30 days, the TSP, DCTO, or QSE shall take the actions necessary to correct the failure or provide ERCOT with a detailed plan with a projected time frame to correct the failure. ERCOT shall post a notice on the MIS Secure Area of any State Estimator Buses not meeting the State Estimator requirements set forth in Section 3.10.9, including a list of all measurements and the residual errors on a monthly basis.

(6)	ERCOT shall implement a study mode version of the State Estimator with special tools designed for troubleshooting and tuning purposes that can be used independently of any other ERCOT process that is dependent on the Real-Time State Estimator.  ERCOT shall implement a process to recognize inaccurate State Estimator results and shall create and implement alternative Real-Time LMP calculation processes for use when inaccurate results are detected.  ERCOT must be guided in this by Section 3.10.9.

(7)	ERCOT shall establish a system to provide overload and over/under limit alarming on all Transmission Elements monitored as constraints in the LMP models.

(8)  	Each TSP shall designate which telemetered measurement of the POI kV bus voltage shall be utilized to determine compliance with Voltage Set Point instructions, and then update the designation as necessary in the Network Operations Model by submitting a NOMCR.  Each TSP shall telemeter this POI kV bus measurement to ERCOT.  If the TSP cannot provide a kV bus measurement at the POI, the TSP may propose an alternate location subject to ERCOT approval.

#### 3.10.7.5.3 	Required Telemetry of Voltage and Power Flow

(1)	QSEs, Resource Entities and Transmission Service Providers (TSPs) as indicated in each subsection below shall provide power operation data to ERCOT, including, but not limited to:

(a)	Real-Time generation data from QSEs;

(b)	Planned and Forced Outage information from QSEs;

(c)	Network data from TSPs and QSEs , including:

(i)	Breaker and line switch status of all ERCOT Transmission Grid devices;

(ii)	Line flow MW and MVAr;

(iii)	Breaker and switch status connected to any Resource;

(iv)	Transmission Facility voltages; and

(v)	Transformer MW, MVAr and tap;

(d)	Real-Time generation and Load Resource meter data from QSEs;

(e)	Real-Time generation meter splitting signal from QSEs;

(f)	Transmission Facility Planned and Forced Outage information from TSPs;

(g)	Network transmission data (model and constraints) from TSPs; and

(h)	Resource modeling data, including any Resource owned transmission equipment data from Resource entity; and

(i)	Dynamic schedules from QSEs.

(2)	Real-Time data will be provided to ERCOT at the same scan rate as the TSP, Resource Entity, or QSE obtains the data from telemetry unless ERCOT requests a slower rate.

### 3.10.7.5.4	General Telemetry Performance Criteria

(1)	The following criteria will apply to telemetry provided to ERCOT.  Performance is posted on the MIS Secure Area in accordance with Nodal Operating Guide Section 9, Monitoring Programs:

(a)	Each TSP shall maintain the sum of flows into any telemetered bus it owns or is responsible for less than the greater of 5 MW or 5% of the largest normal line rating at each bus.

(b)	Each TSP and QSE shall provide data to ERCOT that meets the following availability:

(i)	92% of all telemetry provided to ERCOT must achieve a quarterly availability of 80%.  Availability shall be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with a Valid, Manual, or Calculated quality code at the scheduled periodicity.  Quality codes are defined in Section 3.10.7.5.8.1, Data Quality Codes.

(ii)	TSPs shall make reasonable efforts to obtain data from Customers associated with new Customer-owned substations to meet this requirement or obtain agreement from ERCOT that these Customers have entered into arrangements with ERCOT to provide this data to ERCOT.  If the data cannot be obtained under either of these methods, ERCOT shall report such case to the IMM.

(c)	Exceptions to the general telemetry performance criteria may be made, at ERCOT’s sole discretion, for data points not significant in the solution of the State Estimator or required for the reliable operation on the ERCOT Transmission Grid.  Examples of such data points include but are not limited to:

(i)	A substation with no more than two transmission lines and less than 10 MW of peak Load;

(ii)	Connection of Loads along a continuous, non-branching circuit that may be combined for telemetry purposes; and

(iii)	Substations connected radially to the ERCOT Transmission Grid.

(d)	During a Force Majeure Event, ERCOT may suspend requirements until normal operations have resumed.

### 3.10.7.5.5	Supplemental Telemetry Performance Criteria

(1)	ERCOT shall identify specific MW/MVAr telemetry pairs, not exceeding 10% of the Transmission Elements within the ERCOT System, and the 20 station voltage points that are most important to reliability, system observability or support of State Estimator performance, or are of a commercial market concern.

(2)	The important telemetry points identified pursuant to this Section must meet more stringent criteria for accuracy and availability where specifically addressed.  ERCOT shall review this list annually.  ERCOT shall publish the list of important telemetry points quarterly on the MIS Secure Area.

(3)	ERCOT shall use the following criteria to identify the important telemetry points:

(a) 	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(b) 	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(c) 	Loss of a telemetry point that results in the inability of ERCOT to monitor the loading on Transmission Facilities designated as important to transmission reliability by ERCOT.

(d) 	Telemetry necessary to monitor Transmission Elements identified as causing 80% of all congestion cost in the year for which the most recent data is available.

(e) 	Telemetry necessary to monitor the bus voltages at the 20 most important station voltage points.

(4)	Each TSP and QSE shall provide data to ERCOT such that 92% of the important telemetry points identified achieve a quarterly availability of 90%.  Availability shall be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with Valid, Manual, or Calculated quality codes at the scheduled periodicity.  Quality codes are defined in Section 3.10.7.5.8.1.

### 3.10.7.5.6	TSP/QSE Telemetry Restoration

(1)	Telemetered data shall be provided continuously.  Real-Time data restoration shall comply with Nodal Operating Guide Sections 7.3.3, Data from WAN Participants to ERCOT, and 7.3.4, Resolving Real-Time Data Issues that affect ERCOT Network Security Analysis.

(2)	Some data may be more essential to the State Estimator solution.  ERCOT shall inform the TSP or QSE if, in the sole opinion of ERCOT, a data item is essential and needs to be repaired as quickly as possible.  QSEs and TSPs shall make repair procedures and records available to ERCOT upon request.  When ERCOT notifies a data provider that a data element is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, do one of the following:

(a) 	Calibrate or repair the failing equipment;

(b) 	Request an outage to schedule calibration or repair of the failing equipment;

(c) 	Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame; or

(d)	Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.

(3)	Before ERCOT requests review or re-calibration of a problem piece of equipment, it shall discuss the problem with the data provider to attempt to arrive at a consensus decision on the most appropriate action.

### 3.10.7.5.7	Calibration, Quality Checking, and Testing

(1)	It is the responsibility of the equipment owner to insure that calibration, testing, and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds the requirements specified in this Section 3.10.7.5, Telemetry Requirements, for both the overall system and for individual equipment where detailed herein.  Coordination with ERCOT of outages required for these activities is also the responsibility of the owner.

### 3.10.7.5.8	Inter-Control Center Communications Protocol (ICCP) Links

#### 3.10.7.5.8.1	Data Quality Codes

(1)	Market Participants shall provide documentation to ERCOT describing their native system quality codes and defining the conversion of their quality codes into the ERCOT-defined quality codes.

(2)	Statuses and analogs telemetered to ERCOT shall be identified with the following quality codes:

(a)	Valid – Represents an analog or status the TSP or QSE considers valid.

(b)	Manual – Represents an analog or status entered manually at the Market Participant (i.e., not received from the field electronically).

(c)	Calculated – Represents an analog point that the TSP or QSE calculates.

(d)	Suspect – Represents an analog or status of which the TSP or QSE is unsure of the validity

(e)	Invalid – Represents an analog or status that the Market Participant has identified as out of reasonability limits.

(f)	Com_fail – Informs ERCOT that due to communications failure, the analog or status provided ERCOT is not current.

#### 3.10.7.5.8.2	Reliability of ICCP Associations

(1)	Each Market Participant using Inter-Control Center Communications Protocol (ICCP) associations must achieve a monthly availability of 98%, excluding approved Planned Outages.  Availability shall be measured based on end-to-end connectivity of the communications path and the passing of configured data at the scheduled periodicity.  To meet the 98% monthly availability, each Market Participant should establish a process to coordinate downtime for ICCP associations and database maintenance.  High availability configuration as allowed by the ERCOT Nodal ICCP Communications Handbook should be treated as a single association to achieve this availability measure.

### 3.10.7.5.9	ERCOT Requests for Telemetry

(1)	ERCOT is required to protect Transmission Facilities operated at 60 kV or above from damage.  To do this, ERCOT may request that additional telemetry be installed, while attempting to minimize adding equipment to as few locations as practicable.

(2)	ERCOT may request additional telemetry when it determines that network observability or the measurement redundancy is not adequate to produce acceptable State Estimator results.

(3)	Prior to making a request for additional telemetry, ERCOT shall provide evidence supporting a congestion or reliability problem requiring additional observability and define expected improvements in ERCOT System observability needed.  If the request is for telemetry additions at more than one location, ERCOT shall prioritize the requested additions.

(4)	No later than 60 days after receipt of a request for additional telemetry, the TSP or QSE shall:

(a)	Accept ERCOT’s request for additional telemetry and notify ERCOT of the implementation schedule, which shall be no later than 18 months following the receipt of the request for additional telemetry;

(b)	Provide an alternative proposal to ERCOT, for implementation no later than 18 months following the receipt of the request for additional telemetry, that meets the requirements described by ERCOT;

(c)	Propose a normal topology change by changing normal status of switch(es) in the area that would eliminate the security violations that are ERCOT’s concern;

(d)	Indicate that the requested telemetry point is at a location where the TSP or QSE does not have the authority to install the requested telemetry.  For points on privately owned facilities connected to the ERCOT Transmission Grid, an attempt will be made to facilitate ERCOT's telemetry request;

(e)	Provide ERCOT an analysis of the cost to comply with the request, so that, ERCOT can perform a cost justification with respect to the LMP market; or

(f)	If the TSP or QSE disagrees with the request, the TSP or QSE may request that ERCOT withdraw its request for additional telemetry.

[NPRR979: Replace paragraph (4) above with the following upon system implementation of NPRR857:] (4) No later than 60 days after receipt of a request for additional telemetry, the TSP, DCTO, or QSE shall: (a) Accept ERCOT’s request for additional telemetry and notify ERCOT of the implementation schedule, which shall be no later than 18 months following the receipt of the request for additional telemetry; (b) Provide an alternative proposal to ERCOT, for implementation no later than 18 months following the receipt of the request for additional telemetry, that meets the requirements described by ERCOT; (c) Propose a normal topology change by changing normal status of switch(es) in the area that would eliminate the security violations that are ERCOT’s concern; (d) Indicate that the requested telemetry point is at a location where the TSP, DCTO, or QSE does not have the authority to install the requested telemetry. For points on privately owned facilities connected to the ERCOT Transmission Grid, an attempt will be made to facilitate ERCOT's telemetry request; (e) Provide ERCOT an analysis of the cost to comply with the request, so that, ERCOT can perform a cost justification with respect to the LMP market; or (f) If the TSP, DCTO, or QSE disagrees with the request, the TSP, DCTO, or QSE may request that ERCOT withdraw its request for additional telemetry.

(5) 	If ERCOT rejects an alternative proposal pursuant to paragraph (4)(b), (c), or (f) above, the TSP or QSE may appeal the original request to TAC within 30 days of receiving notice of ERCOT’s rejection.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.  Notwithstanding the foregoing, a TSP or QSE is not required to provide telemetry measurements from a location not owned by that TSP or QSE if the location owner does not grant access to the TSP or QSE for the purpose of obtaining such measurements.  ERCOT shall report such cases to the IMM.

[NPRR979: Replace paragraph (5) above with the following upon system implementation of NPRR857:] (5) If ERCOT rejects an alternative proposal pursuant to paragraph (4)(b), (c), or (f) above, the TSP, DCTO, or QSE may appeal the original request to TAC within 30 days of receiving notice of ERCOT’s rejection. If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP, DCTO, or QSE may present its appeal to the ERCOT Board. Notwithstanding the foregoing, a TSP, DCTO, or QSE is not required to provide telemetry measurements from a location not owned by that TSP, DCTO, or QSE if the location owner does not grant access to the TSP, DCTO, or QSE for the purpose of obtaining such measurements. ERCOT shall report such cases to the IMM.

### 3.10.7.5.10	ERCOT Requests for Redundant Telemetry

(1)	ERCOT shall maintain redundancy on monitored non-Load substations.

(2)	ERCOT shall identify new telemetry required to maintain N-1 observability on monitored non-Load substations.  The following conditions shall be used to determine what additional telemetry is required:

(a)	Inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(b)	Inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(c)	Inability of ERCOT to monitor loading on Transmission Facilities designated as important to transmission reliability by ERCOT.

(3)	ERCOT may request additional MW, MVAr and voltage telemetry to make these measurements redundant.  In this request, ERCOT shall identify these measurements, and the contingency/overload condition and the unit dispatch that makes this a concern.  If the request is for telemetry at multiple locations, ERCOT shall prioritize the requested additions.

(4)	Except as provided in paragraph (5) below, no later than 60 days after receipt of a request for additional telemetry, a TSP or QSE shall:

(a)	Accept ERCOT’s request for additional telemetry and notify ERCOT of the implementation schedule, which shall be no later than 18 months following the receipt of the request for additional telemetry; or

(b)	Propose an alternative solution that will serve the same purpose as the ERCOT identified telemetry additions, with a proposed implementation no later than 18 months following the receipt of the request for additional telemetry;

(5)	In cases where the request is based on the availability rate of an existing telemetry point, no later than 30 days after receipt of a request for additional telemetry, the TSP or QSE shall:

(a)	Provide a plan to improve the availability rate of the identified telemetry to meet the requirements of paragraph (1)(b)(i) of Section 3.10.7.5.4, General Telemetry Performance Criteria, and paragraph (3) of Section 3.10.7.5.5, Supplemental Telemetry Performance Criteria;

(b)	Provide documentation for why the improvements set forth in paragraph (a) above cannot be accomplished;

(c)	Identify and propose a schedule of equipment installations or maintenance to be completed no later 18 months following the receipt of the request for additional telemetry that would, as a result, change the classification of the Transmission Element identified by ERCOT; or

(d)	Indicate that the facility for which telemetry is being requested is not owned or covered by an agreement that allows the requested party to install the additional telemetry.

(6) 	If ERCOT rejects an alternative solution proposed pursuant to paragraph (4) or (5) above, the TSP or QSE may appeal the original request to TAC within 30 days of receiving notice of ERCOT’s rejection.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.  Notwithstanding the foregoing, a TSP or QSE is not required to provide telemetry measurements from a location not owned by that TSP or QSE if the location owner does not grant access to the TSP or QSE for the purpose of obtaining such measurements.  ERCOT shall report such cases to the IMM.3.10.9	State Estimator StandardsRequirements

C subcommitt

(1)	The appropriate TAC subcommittee shall coordinate with Market Participants to ensure a common understanding of the level of State Estimator performance required to enable LMP calculation and address the State Estimator’s ability to detect, correct, or otherwise accommodate communications system failures, failed data points, stale data condition codes, and missing or inaccurate measurements to the extent these capabilities contribute to LMP accuracy and State Estimator performance or as needed to meet reliability requirements.

3.10.9.1	Considerations for State Estimator Requirements

(1)	In maintaining the State Estimator requirements, the following may be considered:

(a)	Desired confidence levels of State Estimator results;

(b)	Measurement requirements to estimate power injections and withdrawals at transmission voltage Electrical Buses defined in the SCED transmission model, which may provide for variations in criteria based on:

(i)	The number of Transmission Elements connected to a given transmission voltage Electrical Bus;

(ii)	The peak demand of the Load connected to a transmission voltage Electrical Bus;

(iii)	The total of Resource capacity connected to a transmission voltage Electrical Bus;

(iv)	The nominal transmission voltage level of an Electrical Bus;

(v)	The number of Electrical Buses with injections or withdrawals along a circuit between currently monitored transmission voltage Electrical Bus;

(vi)	Connection of Loads along a continuous, non-branching circuit that may be combined for modeling purposes;

(vii)	The quantity of Load at an Electrical Bus that may have its connection to the transmission system automatically transferred to an Electrical Bus other than the one to which it is normally connected (rollover operation);

(vii)	Electrical proximity to more than one Resource Node;

(viii)	Degree or quality of continued observability following the loss of telemetry measurements resulting from a common mode failure of telemetry-related equipment (i.e., an N-1 telemetry condition); and

(ix)	Other parameters or circumstances, as appropriate;

(c)	Sensitivity of State Estimator results with respect to variations in input parameters;

(d)	Reasonable safeguards to assure State Estimator results are calculated on a non-discriminatory basis; and

(e)	Other parameters as deemed appropriate.

### 3.10.9.2	State Estimator Data

(1)	ERCOT uses a State Estimator to produce Load flow base cases, which are used to analyze the reliability of the ERCOT Transmission Grid.  Accurate and redundant telemetry and an accurate transmission power system model are required by the State Estimator in order to produce an optimal estimation of the transmission power system state.  State Estimator results are used in contingency analysis, congestion management, and other network analysis Real-Time sequence functions.

### 3.10.9.3	Telemetry Status and Analog Measurements Data

(1)	Good telemetry status and analog measurements data for the transmission power system together with an accurate model of the ERCOT System are processed by the State Estimator to provide an optimal estimate of the ERCOT System state at a given point in time while filtering minor measurement errors and detecting gross errors.  The quality and availability of telemetry provided to ERCOT is important to the performance of the ERCOT State Estimator.

(2)	Telemetry is not needed at every node of the ERCOT System to arrive at a good estimate of the ERCOT System’s state. State Estimator performance must meet the performance requirements set forth in Section 3.10.9.4, State Estimator Performance Requirements, unless otherwise provided for in the Operating Guides.

(3)	Beyond general telemetry performance criteria there are more stringent criteria needed at locations where state estimates are critically important, including, but not limited to, locations where reliability, security, and market impacts are of heightened concern.

### 3.10.9.4	State Estimator Performance Requirements

(1)	The State Estimator shall converge 98% of runs during a one month period.

(2)	For MW flows on Transmission Elements identified by ERCOT as causing 80% of congestion costs in the latest year for which data is available, the residual difference between State Estimator results and power flow results shall be less than 3% of the associated element Emergency Rating on at least 95% of samples measured in a one month period.

(3)	For Transmission Elements identified by ERCOT as causing 80% of all congestion costs in the latest year for which data is available, the difference between the telemetry value (MW) and the State Estimator value (MW) shall be less than 3% of the associated element Emergency Rating on at least 95% of samples measured in a one month period.

(4)	For the 20 most important station voltage points, as designated by ERCOT and approved by ROS, the telemetered voltage minus State Estimator voltage shall be within 2% of the telemetered voltage measurement for at least 95% of samples measured during a one month period.

(5)	For all Transmission Elements 100 kV and above, the difference between the State Estimator solution (MW) and the SCADA measurement will be less than 10 MW or 10% of the associated Emergency Rating (whichever is greater) on 99.5% of samples measured during a one month period.  ERCOT shall report all equipment failing this test to the associated TSP who shall repair such equipment no later than 10 days following detection by ERCOT.

(6)	ERCOT shall post the State Estimator performance requirements contained in this Section on the MIS Secure Area.

### 3.10.9.5	ERCOT Directives

(1)	ERCOT shall work with the TSP or QSE to resolve telemetry and/or model problems in accordance with telemetry requirements prior to directing additional equipment.

(2)	In the event of failure to meet the requirements in paragraphs (2) or (3) of Section 3.10.9.4, State Estimator Performance Requirements, ERCOT may direct additional telemetry to be installed on elements contributing most to 80% of congestion costs for the latest year for which data is available.  If the TSP or QSE disputes the request for additional telemetry, pursuant to paragraph (4) of Section 3.10.7.5.9, the TSP or QSE may provide an alternative proposal.

(3)	ERCOT shall enforce the requirements of paragraph (5) of Protocol Section 3.10.7.5.2, Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows, by alarming any sum of flow around a bus that is more than (a) 5% of the largest normal line rating connected to the bus, or (b) 5 MW, whichever is greater, and requesting that the applicable TSP or QSE correct the failure.

(4)	ERCOT shall consider the quality codes sent by the data provider in determining how confidence factors are assigned for the data to be used in the State Estimator.  Valid and manual quality codes as defined in Section 3.10.7.5.8.1, Data Quality Codes, shall be considered as good quality.  Quality codes sent as not good quality shall be considered at a lower confidence.

3.10.9.6	Telemetry and State Estimator Performance Monitoring

(1)	ERCOT shall monitor the performance of the State Estimator, Network Security Analysis, SCED, and LMP Calculator.  ERCOT shall post a monthly report of these items on the MIS Secure Area.  ERCOT shall notify affected TSPs and QSEs of any lapses of observability of the transmission system.

[NPRR857: Replace paragraph (1) above with the following upon system implementation:] (1) ERCOT shall monitor the performance of the State Estimator, Network Security Analysis, SCED, and LMP Calculator. ERCOT shall post a monthly report of these items on the MIS Secure Area. ERCOT shall notify affected TSPs, QSEs, or DCTOs of any lapses of observability of the transmission system.