| NPRR Number | 1034 | NPRR Title | Frequency-Based Limits on DC Tie Imports or Exports |
| --- | --- | --- | --- |
| Date of Decision |  | January 14, 2021 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation |  |
| Priority and Rank Assigned |  | Priority – 2021; Rank – 3280 |  |
| Nodal Protocol Sections Requiring Revision |  | 4.4.4, DC Tie Schedules 4.4.4.3, Frequency-Based Limits on DC Tie Imports or Exports (new) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) creates new Section 4.4.4.3 to allow ERCOT to establish import or export limits on Direct Current Ties (DC Ties) to avoid the risk of any unacceptable frequency deviation that may be identified in the event of an unexpected loss of one or more DC Ties when importing or exporting. Revisions to Section 4.4.4 would allow ERCOT to curtail DC Tie Schedules on a DC Tie on a last-in-first-out basis when necessary to address this risk. The last-in-first-out curtailment methodology is consistent with current practice documented in the ERCOT DC Tie Operating Procedure Manual. ERCOT would be required to post on the Market Information System (MIS) Public Area the operating conditions and associated limits that it would expect to use. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NPRR is proposed in accordance with the May 23, 2017, order of the Public Utility Commission of Texas (PUCT) in Project No. 46304, Oversight Proceeding Regarding ERCOT Matters Arising Out of PUC Docket No. 45624 Relating to DC Tie Project Proposed by Southern Cross Transmission, LLC, which requires ERCOT to address a number of issues as a condition for the energization of the DC Tie project proposed by Southern Cross Transmission LLC (“Southern Cross Transmission”). As proposed, the Southern Cross DC Tie would be capable of importing 2,000 MW or exporting 2,100 MW. The PUCT’s Directive 9 in the order requires ERCOT to “evaluate what modifications to existing and additional Ancillary Services, if any, are necessary for the reliable interconnection of the Southern Cross DC tie.” ERCOT’s studies evaluating the potential need for Ancillary Services associated with the Southern Cross DC Tie identified a risk of unacceptable frequency overshoot in the event of the loss of the Southern Cross DC Tie when exporting above certain levels under certain operating conditions. ERCOT’s evaluation further identified likely future procurement of incremental Ancillary Services as a means to address the frequency overshoot concern. Southern Cross Transmission proposes this NPRR as a more efficient solution for the entire market by establishing limits on certain DC Tie transfers when necessary to address the risk of frequency overshoot, rather than requiring procurement of additional Ancillary Services. |  |
| Credit Work Group Review |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR1034 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |
| PRS Decision |  | On 8/13/20, PRS voted via roll call to table NPRR1034 and refer the issue to ROS. There was one abstention from the Investor Owned Utility (IOU) (Lone Star Transmission) Market Segment. All Market Segments were present for the vote. On 11/11/20, PRS voted unanimously via roll call to recommend approval of NPRR1034 as amended by the 10/22/20 SCT comments. All Market Segments were present for the vote. On 12/10/20, PRS voted unanimously via roll call to table NPRR1034. All Market Segments were present for the vote. On 1/14/21, PRS voted via roll call to endorse and forward to TAC the 12/10/20 PRS Report and Impact Analysis for NPRR1034 with a recommended priority of 2021 and rank of 3280. There was one abstention from the Independent Power Marketer (IPM) (Morgan Stanley) Market Segment. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 8/13/20, there was no discussion. On 11/11/20, there was no discussion. On 12/10/20, ERCOT Staff requested additional time to develop the Impact Analysis for NPRR1034. On 1/14/21, participants reviewed the Impact Analysis. |  |

| Sponsor |  |
| --- | --- |
| Name | Mark Bruce |
| E-mail Address | mark.bruce@cratyl.us |
| Company | Cratylus Advisors, on behalf of Southern Cross Transmission LLC |
| Phone Number |  |
| Cell Number | 512-810-1516 |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-636-1852 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ROS 090920 | Requested PRS continue to table NPRR1034 to allow for review by the Performance, Disturbance, Compliance Working Group (PDCWG) |
| SCT 102220 | Proposed language to allow ERCOT to tailor reliability-oriented import/export restrictions to the appropriate Operating Hours under relevant system conditions |
| ROS 110920 | Endorsed NPRR1034 as amended by the 10/22/20 SCT comments |
| ERCOT 120920 | Proposed an alternative schedule for the development of the Impact Analysis |

Market Rules Notes

Please note the baseline Protocol language in the following section(s) has been updated to reflect the incorporation of the following NPRR(s) into the Protocols:

- NPRR999, DC Tie Ramp Limitations (incorporated 11/1/20)

  - Section 4.4.4

- NPRR1008, RTC – NP 4: Day-Ahead Operations (incorporated 1/1/21)

  - Section 4.4.4

- NPRR1030, Modify Allocator for CRR Auction Revenue Distribution (incorporated 9/1/20)

  - Section 4.4.4

- NPRR1039, Replace the Term MIS Public Area with ERCOT Website (incorporated 1/1/21)

  - Section 4.4.4

Please note that the following NPRR(s) also propose revisions to the following section(s):

- NPRR1054, Removal of Oklaunion Exemption Language

  - Section 4.4.4

Proposed Protocol Language Revision

4.4.4	DC Tie Schedules

(1)	All schedules between the ERCOT Control Area and a non-ERCOT Control Area(s) over Direct Current Tie(s) (DC Ties(s)), must be implemented under these Protocols, any applicable North American Electric Reliability Corporation (NERC) Reliability Standards, North American Energy Standards Board (NAESB) Practice Standards, and operating agreements between ERCOT and the Comision Federal de Electricidad (CFE).

[NPRR857: Replace paragraph (1) above with the following upon system implementation:] (1) All Direct Current Tie (DC Tie) Schedules between the ERCOT Control Area and a non-ERCOT Control Area(s) must be implemented in accordance with these Protocols, any applicable North American Electric Reliability Corporation (NERC) Reliability Standards, North American Energy Standards Board (NAESB) Practice Standards, and operating agreements between ERCOT and the appropriate operating authority for the non-ERCOT Control Area.

(2)	A DC Tie Schedule for hours in the Operating Day corresponding to an Electronic Tag (e-Tag) that is reported to ERCOT before 1430 in the Day-Ahead creates a capacity supply for the equivalent Resource or an obligation for the equivalent Load of the DC Tie in the DRUC process.  DC Tie Schedules corresponding to e-Tags approved after 1430 in the Day-Ahead for the Operating Day create a capacity supply or obligation in any applicable HRUC processes.  DC Tie Schedules corresponding to e-Tags approved after the Reliability Unit Commitment (RUC) snapshot are considered in the Adjustment Period snapshot in accordance with the market timeline.

(3)	A QSE that is an importer into ERCOT through a DC Tie in a Settlement Interval under an approved e-Tag must be treated as a Resource at that DC Tie Settlement Point for that Settlement Interval.

(4)	A QSE that is an exporter from ERCOT through a DC Tie in a Settlement Interval under an approved e-Tag must be treated as a Load at the DC Tie Settlement Point for that Settlement Interval and is responsible for allocated Transmission Losses, Unaccounted for Energy (UFE), System Administration Fee, and any other applicable ERCOT fees.  This applies to all exports across the DC Ties except those that qualify for the Oklaunion Exemption.

(5)	ERCOT shall approve any e-Tag that does not exceed the available physical capacity of the DC Tie and any limits supplied the non-ERCOT Control Area for the time period for which the e-Tag is requested unless a DC Tie Curtailment Notice is in effect for the particular DC Tie for which the e-Tag request is made.  While a DC Tie Curtailment Notice is in effect, ERCOT will deny any additional e-Tag requests that would exacerbate the transmission security violations that led to that DC Tie Curtailment Notice.  Notwithstanding the foregoing, ERCOT shall deny or curtail any e-Tag over any of the DC Ties if necessary to avoid causing any Entity in the ERCOT Region that is not a “public utility” as defined in the Federal Power Act (FPA), including ERCOT, to become such a public utility.  If ERCOT determines that it is necessary to deny or curtail e-Tags in order to prevent any Entity from becoming a “public utility,” it shall provide notice of that determination by posting an operations message to the ERCOT website and issuing a Market Notice.

[NPRR999: Replace paragraph (5) above with the following upon project implementation of the Intra-Hour Variability (iCAT) Tool:] (5) ERCOT shall approve any e-Tag that does not exceed the available physical capacity of the DC Tie, system ramping capability, and any limits supplied by the non-ERCOT Control Area for the time period for which the e-Tag is requested unless a DC Tie Curtailment Notice is in effect for the particular DC Tie for which the e-Tag request is made; otherwise, ERCOT shall deny the e-Tag. While a DC Tie Curtailment Notice is in effect, ERCOT will deny any additional e-Tag requests that would exacerbate the transmission security violations that led to that DC Tie Curtailment Notice. Notwithstanding the foregoing, ERCOT shall deny or curtail any e-Tag over any of the DC Ties if necessary to avoid causing any Entity in the ERCOT Region that is not a “public utility” as defined in the Federal Power Act (FPA), including ERCOT, to become such a public utility. If ERCOT determines that it is necessary to deny or curtail e-Tags in order to prevent any Entity from becoming a “public utility,” it shall provide notice of that determination by posting an operations message to the ERCOT website and issuing a Market Notice.

(6)	ERCOT shall perform schedule confirmation with the applicable non-ERCOT Control Area(s) and shall coordinate the approval process for the e-Tags for the ERCOT Control Area.  An e-Tag for a schedule across a DC Tie is considered approved if:

(a)	All Control Areas and Transmission Service Providers (TSPs) with approval rights approve the e-Tag (active approval); or

[NPRR857: Replace paragraph (a) above with the following upon system implementation:] (a) All Control Areas and Direct Current Tie Operators (DCTOs) with approval rights approve the e-Tag (active approval); or

(b)	No Entity with approval rights over the e-Tag has denied it, and the approval time window has ended (passive approval).

(7)	Using the DC Tie Schedule information corresponding to e-Tags submitted by QSEs, ERCOT shall update and maintain a Current Operating Plan (COP) for each DC Tie for which the aggregated DC Tie Schedules for that tie show a net export out of ERCOT for the applicable interval.  When the net energy schedule for a DC Tie indicates an export, ERCOT shall treat the DC Tie as an Off-Line Resource and set the High Sustained Limit (HSL) and Low Sustained Limit (LSL) for that DC Tie Resource to zero.  ERCOT shall monitor the associated Resource Status telemetry during the Operating Period.  When the net energy schedule for a DC Tie shows a net import, the Resource HSL, High Ancillary Service Limit (HASL) and LSL must be set appropriately, considering the resulting net import.

[NPRR1008: Replace paragraph (7) above with the following upon system implementation of the Real-Time Co-Optimization (RTC) project:] (7) Using the DC Tie Schedule information corresponding to e-Tags submitted by QSEs, ERCOT shall update and maintain a Current Operating Plan (COP) for each DC Tie for which the aggregated DC Tie Schedules for that tie show a net export out of ERCOT for the applicable interval. When the net energy schedule for a DC Tie indicates an export, ERCOT shall treat the DC Tie as an Off-Line Resource and set the High Sustained Limit (HSL) and Low Sustained Limit (LSL) for that DC Tie Resource to zero. ERCOT shall monitor the associated Resource Status telemetry during the Operating Period. When the net energy schedule for a DC Tie shows a net import, the Resource HSL and LSL must be set appropriately, considering the resulting net import.

(8)	A QSE exporting from ERCOT and/or importing to ERCOT through a DC Tie shall:

(a)	Secure and maintain an e-Tag service to submit e-Tags and monitor e-Tag status according to NERC requirements;

(b)	Submit e-Tags for all proposed transactions; and

(c)	Implement backup procedures in case of e-Tag service failure.

(9)	ERCOT shall post a notice to the MIS Certified Area when a confirmed e-Tag is downloaded, cancelled, or curtailed by ERCOT’s systems.

(10)	ERCOT shall use the DC Tie e-Tag MW amounts for Settlement.  The DC Tie operator shall communicate deratings of the DC Ties to ERCOT and other affected regions and all parties shall agree to any adjusted or curtailed e-Tag amounts.

[NPRR857: Replace paragraph (10) above with the following upon system implementation:] (10) ERCOT shall use the DC Tie e-Tag MW amounts for Settlement. The DCTO shall communicate deratings of the DC Ties to ERCOT and other affected regions and all parties shall agree to any adjusted or curtailed e-Tag amounts.

(11)	DC Tie Load is considered as Load for daily and hourly reliability studies, and settled as Adjusted Metered Load (AML).  DC Tie Load is curtailed prior to other Load on the ERCOT System as described below, and during Energy Emergency Alert (EEA) events as set forth in Section 6.5.9.4.2, EEA Levels.

(12)	DC Tie Load shall neither be curtailed by ERCOT during the Adjustment Period, nor for more than one hour at a time, except for the purpose of maintaining reliability, or as indicated in paragraphs (13), (14), (15), and (16) below.

(13)	If a system operator in a non-ERCOT Control Area requests curtailment of a DC Tie Schedule due to an actual or anticipated emergency in its Control Area, ERCOT may curtail the DC Tie Schedule.  If the DC Tie Schedule is curtailed, ERCOT shall post a DC Tie Curtailment Notice to the ERCOT website as soon as practicable.

(14)	If a DC Tie experiences an Outage, ERCOT may curtail DC Tie Schedules that are, or that are expected to be, affected by the Outage based on system conditions and expected restoration time of the Outage.  ERCOT shall post a DC Tie Curtailment Notice to the ERCOT website as soon as practicable.  Updated DC Tie limits shall be posted as required in paragraph (1) of Section 3.10.7.7, DC Tie Limits.

(15)	If market-based congestion management techniques embedded in Security-Constrained Economic Dispatch (SCED) as specified in these Protocols will not be adequate to resolve one or more transmission security violations that would be fully or partially resolved by the curtailment of DC Tie Load and, in ERCOT’s judgment, no approved Constraint Management Plan (CMP) is adequate to resolve those violations, ERCOT may instruct Resources to change output and, if still necessary, curtail DC Tie Load to maintain reliability and shall post a DC Tie Curtailment Notice to the ERCOT website as soon as practicable.  The quantity of DC Tie Load to be curtailed shall be the minimum required to resolve the constraint(s) after the other remediation actions described above have been taken.

(16)	ERCOT may curtail DC Tie Schedules as necessary to ensure that any Entity in the ERCOT Region that is not a “public utility” as defined in the FPA, including ERCOT, does not become such a public utility.

(17)	ERCOT may curtail DC Tie Schedules on a DC Tie on a last-in-first-out basis when ERCOT determines that one or more DC Tie Schedules on that DC Tie would exceed a limit established pursuant to paragraph (1) of Section 4.4.4.3, Frequency-Based Limits on DC Tie Imports or Exports.

(18)	Market Participants shall not engage in DC Tie export transactions that are reasonably expected to be uneconomic in consideration of all costs and revenues associated with the transaction, excluding Congestion Revenue Right (CRR) Auction Revenue Distribution (CARD) and CRR Balancing Account (CRRBA) allocations.

[NPRR1030: Delete paragraph (18) above upon system implementation.]

- 4.4.4.3	Frequency-Based Limits on DC Tie Imports or Exports

(1)  	ERCOT may establish import or export limits applicable to any DC Tie to mitigate the risk of significant frequency deviation due to the unexpected loss of that DC Tie.  ERCOT shall identify the operating conditions and limits it would expect to use in a posting to the MIS Public Area.