## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
February 4th, 2021

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs & IMFR
    4 FMEs in the month of November
    1 FME in the month of December
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 01/13/2021
  ERCOT study proposal for RRS limits – Status report
  Annual ERCOT Inertia analysis report
  Update on BAL-001-TRE, SAR 12
  ERCOT Reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 4 FMEs in November
  11/7/2020 18:05:14
    Loss of 474 MW
    Interconnection Frequency Response: 729 MW/0.1 Hz
    6 of 34 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 34 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  11/15/2020 10:47:36
    Loss of load of 579 MW
    Interconnection Frequency Response: 1485 MW/0.1 Hz
    79 of 209 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    64 of 209 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  11/16/2020 09:51:37
    Loss of 1034 MW
    Interconnection Frequency Response: 1641 MW/0.1 Hz
    3 of 37 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 37 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  11/21/2020 00:20:06
    Loss of load of 734 MW
    Interconnection Frequency Response: 789 MW/0.1 Hz
    7 of 33 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    7 of 33 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Frequency Measurable Events
There was 1 FME in December
  12/10/2020 14:34:32
    Loss of 571 MW
    Interconnection Frequency Response: 984 MW/0.1 Hz
    22 of 64 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    21 of 64 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 8: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1101.96 MW/0.1Hz
Frequency Response Obligation (FRO): 425 MW/0.1 Hz

## Slide 9: Frequency Control Report
October 2020

## Slide 10: CPS1 Performance

## Slide 11: RMS1 Performance of ERCOT Frequency

## Slide 12: Frequency Profile Analysis

## Slide 13: Time Error Corrections

## Slide 14: ERCOT Total Energy
Notes: 31,210,036 MWh

## Slide 15: ERCOT Total Energy from Wind Generation
Notes: 7,264,919 MWh

## Slide 16: ERCOT % Energy from Wind Generation
Notes: 23.28%

## Slide 17: ERCOT Total Energy from Solar Generation
Notes: 682,932 MWh

## Slide 18: ERCOT % Energy from Solar Generation
Notes: 2.19%

## Slide 19
Questions?