## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
March 4th, 2021

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs & IMFR
    4 FMEs in the month of January
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 01/13/2021
  Update on BAL-001-TRE, SAR 12
  OBDRR25 – ERCOT RFP status update
  ERCOT Reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 4 FMEs in January
  1/3/2021 11:34:14
    Loss of 776 MW
    Interconnection Frequency Response: 1094 MW/0.1 Hz
    5 of 45 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    7 of 45 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  1/6/2021 18:20:35
    Loss of load of 774 MW
    Interconnection Frequency Response: 956 MW/0.1 Hz
    10 of 45 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    9 of 45 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  1/11/2021 13:03:26
    Loss of 757 MW
    Interconnection Frequency Response: 1147 MW/0.1 Hz
    5 of 52 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 52 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  1/28/2021 14:21:20
    Loss of load of 718 MW
    Interconnection Frequency Response: 1197 MW/0.1 Hz
    9 of 53 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    8 of 53 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 471 MW/0.1 Hz
IMFR Performance currently 1027.82 MW/0.1Hz

## Slide 8: Frequency Control Report
January 2021

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy
Notes: 31,210,036 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes: 7,264,919 MWh

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 23.28%

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 682,932 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 2.19%

## Slide 18
Questions?