## Slide 1
ERS Deployment Estimation Error and Potential Price Correction – Analysis of Price and Settlement Impacts
David Maggio
Director, Market Design & Analytics
TAC
March 24, 2021

## Slide 2: Background
At 00:17 on February 15, 2021, ERCOT began sending Extensible Markup Language (XML) messages to deploy Emergency Response Service (ERS) resources due to Energy Emergency Alert (EEA) conditions.
The Market Management System (MMS) began estimating the amount of ERS deployed in order to allow the software to determine the Real-Time On-Line Reliability Deployment Price Adders (RTORDPAs) at the 00:20 Security-Constrained Economic Dispatch (SCED) interval.
  Per Protocol 6.5.7.3.1(2)(d), estimated ERS deployment is a component that feeds the pricing run used to determine RTORDPAs.
  ERS deployment estimations are based on:
    contracted ERS capacities;
    type of ERS being provided;
    the relevant time period; and
    an approximated restoration that is linearly ramped over a 4.5 hour period.
Because of the duration of the EEA event, ERS resources remained deployed until their deployment obligations were exhausted entirely.

## Slide 3: Issues
ERCOT has discovered that the MMS software contains programming errors that resulted in incorrect MW amounts being used for the estimated deployed ERS component of the RTORDPA for certain SCED intervals on Operating Day (OD) February 15, 2021.
ERCOT has identified three specific errors, primarily related to estimating the exhaustion of ERS deployment obligations:
  The logic for exhaustion calculated ERS-10 and ERS-30 deployments starting from the XML deployment instruction, rather than the end of the 10-minute (for ERS-10) or 30-minute (for ERS-30) ramp times;
  The logic improperly treated Weather-Sensitive (WS) ERS as having the same deployment obligation time as Non-Weather-Sensitive (NWS) ERS; and
  The logic did not properly account for the fact that some ERS resources may have an obligation for only a subset of the time periods within the overall ERS deployment timeframe.
These issues have been in place since the implementation of the RTORDPAs. However, this is the first instance of associated pricing errors.

## Slide 4: Issue: RTORDPA logic did not reflect actual ERS performance obligations
Protocol Section 3.14.3.3(2) provides that ERS “[d]eployment obligation time does not include the ramp time.”
For certain SCED intervals on OD February 15, 2021, the logic for exhaustion calculated ERS-10 and ERS-30 deployments starting from the XML deployment instruction, rather than the end of the 10-minute (for ERS-10) or 30-minute (for ERS-30) ramp times—i.e., the RTORDPA logic began accounting for deployed ERS MWs too early, and therefore didn’t include deployed ERS MWs in the RTORDPA during SCED intervals in which ERS Resources continued to have deployment obligations.
Result: The RTORDPA calculation for SCED intervals on OD February 15, 2021 that fell towards the end of ERS deployment obligation times under-counted the estimated deployed ERS MWs.
This error had the most significant impact on RTORDPAs for this event.

## Slide 5: Issue: RTORDPA logic improperly calculated WS ERS deployment obligation times
Protocol Section 3.14.3.3(3)(b)(ii) provides, “The duration of a Weather-Sensitive ERS Load’s deployment obligation time for a single event shall be a maximum of three hours.”
For certain SCED intervals on OD February 15, 2021, the RTORDPA logic improperly treated WS ERS as having the same deployment obligation time as NWS ERS.
  WS ERS has a shorter maximum obligation time in a single event (3 hours) than NWS ERS (12 hours).
Result: WS ERS MWs were included in the RTORDPA calculation for certain SCED intervals on February 15, 2021 when there were no WS ERS deployment obligations.

## Slide 6: Issue: Other RTORDPA logic errors
For certain SCED intervals on OD February 15, 2021, the RTORDPA logic did not properly account for the fact that some ERS resources may have had an obligation for only a subset of the time periods within the overall ERS deployment timeframe.
Result: Similar to the first issue, the RTORDPA calculation for SCED intervals on OD February 15, 2021, that fell towards the end of ERS deployment obligation times under-counted the estimated deployed ERS MWs.
For certain SCED intervals on OD February 15, 2021, the logic used to estimate ERS deployments over time contained a numeral conversion error that impacted precision.
Result: This small loss in precision resulted in minor errors in the ERS MW values as the ERS deployment persisted throughout OD February 15, 2021. These errors varied in direction and were ~2 MW or less in magnitude.

## Slide 7: Estimated ERS deployment differences for OD February 15, 2021
Chart: ERS Deployment Modeling for the Pricing Run for OD February 15, 2021 Production vs. Rerun
The comparison shows the SCED intervals with estimated ERS deployment differences on OD February 15, 2021, up until adjustments were made to the RTORDPA process per the Public Utility Commission of Texas order issued on February 15, 2021 in Project No. 51617.
  Following the adjustments, any remaining incremental error in the ERS deployment estimation would not have impacted pricing.

## Slide 8: Estimated RTORDPA differences for OD February 15, 2021
For the relevant time window, only a subset of the SCED intervals saw a change in price (79 of 186 SCED intervals).
For the 79 identified SCED intervals, the average change in RTORDPA was an increase of ~$58/MWh.
Chart: RTORDPA for OD February 15, 2021 Production vs. Rerun

## Slide 9: Estimated price correction impact
ERCOT’s analysis used original settled quantities with revised prices based on RTM reruns, with the corrected estimated ERS deployments and RTORDPAs.
  The Settlement data was recalculated using the Real-Time Settlement Point Prices (RTSPPs) and the Real-Time Price for Energy Metered for Resources (RTRMPRs), which would be updated as part of the price correction.
  Note: The Settlement data provided herein is estimated; final Settlement amounts may change.
All Settlement amounts are net amounts due to/from ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled net amount due to/from ERCOT.

## Slide 10: Price correction summary
Market: RTM
Impacted OD: February 15, 2021
Impacted Intervals: Certain SCED intervals between 09:45 and 20:35
Price Correction Methodology: ERCOT reran the impacted SCED intervals with corrected ERS deployment estimations to determine the correct RTORDPAs. These values were then used to recalculate the Real-Time Settlement Point Prices (RTSPPs) and the Real-Time Price for Energy Metered for Resources (RTRMPRs) for the impacted settlement intervals.
The following slides include an analysis of price and Settlement impacts of a RTM price correction for certain intervals on OD February 15, 2021, using revised price adders.

## Slide 11: Estimated Settlement impacts
OD | Change in the Sum of all Statements Due to ERCOT | 
2/15/2021 | $6,133,297.92 | 0.20%
OD | Maximum Impact to a Counter-Party | 
 | Maximum Amount* | Maximum Percentage**
2/15/2021 | $868,052.10 | 3.04%
OD | Energy Imbalance |  | DC Tie Imports |  | RENA |  | Base Point Deviation Charge | 
2/15/2021 | $271,081.17 | 0.095% | $(269,170.97) | 0.17% | $(695.53) | 0.002% | $17,176.88 | 0.39%
* The largest absolute impact to any single Counter-Party
** The largest percent change to any single Counter-Party with impact more than $20,000
The table above is a subset of the RTM charge types

## Slide 12: Additional notes and next steps
Nodal Protocol Revision Request (NPRR) 1024, Determination of Significance with Respect to Price Corrections
  NPRR1024 was approved by the ERCOT Board of Directors (Board) in February 2021. NPRR1024 is scheduled to become effective on April 1, 2021.
  NPRR1024 requires ERCOT to seek Board review of prices if the change in RTM Settlement Statement(s) would result in the absolute value impact to any single Counter-Party, based on the sum of all original RTM Settlement Statement amounts of Market Participants assigned to the Counter-Party, to be greater than:
    2% and also greater than $20,000; or
    20% and also greater than $2,000.
  Had NPRR1024 been in effect for the OD and price correction at issue, the significance threshold would have been met by two Counter-Parties under the first criteria (i.e., 2% and also greater than $20,000).
ERCOT will request that the Board review and consider this potential price correction at the next meeting, currently scheduled for April 13, 2021.