Severe Weather Readiness Workshop

Welcome and opening by John Adams who introduced the panel:

Trip Doggett – ERCOT

John Adams – Calpine

Mike Kotara – CPS Energy

Andrew Valencia – LCRA

Mike Williams – Luminant

Fran Sullivan - NRG

# Opening remarks and comments from Trip Doggett:

- Acknowledge chairman Smitherman for his leadership with bringing this workshop together and document lessons learned;

- No one will forget the events of 2/11…..Trip challenged everyone to keep weatherization and documentation in mind in preparing for the next event whether summer or winter;

- Keep weatheriziation in the fore front of your mind as we move forward. Make sure all equipment is documented and is ready for severe weather; modify all manuals accordingly (new or upgrade equipment needs to be documented) ; and include safety and training;

- Today’s discussion is not just about winter weather but all weather discussion…hot weather as well as hurricanes; and

- Specifically thank all companies that put this material together.  A very talented team, lead by Mike Williams, that developed a great work product that everyone will benefit from.

# Mike Williams from Luminant:

How do we go forward from the events in Feb?  How do we all agree on the things that need to be done to be prepared for another event like in February whether 10 or 20 years in the future? We will cover 3 items:

1. 	Review events and subsequent call to action

2.	 Best practices/lessons learned

3. 	Recommended Guidelines

Introduction and summary of findings from February 22, 2011:

- Winds of 30 – 40 with gust of 50+

- New ERCOT winter peak demand

- 225 units tripped, de-rated or failed to start

- 17.6% of total ERCOT winter 2011 capacity out

- All power plant types except nuclear experienced problems

Summary of findings from TRE:

- ERCOT followed normal procedures

- No indication that QSE, TSP or DSP failed to act to prepare for an emergency

- ERCOT did experience some communication problems

- Protocols and operating guides exist and conduct of market participants appeared to be consistent with the guidelines during the EEA but the protocols and guidelines do not establish requirements for specific actions to prepare for extreme weather

- Key finding of the TRE investigation was that the event was caused by either insufficient or ineffective preparation of generating facilities for prolonged freezing weather.

Call to Action:

A team of five companies (Calpine, CPS, LCRA, Luminant and NRG) were asked to participate by the PUC chairman and a working team was established with meetings held in Austin and Houston in March and April. The team developed the following:

- White paper (on event and request)

- Best practices/lessons learned

- Recommended Severe Weather Preparation Guidelines.

These 3 documents were presented to ERCOT CEO, Trip Doggett who asked the group to present this information at a workshop.

Question from floor: Did you look at winter and summer both? Mostly looked at winter but practices will work for summer also.

Fran Sullivan/NRG presentation:  Best Practices:

Challenge everyone to listen and look at the suggestions you might get out of this presentation. Awareness before the event is what Fran learned from this lesson.

Safety is the top priority and will not be compromised. Senior and upper management are to be held accountable; pre-plan and execute the plan.

Company operating plans; have a checklist. Write down expectations and hold people accountable for these expectations; document lessons learned from each event and utilize in a continuous improvement process; Implement freeze protection design criteria consistently across the fleet.

Write down all work orders and request. Prepare for all events; staff, management team; plant operators, shift operators and/or managers.  Do you have people on duty at night that can see the big picture? Practice and be prepared. Share lessons learned with other generators in ERCOT.

1. Safety – first

2. Communicate – before, during and after {Leadership and management}

3. Accountant ability – write down procedures

# Q&A for the Panel:

John Adams/ERCOT: Looking forward to the future what percentage of forced outage rates should we be looking out during this type of event?

- 18% forced outage rate is very high…this wasn’t just forced outage but also some schedule outages but regardless this number should be much lower. Anticipate there are going to be problems and be prepared; be more conservative about planning reserve margins and allow more time to start units up and learn from lessons in the past

- This percentage is way too high; take internal challenge; have corrective action plans and be prepared for liability. Start plants earlier and learn from mistakes. When you bring on a large number of units you have to be prepared for problems.

- There were a lot of plants that stayed on but had issues; just not prepared for the weather.

- We cannot have a repeat of 2/11….doing corrective action and learn from previous lessons.

- There is a risk the way the markets are set up….in the zonal market we had complete control of starting plants, but with the nodal market we do not. We have to be more prepared and not wait to be told when to start the plants….

- Trip/ERCOT: We need to look at historical temperature data; gather more historical data and review, and share and learn from this analysis.

Beth Garza/IMM:  Where does the responsibility lie between the resource owner and ERCOT with respect to responsibility for committing generation?

- Mike Kotara/ CPS Energy:  We have a gray area….beyond a day out who is calling the shots? It can be expensive for generators to start up. We have a market design for one day out, but maybe we need to give ERCOT another tool for severe weather for 2 or 3 days out….give ERCOT a tool that can actually do  this, a market mechanism, rather than leaving up it to the generators.

- Randy Jones from Calpine: The stakeholders have been talking about this; stakeholders need to implement a 2 day sequence where units can be brought on, warmed up, running and available coupled w/ERCOT’s ability to define type what of weather event level is coming on. Multiple sequence events.

BETH Garza/IMM: Some units declare themselves to need 24-hour to start; ERCOT called on those units in advance to make sure they were there…if resource owners say they need 8 hr to start but in reality need 12 hrs. to start. How do we explore further the mechanisms already there in terms of providing information about the characteristics of their units for ERCOT to use?

We didn’t even recognize that it would take 18 hours instead of 12 to start up with multiple sequence events happening….lessons learned and communication……there is an issue.

Beth Garza/IMM: ERCOT defines a winter level event and let the stakeholders know in advance. Resource owners need 8 – 12 hours in advance…..

Mike Williams: These conditions might take more than 12 hours…might take 18 hours….share responsibility…we still have an issue….need to look internally at communications

Question for John Adams and Trip Doggett: Don’t you already have the ability/tools –WRUC that we have  never run  and a  2 day out zone we never used….to do these things and we are you seem so reluctant to use them?

Trip Doggett/ERCOT:  I think we do have the tools but it’s really about the reports. We have a RUC tool so if the minimum start times are accurate in the RUC tool we can evaluate which units are available to start to meet the reserve margins that we need; perhaps it did take longer than the minimum start times within RUC; I don’t think that was a major issue for us in this event; we actually use those tools and if you look at it we had more planned reserves on line going into 2/2 than we had planned reserved going into the week later event. We should look more statically at the outage date and perhaps argue for more increased reserved margins. The real issue was the unprecedented forced outage rates that we experience and even with the right tools we didn’t have enough units’ lefts and with the short start up time thrown on you. We probably need to look at some out of market tools

John Adams/ERCOT: The comment I heard is that we could have asked generators to start units and keep them warm ahead of time. The capacity was there, it just did not remain online and I don’t think any tools would solve that problem.  It is more of a market policy question, should we start all units whenever we see a cold weather alert as opposed to expecting our reserves to be sufficient?

Randy made a comment: When ERCOT is faced with a cold weather event and they need to use actions to secure the system for loads we probably ought to make RUC a friendlier trigger for generation owners. Suspend the RUC claw-back portion in the market so that you get both bringing units on line voluntarily through the RUC process without the worry of having revenues clawed-back while you are trying to secure the system for everybody.

Fran Sullivan/NRG:  We will never design the perfect process; crisis will go on.  We have the tools; it’s getting them in place. I think having discussions helps. We know our plants and we can’t have ERCOT tell us what to do…we have to be held accountable.

John Adams/ERCOT: Can you make some suggestions on how can we organize the checklist for units/cold weather?

- ERCOT has the data….RUC keeps track of how long a unit has been off line so reach out to the resource owner when the unit has been off line for a while. Issue RUC instructions if you think there is going to be a problem. It is not the machines that have been running; it’s the ones that have not been running for a couple of months. These are the units that are going to have the problem;

- Do what you think is the right thing and be liable;

- We have a lot of load and if we can’t supply that load someone else is going to and at a price we don’t like;

- It’s easier to fix a problem when the temperature outside 50 rather than 20;

- Start looking earlier and if there is a chance of severe weather start preparing

DAVID /PUCT:  As you are preparing your plants for the winter weather is it possible that some of the things that you do in the winter would be a benefit to the summer and how do you deal with that?

John Adams /Calpine: The winter and summer preparedness is different. AC systems and heating systems are different and the wind protector  is different from the winter and summer, or hurricane winds and you must be able to deal with all extremes. Wind protector keeping the heat in or the heat out. The plant is designed with a plant basis and you must be ready to be outside of the plant basis. The checklist is going to be very different for the winter and summer.

A lot of the plans are just opposite for the winter vs. summer. We need to recognize what these differences are and be prepared. Document and have records…wind breaks for the summer and then have the necessary information to put the wind protector back where it should be for the winter.

Question: A lot of the new plants were outside of the design parameters for the cold weather. Of the 200+ plants that went down, were the majority of the new plants the ones that went down?  If we get up to 115 degrees for the summer weather are these new plants going to be outside of the plant design parameters also?

- Anything that was built post 1989 was hit a lot worse. Most plants found that they weren’t outside of the design parameter for temperatures, but the wind was the issue.

- Lessons learned from the 2/11 will be used to design the new (future) plants…make the changes and be ready to adjust….especially for the new units…share the lessons learned….make adjustments and challenge everyone…bring teams together and work together…do an analysis and make changes…learn from the past.

- Michael Kotara/CPS Energy: We have 20 generators that are a combination of old and new units and there was no consistency with the problems and the units. We didn’t catch some of the problems in the construction of the new units, but not all of the new units had problems. Not all of the old units had problems either. We have owned up to the lessons learned and are making the adjustments.

- Fran Sullivan/ NRG: We are taking things from a weather event and are learning from all weather patterns everywhere and are trying to learn from them.

Question: John Adams/ ERCOT: Any ideas on how to test new units to see if they are prepared?

- Prepare and go over your checklist

- Make sure everything working correctly

- No matter how prepared you think are, there are going to be problems

- Lesson learned from this event and use it

- Sometimes  experience is the best teacher

BETH/IMM:  So I build a new unit and I have to wait for it to get really cold to get a definite answer on whether everything is working?

Mike Williams/Luminant – that is not what I meant….you think you are ready and you have done everything possible, but until you go through a severe weather event, you don’t know what is going to happen. Unfortunately, experience is the best teacher.

Beth Garza/IMM: What I heard in John’s questions, is there something in particular that had issues for the new units that hadn’t been through severe weather,  a lesson learned in the aftermath, that now could be applied to a new unit that is being ready to be built so that we have a higher of confidence for the next 20 degree next winter that they will have done enough work before hand to get through the event so that the units don’t have to trip off-line in order to find the failure.

Move up weatherization a notch or two in your culture and in your thinking.

Lessons learned are the most valuable and try to apply those principals and look out for monitoring the right things.

Question: We have talked about ownership, documentation, preparation. The next one is going to happen in 2035 and none of us are going to be here at that time. Do we need to look at a protocol provisions for a weatherization preparation legacy to pass on to the future? Plant design to pass on to our future?

- Trip:  We have been talking with commission staff about weatherization and best practices, and we will work with David and his staff and how we take the results and whether there is something that needs to be incorporated or modified. Yes, there is work that can be done and ERCOT will be working with the commission staff.

- FRAN…I don’t believe we need regulation. These plants went through severe weather, they went through the cold. l believe that sharing lessons learned is the best practice. Not more codes and regulations.

- MIKE WILLIAMS:  If you are going to learn lessons how do you share these lesions? Is the PDOC the right vehicle or is a workshop the best solution?  I think sharing information is the best thing. How do you learn those lessons on regular bases and keep track of them and how do you learn from others? I’m not a fan of regulations. We share information and do the right thing we are going to be a lot better off.

- DAVID @ PUC….Yes we are looking at this issue and conducting an investigation and we are planning possible rule makings, but in those rule makings I doubt you will see anything that says a company should do XYZ to winterize their plants. One of the things we attempt to do in regulation is to bring groups together like this to share information, where the companies can compare notes and ideas. In Texas a one size fits all does not work.

# John Adams/ Calpine – presentation: Recommended Summer Weather Readiness Guidelines

Culture and discipline is needed for winter and summer.  Each plant should have its own specific program. Have a timeline for summer readiness, which means starting in September.

Have a timeline for hurricane readiness, which means Phases I – VI, beginning June 1. Have an action plan.

Readiness, communication, and emergent condition. Drought, heat, hurricane, tornado and even earthquake readiness. Have specific plan at each potentially impacted plant.

Laura Doll: You mentioned drought conditions. Is there anything else in particular that are you doing to plan for an extended drought?

Mike Kotara/CPS Energy:

- Watch water levels and pump water if necessary;

- Make sure your “rights” are okay for additional water supplies;

- Be pro-active; clean and check brush around plants/units to make sure there is no fire hazard;

- Don’t drive in grassy areas;

- Have  fire extinguishers in the trucks;

- Monitor cooling lake temperatures

- Watch for fish getting into traveling screens.

John Adams/ ERCOT:  Would this workshop be something that you would like to do annually?

PDOC might need to be the forum and ERCOT do the facilitation. Probably need to get the people who work in the plant engaged in the workshop.

John Adams/ERCOT: With respect to culture preparedness, how does ERCOT help facilitate this culture throughout the industry?

FRAN:  I don’t think this is ERCOT’s role.

Mike Williams, I agree. I think that ERCOT could have a role in promoting the awareness…..safety, severe weather, drought, hurricanes, etc. Let our group think about this.

ERCOT should promote preparedness….I don’t know how you can do this, but ERCOT should advocate being prepared for severe weather.  The annual Black Start Training could include summer and winter awareness in their training program. Broaden the summer/winter awareness to include the entire group. Look at the generator and transmission and distribution side.

John Adams/ERCOT: What did we learn and what are next steps for the future? Should we do this type workshop annually? Should ERCOT lead this workshop?

General census of the panel agreement to let PDOC lead the workshop and ERCOT do any facilitation work.  Maybe ERCOT could look at generators who have issues outside of weatherization. Is there something else you are seeing, the drought for example, you are sitting at a different level from the rest of us. What do you see that we don’t…how do we extend this learning and be pro-active?

Do generators have issues outside of weatherization? How do we extend this learning to other areas to be pro-active?

- Bring things that ERCOT is worried about to the forum? Interaction with the trade list? Generators? Is there anything? The senior team might need to get together and brain storm;

- Weather preparedness might need to involve the TSP….be pro-active;

- New plants failing more often that old ones….would it make sense to share the list of causes that made this happen with others…share the lessons learned…PDOC

QUESTION: I think this workshop was very informative and much needed. However, not all weather conditions are created the same. If we are going to institutionalize this process of weather preparedness, we might consider the next workshop to involve TDSPs. The next event might not just be a plant freeze, it could involve the TSPs more that the plants.

Tina/PUCT: We are planning an exercise in the fall, probably in November and we would like to have generators/TDSP, just as many people involved as possible. Suggestion….maybe invite the pipeline fuel supply group would be beneficial. We are planning this exercise with the railroad commission.

# Adjourn