## Slide 1: ERCOT Generation Weatherization Workshop
Seasonal Weather Readiness for Texas Generators
June 8, 2011

## Slide 2: Presentation Overview
Introduction and Summary of Findings
Call to Action
Best Practices
Recommended Guidelines

## Slide 3: Introduction and Summary of Findings

## Slide 4
Introduction February 2011 Weather Event
Coldest Texas weather since 1989.
Single-digit and sub-freezing temperatures for more than 100 hours.
Sustained winds of 30-40 mph with gusts of 50+ mph.
New ERCOT winter peak demand record of 56,344 MW (with a second record set the following week).
225 units tripped, de-rated or failed to start (Feb. 1-3).
17.6% of total ERCOT winter 2011 capacity out at Feb. 2 peak.
Except for nuclear facilities, all power plant types including coal/lignite, simple cycle gas, combined cycle gas and wind resources experienced problems.

## Slide 5: Summary of Findings– TRE Report
Wednesday, Feb. 2, 2011 was one of the coldest days in the last 25 years.
During the Feb. 1 – 3 period, an extraordinary number of generating units tripped, de-rated or failed to start due mostly to freezing instruments and pipes, but some fuel availability issues occurred as well.
High winds combined with the cold temperatures over an extended time period appears to have aggravated the freezing of instruments and piping.

## Slide 6: Summary of Findings– TRE Report
Approximately 17,519 MW was out of service prior to Feb. 2 due to scheduled outages (6640 MW), forced outages (5106 MW) and mothballing (5773 MW).
ERCOT followed normal procedures but did experience some communication problems on Feb. 2.
No indication that QSEs, TSPs and DSPs failed to act to prepare for an emergency.
Conduct of ERCOT and market participants during the EEA was, for the most part, consistent with requirements in Protocols and Operating Guides, although…..

## Slide 7: Summary of Findings– TRE Report
Protocols and Operating Guides do not establish requirements for specific actions to prepare for extreme weather.
Key Finding of TRE Report:
The February 2, 2011 EEA event was caused by either insufficient or ineffective preparation of generating facilities for prolonged freezing weather.

## Slide 8: Call to Action

## Slide 9: Call to Action
Subsequent to the Feb. 2 event, PUC Chairman Smitherman called several generating company CEOs and asked them to review the event and make recommendations on how to prevent this from happening again.
Five companies were asked to participate: Calpine, CPS Energy, LCRA, Luminant and NRG.
A working team was established with meetings held in Austin and Houston in March and April.

## Slide 10: Call to Action
Team assessed event and the actions taken prior to and during the severe weather. Team developed:
  White paper (on event and request)
  Best practices
  Recommended Severe Weather Preparation Guidelines
These three documents were presented to ERCOT CEO Trip Doggett on May 3, 2011.

## Slide 11: Best Practices

## Slide 12: Best Practices: Corporate Level
Executive involvement and support.
Company-specific emergency operating plan that includes:
  Policy
  Documented, written procedures with a timeline for activities
  Seasonal weather preparation meetings for winter and summer
  Accountability / verification procedures
  Internal and external communications plan
Continuous improvement process to document lessons learned / best practices after each event.
Freeze protection design criteria implemented consistently across the entire fleet.

## Slide 13: Best Practices: Plant Level
Plant-specific emergency operating plan that includes:
  Checklists to ensure proper preparation for severe weather
    Inspection of heat tracing circuits (especially on critical instrumentation) including wiring, insulation, control panels, etc.
    Installation of secondary wind barriers to protect critical equipment and instrumentation.
  Procedure for continuous monitoring of heat tracing on critical lines and pipes during severe weather events.
  Process for ensuring adequate quantities of winter weather supplies in advance of season and an event.
  Process for ensuring adequate staffing during an event.
Work orders / requests automatically generate each year to ensure preparation activities are initiated and completed prior to season.

## Slide 14: Best Practices: External
Consider formalizing process for requesting discretionary enforcement regarding environmental permits in support of grid reliability. Develop an MOU with PUC, TCEQ and ERCOT.
Consider warming / starting additional gas units prior to winter weather to improve unit readiness and reliability. Allow for longer start times.
Share lessons learned with generators in ERCOT
  Standing PDOC agenda item?
  Other mechanisms?

## Slide 15: Recommended Winter Weather Readiness Guidelines

## Slide 16: Recommended Guidelines
Purpose
  To maintain individual unit reliability with freeze protection guidelines, lessons learned and best practices.
Assumptions
  Generation operators are responsible for maintaining the readiness and reliability of their units.
  Generation operators should develop robust company and plant-specific guidelines based on geographical location, design, technology and plant configuration.
Notes: <number>

## Slide 17: Recommended Guidelines
Safety
  Safety remains top priority and will not be compromised.
Management readiness and involvement
  Corporate management accountability.
    Set expectations for safety, environmental compliance and generation
    Ensure weather preparation policy and plan exist for fleet.
    Ensure communications plan exist.
    Executive involvement and signoff to verify readiness.
  Plant management accountability.
    Develop plant-specific procedures and checklists to direct and document preparation of plant and all critical instrumentation and equipment for severe weather.
    Ensure all preparation measures are documented, completed, verified and provided to senior executives by a specified date.
    Ensure adequate staffing, supplies and fuel prior to and during an event.
Notes: <number>

## Slide 18: Recommended Guidelines
Communications
  Before
    Communicate readiness prior to event.
  During
    Activate an Emergency Operating Center (EOC) or similar facility to coordinate all internal and external communications.
  After
    Document lessons learned / best practices and review annually.

## Slide 19: Recommended Summer Weather Readiness Guidelines

## Slide 20: Recommended Guidelines
Purpose
  To maintain individual unit reliability during summer heat, lessons learned and best practices.
Assumptions (same as winter)
  Generation operators are responsible for maintaining the readiness and reliability of their units.
  Generation operators should develop robust company and plant-specific guidelines based on geographical location, design, technology and plant configuration.
Notes: <number>

## Slide 21: Recommended Guidelines
Safety
  Safety remains top priority and will not be compromised.
Management readiness and involvement
  Corporate management accountability.
    Set expectations for safety, environmental compliance and generation
    Ensure weather preparation policy and plan exist for fleet.
    Ensure communications plan exist.
    Executive involvement and signoff to verify readiness.
  Plant management accountability.
    Develop plant-specific procedures and checklists to direct and document preparation of plant for heat.
    Ensure all preparation measures are documented, completed, verified and provided to senior executives by a specified date.
    Ensure adequate staffing, supplies and fuel prior to and during an event.
Notes: <number>

## Slide 22: Typical Summer Readiness
Timeline
  Post summer
    September: Review recent summer performance/ lessons learned and best practices.
    Fall through spring: Conduct engineering reviews, identify improvements and corrective actions, implement work orders, complete tasks
  Pre- Summer
    April: All plants summer readiness meeting
    Before May 15: Plants complete checklists and work orders
    June 1: certify completed work and list exceptions/ risks and compensatory action to be taken.
  Summer:
    Communications: Plant operations, system dispatch, coordination to ERCOT, management
    Emergent Conditions: plan for most likely scenarios (e.g., loss of AC HVAC, etc…); be aware of unlikely scenarios (e.g., extended drought, etc…)

## Slide 23: Hurricane Preparedness and Action Plan
Specific Plan at each potentially impacted plant
  Communicate readiness for tropical storm and hurricane
  Plant preparation pre-season
  Outlines action and steps as guideline depending upon severity of storm AND speed storm is traveling.

## Slide 24: Hurricane Preparedness and Action Plan
Phase I
  Beginning of storm season (June 1)
Phase II
  Storm/ Hurricane Alert (in Gulf but not immediate threat)
Phase III
  Storm/ Hurricane Watch (storm in Gulf, potential threat within36 hours)
Phase IV
  Storm/ Hurricane Warning (predicted to make landfall within 24 hours
Phase V
  Hurricane Duty
Phase VI
  Post Hurricane

## Slide 25: Hurricane Preparedness and Action Plan
Staffing Plan and Duty Lists
Emergency Shutdown Procedure
Hurricane Supplies
  Goods: Tape, rope, wire, plastic
  Food: multi day supply
  Fuel/ Light/ Heat: batteries, stove , propane
  Hygiene: Toothpaste, soap razors, hairbrushes, etc.
  Misc: cots, blankets, socks,
  Communications: radio, cell phone, sat phone
Training
  Hurricane Awareness training
  Hurricane terminology
  Vendor lists