## Slide 1: TRE Workshop for Generator Weatherization 10/16/13
Alan H. Allgower
512-248-4613 alan.allgower@ercot.com
Notes: <number>

## Slide 2
Resource Weatherization Objective
Prepare for the best and hope for the worst.
Prepare for the worst and hope for the best.
Notes: <number>

## Slide 3
Declaration of Completion of Generation Resource Weatherization Preparations (Winter)
Nodal Protocol 3.20 (3)
No earlier than November 1 and no later than December 1 of each year, each Resource Entity shall submit the declaration Section 22, Attachment K, Declaration of Completion of Generation Resource Weatherization Preparations, to ERCOT stating that, at the time of submission, each Generation Resource under the Resource Entity’s control has completed or will complete all weather preparations required by the weatherization plan for equipment critical to the reliable operation of the Generation Resource during the winter time period (December through February).
If the work on the equipment that is critical to the reliable operation of the Generation Resource is not complete at the time of filing the declaration, the Resource Entity shall provide a list and schedule of remaining work to be completed.
The declaration shall be executed by an officer or executive with authority to bind the Resource Entity.
Submit declaration to: eop@ercot.com
Notes: <number>

## Slide 4
Declaration of Completion of Generation Resource Weatherization Preparations (cont.)
Nodal Protocol 3.20 (3)
This declaration shall not apply to any Generation Resource for any part of the above designated winter time period for which the Resource Entity expects the Generation Resource to be mothballed, and a Resource Entity is not required to submit a declaration for any Generation Resource that is expected to be mothballed for the entire winter time period.
However, if a Generation Resource was not included on the declaration because it was mothballed at the time the declaration was submitted and was not intended to be operational during the winter time period, a Resource Entity shall provide the declaration for that Generation Resource prior to changing its status from mothballed to operational during the winter time period.
Nodal Protocol 3.20 (5)
On or before January 15 each year, ERCOT shall report to the Public Utility Commission of Texas (PUCT) the names of Resource Entities failing to provide the declaration required by paragraph (3).
Notes: <number>

## Slide 5
Extreme Weather Assessment
Under PUCT Rules, ERCOT is charged with assessment of the reliability and adequacy of the system during extreme weather after the events of February 2, 2011.
For the winter 2012-2013 forty generation sites were selected for review of weatherization preparedness.
ERCOT visited generation sites that had performance problems in February 2011 and that were not visited in the 2011-12 spot checks.
Operations Planning randomly selects a subset of generators to be included in spot checks.
The implementation of weatherization plans submitted to ERCOT by resource entity is reviewed during site visits.
ERCOT is planning site visits for the 2013-2014 winter starting with black start resources.
Notes: <number>

## Slide 6
ERCOT observations from site visits
Plants have identified causes and taken the following measures to prevent freezing:
    Repaired or replaced heat trace
    Identified a need for wind barriers
    Replaced insulation
    Relocated critical transmitters
Notes: <number>

## Slide 7
ERCOT observations from site visits
1. Temperature design parameters of generating
units.
  It is sometimes not known without additional research by the plant at what ambient temperature (including wind chills) the unit will be able to operate, or to what temperature heat tracing and insulation can prevent the water or moisture in its critical components from freezing.
  Engineering analysis would be helpful for plants that are unsure or do not know.
Notes: <number>

## Slide 8
ERCOT observations from site visits
2. Weatherization plans, procedures and
checklists.
  Weatherization plans, procedures and checklists vary from detailed to general requirements.
  Plants that have detailed weatherization plans, procedures and checklists remained on line with minor problems during February 2011.
Notes: <number>

## Slide 9
ERCOT observations from site visits
3. Heat Tracing
  All plants do not test amperage and voltage for their heat tracing circuits and compare to design criteria, if known, or to the previous years readings.
  There are challenges with amperage readings and Thermon Corporation will discuss this further.
  Inconsistency observed in records management of heat trace maintenance.
Notes: <number>

## Slide 10
ERCOT observations from site visits
Heat Tracing (cont.)
  For newer plants and upgrades, the heat trace panels have individual circuit amperage meters for operators.
  Some plants telemeter heat trace panel alarms to the control room operator.
  After February 2011 many plants made upgrades to their heat tracing.
Notes: <number>

## Slide 11
ERCOT observations from site visits
3. Heat Tracing (cont.)
  One practice observed was in addition to annual amperage readings, some plants installed small lights along circuits for an indication to operators that heat trace is energized.
  Because heat trace worked last year doesn’t mean it’s working this year.
  One plant reported having 120 heat trace circuits and during the annual fall maintenance of 2012, 22 circuits (18.33%) failed maintenance inspections from the previous year.
Notes: <number>

## Slide 12
ERCOT observations from site visits
4. Instrument air maintenance and dryers.
  Most plants do maintenance bi annually.
  Moisture is removed by air dryers, dew point monitoring or periodic automatic blow downs.
  Instrument air drying is normally remotely alarmed.
  One plant reported switching to Nitrogen Gas (by product of their host) during the winter months.
Notes: <number>

## Slide 13
ERCOT observations from site visits
5. Winter weather supplies needed for extreme
weather.
  Some plants have locked job boxes at strategic plant locations with a laminated list for the supplies it should contain.
  Some plants have their supplies staged in the stores warehouse.
  One common observation is the winter supplies are secured.
  Consistency observed for supplies.
Notes: <number>

## Slide 14
ERCOT observations from site visits
6. Plants employ several methods for insulation
integrity.
  Plant is walked down and inspected in the fall.
  Repairs are tracked by plants PM system.
  Installation of temporary insulation on auxiliary equipment in the fall.
  Extra insulation is part of winter supplies.
Notes: <number>

## Slide 15
ERCOT observations from site visits
7. Plant training for extreme cold weather event.
  Does the plant do an annual extreme cold weather drill or training?
    66% of the plants visited during the winter 2012-2013 reported they conduct annual training and provided records.
    34% of the plants visited during the winter 2012-2013 reported they do not conduct annual training.
    All plant personnel should be aware of the critical components that could freeze and train accordingly.
Notes: <number>

## Slide 16
ERCOT observations from site visits
8. Operator training – critical transmitters
  Training would be beneficial to include the loss of critical transmitters.
  How many transmitters i.e., boiler drum level transmitters can be lost and the plant remain on line?
    Some plants are willing to run with one drum level transmitter in service and remain on line.
Notes: <number>

## Slide 17
Results from 2012-2103 winter fuel survey
Units with alternate fuel capability
  Total capability 5307.9MW.
    Units that were tested in 2012 – 2235.5MW (42%)
    Units that were tested in 2011 – 1865MW (35%)
    Units that were tested between 2003-2006 – 1041MW (20%)
    Units that were unable to determine the last test – 166.4MW (.03%)
  ERCOT will be sending a fuel survey to all Resource Entities in November for the 2013-2014 Winter.
Notes: <number>

## Slide 18
Additional information for 2013-3014 spot checks
Combustion tuning during a cold weather event.
  What measures have been taken for tuning during an extreme cold weather event?
  Are factory representatives able to remotely access the CT and make adjustments without having to take the unit off line?
Notes: <number>

## Slide 19
Best Practices Observed
One plant utilizes hand held scanners that are distributed to operators for use during an extreme cold weather event. The operators scan bar codes at critical locations when making rounds.
Detailed records management leads to success.
  In addition to annual amperage readings, some plants install small lights along circuits for an indication to operators that heat trace is energized.
  Annual preventative maintenance on heat trace circuits with records management.
Notes: <number>

## Slide 20
Challenges and Success
In Texas our plants are designed to dissipate the heat from the auxiliary equipment. That results in much of our plant auxiliary equipment being exposed to the elements.
Success is in the details and efforts that are put into the plans of identifying the critical auxiliary equipment that can freeze.
Notes: <number>

## Slide 21
References
http://www.nerc.com/pa/rrm/ea/Pages/February-2011-Southwest-Cold-Weather-Event.aspx#
  NERC lessons learned from the 2011 Southwest Cold Weather Event.
  FERC/NERC Report on Outages and Curtailments During the Southwest Cold Weather Event of February 1-5, 2011.
  Guideline for Generator Unit Weather Readiness – Current Industry Practices.
  Cold Weather Training Materials
Nodal Protocols for weatherization preparations.
  3.20 (3) (5)
PUCT §25.53(c)(2). Revisions to ERCOT within 30 days for the following:
  (A) A summary of power plant weatherization plans and procedures.
  (B) A summary of alternative fuel and storage capacity.
  Submit updates to eop@ercot.com
Notes: <number>

## Slide 22
Questions
?
?
Notes: <number>