Winter Weather Readiness for Texas Generators

Calpine, CPS Energy, LCRA, Luminant, NRG Energy

EXTREME WINTER WEATHER EVENT MANAGEMENT REVIEW

BY SOME TEXAS GENERATION PLANT OPERATORS

SCOPE

Some Texas generation plant operators were asked to review their current winter weather event management programs in light of their experiences during the February 2011 extreme and sustained cold weather event.  These operators believe it will be helpful to jointly develop winter weather readiness guidelines.

INTRODUCTION & BACKGROUND

Severe winter weather affected power generators in the Electric Reliability Council of Texas (ERCOT) power region from the morning of February 1, 2011 to the afternoon of February 5, 2011. As a result of this event, and its subsequent effects on generating unit availability across the state, the office of the Chairman of the Public Utility Commission of Texas (PUC) canvassed the corporate leaders of several Texas generating operators to gain their support to initiate a review of their current programs for dealing with extreme winter weather events.

THE EVENT

The strong arctic front that arrived in North Texas on February 1, 2011 was the most intense cold wave for the majority of the state of Texas since December 1989. The event was so severe that the National Weather Service issued a rare Wind Chill Advisory for much of the state. The arctic front reached deep into Texas and sustained below freezing temperatures as far south as Corpus Christi. Much of North Texas experienced record setting sleet and snow, producing blizzard conditions and temperatures well below freezing for up to 100 hours. Snowfall occurred as far south as San Antonio, with snowfall totaling up to seven inches in North Texas. This winter storm was also accompanied by sustained winds of 30-40 mph with gusts as high as 51 mph.

The icy conditions of this winter storm resulted in the closing of both DFW Airport and Dallas Love Field. In addition, Dallas-Fort Worth area water utilities reported hundreds of water main bursts during the event, compared to expected four to five on an average winter day. ERCOT also reported a new record winter peak of 56,334 megawatts.

The winter weather event of February 1-5, 2011 was determined to be a one in ten year event for some regions of Texas in terms of low temperature extremes and duration. Lows during the period were in the teens for five consecutive mornings and there were many consecutive hours below freezing temperatures throughout Texas. Taking these temperature extremes into account, and coupling them with the sustained winds of this event, it is estimated that the resultant convective heat loss (wind plus ambient temperature) event suffered by many Texas generation facilities approached a one in 25 year severity. (Reference: Weatherbank, Inc.)

Generating unit issues that affected reliability were mostly attributed to frozen instrumentation due to convective heat losses greater than instrumentation design, faulty instrumentation heat tracing or compromised insulation. It is normal practice for the operating units to add incremental protection against these extreme winter weather events.  Typical examples are wind breaks and heat sources applied to high risk areas.

In addition, the cold and wind affected the units that were not operating. Units in cold start status are less prone to derates/trips if they are dispatched to minimum stable load (MSL) before the onset of extreme winter weather.  Bringing all units to MSL gives ERCOT maximum flexibility in responding to grid emergencies.

HOW IT AFFECTED ERCOT

The high load demand, coupled with generation issues within ERCOT, resulted in actions from ERCOT that triggered an Operating Condition Notice (OCN) issued for cold weather at 08:55 on February 1. The event level escalated to an EEA2A (Energy Emergency Alert) declaration at 05:18 on February 2 to deploy responsive reserves, followed quickly by an EEA3 declaration at 05:58 on February 2 to begin shedding firm load to maintain system frequency at 59.8 Hz or greater. The event continued until ERCOT cancelled the EEA at 09:58 on February 3.

PARTICIPANTS

- Luminant (lead)

- NRG Energy

- Calpine

- LCRA

- CPS Energy

DELIVERABLES

Upon receipt of PUC Chairman Smitherman’s request, senior management from the listed participants met via conference call to formulate a method of response.  The outcome of this meeting was a consensus on the following deliverables:

- A white paper outlining the February winter weather event

- Discussion and sharing of significant  winter weather lessons learned and best practices during the February freeze event amongst Texas generator operators

- Winter weather readiness guidelines for Texas generation plant operators

TIMELINE

- March 30 – 31		Generator operators meeting in Austin to develop winter weather

readiness guideline

- April 6		 	Executive review meeting

SOME BEST PRACTICES FOR TEXAS GENERATORS DURING EXTREME WINTER WEATHER

The following list represents some best practices for dealing with an extreme winter weather event:

PLANT

- Freeze protection guidelines and design criteria that are implemented consistently across the entire fleet.

- Plant-specific emergency operating plans for winter weather.

- Heat tracing on critical lines and pipes monitored throughout winter weather events to ensure the circuits are functional (evaluate the use of infrared cameras, and other technologies, to inspect critical heat circuits).

- Secondary wind barriers as deemed appropriate to protect critical instrument cabinets, heat tracing and sensing lines.

- Consider enhancing staffing 24x7 during winter weather events.

- Consider enhancing management staffing 24x7 during winter weather events.

- Consider developing a master trip logic block switch for use during winter weather preparation with appropriate senior management approval.

- Review of operator and maintenance training to support winter weather guideline implementation.

- Process for ensuring adequate quantities of winter weather commodities and personal protection equipment are available during winter weather events (e.g., heat lamps, heaters, fuel supply, etc).

- Process for monitoring instrument air dew points year-round to ensure air is moisture free.

- Consider developing a plan for the removal of dead fish at plant’s intake structure in case low lake temperatures cause massive fish kill.

CORPORATE

- Company-specific emergency operating plan for winter weather.

- Use of continuous improvement to document lessons learned, best practices and to implement enhancing actions after each winter weather event.

- Executive support of winter weather preparation (e.g., by sponsoring a fleet-wide annual winter preparedness review).

- Consider asking transmission service providers to staff plant switchyard 24x7 during winter weather events to seek to ensure minimal line outages.

- ERCOT generator operators will share technical information and lessons learned, as it enhances unit availability, on an annual basis.

EXTERNAL

- Consider warming/starting additional gas units and auxiliary boilers prior to a winter weather event to improve unit readiness and reliability. Allow for longer start times.

- Consider formalizing process for requesting discretionary enforcement from applicable environmental permits in support of grid reliability. Memorandum of Understanding (MOU) would be developed with the PUC, TCEQ and ERCOT to formalize the process.

WINTER WEATHER READINESS GUIDELINES

FOR TEXAS GENERATORS

- PURPOSE

Collaborative effort to formulate a freeze protection process outlining guidelines, lessons learned and best practices for winter weather events with focus on maintaining individual unit reliability.

- SCOPE

Applies to all active electric generation plant operators (EGPO) in ERCOT.

- ASSUMPTIONS

  - EGPO are responsible and accountable for maintaining the reliability of their generating units.

  - EGPO should develop and apply plant-specific guidelines as appropriate based on factors such as geographical location, design, technology and plant configuration.

- WINTER WEATHER GUIDELINES

  - Safety

Management must emphasize that personnel safety remains the top priority during winter weather events and will not be compromised.

  - Management Readiness and Involvement

    - Accountability

      - Corporate Management

- Responsible for setting expectations for safety, environmental compliance and generation.

- Ensure that a winter preparation process exists for each operating plant.

- A senior executive will be designated to ensure compliance with all winter weather preparation procedures.

- Ensure that communication plans are developed.

      - Plant Management

- The plant manager will ensure that all winter preparation measures are documented and provided to senior executive management.

- EGPO will develop plant-specific procedures and checklists to document completion of winter weather preparations.  Primary areas of focus are:

- Critical Instrumentation Protection – Defined as instrumentation that places the unit at risk for tripping offline.

- Heat Trace and Insulation Readiness – Processes and procedures to verify full functionality before and during a cold weather event.

- Supplies – Ensure adequate inventories of all consumables, equipment and other necessary supplies.

- EGPO will develop processes, staffing plans and timelines that direct all key activities before, during and after winter weather events.

  - Communications

    - Before a Winter Weather Event

EGPO will acknowledge, evaluate and communicate to appropriate senior executive management all readiness activities based on the severity of forecast conditions.

    - During a Winter Weather Event

EGPO will activate an Emergency Operating Center (EOC), or similar facility, to coordinate all internal and external communications.

    - After a Winter Weather Event

EGPO will develop and maintain documentation containing lessons learned and best practices resulting from each winter weather event to be reviewed annually.