SAMPLE MODEL QUALITY TEST REPORT

LITTLE TURTLE WIND, 12INR0000

Date of Test:  April 5, 2020

Note: As of June 2023, MQT reports for Inverter-based (IBR) plants should show the PSS/E, PSCAD, and TSAT responses overlaid on the same plot axis (i.e. there should be one combined report). If utilizing a generic model, then the TSAT response is not required. Very old IBR plants that were never required to submit a PSCAD model would not be required to display a PSCAD model response unless requested by ERCOT. PSCAD and TSAT models should be packaged with the PSS/E model submission where applicable.

This is a sample model quality test report.  Per Planning Guide 6.2 and DWG Procedure Manual Section 3.1.5, Resource Entities and Interconnecting Entities should submit a similar test report when submitting their dynamic model.  Please refer to the Dynamic Model Submittal Guideline document for more info.

PROJECT DESCRIPTION

| Name | INR or SITECODE | Size | Turbine Quantity and Type (for IRRs & Batt.) and MVA Size (for non-IRRS) by Unit/Resource Name |
| --- | --- | --- | --- |
| LITTLE TURTLE WIND | 12INR0000 | 180 MW | Unit 1: 50 × 2 MW of Windtech 2000 Unit 2: 40 × 2 MW of Windtech 2000 |

Reason for this model update:

This is an updated model correcting a voltage ride through issue with the old model. This model improves the reactive power response during VRT.

Date of MOD 26/27 study (if applicable):

Future project. No MOD 26/27 study performed yet.

DESCRIPTION OF TEST PROCEDURE

These model tests were performed in PSSE using the DMVIEW tool.  The simulation was set up with a controllable slack bus connected to the plant POI and the entire plant was tested at the same time.  Following the DWG Procedure Manual, all tests were run initialized at full real power dispatch except the frequency tests which were initialized at 80% real power dispatch.  Results were compared with the examples posted in the DWG Procedure Manual and one discrepancy was found regarding the Frequency Step with Headroom test.

The following tests were run:

- Flatstart

- POI Voltage Step Down 3%

- POI Voltage Step Up 3%

- HVRT Leading and Lagging

- LVRT Leading and Lagging

- Frequency Step Down 0.03 Hz, No Headroom Assumption (default)

- Frequency Step Down 0.03 Hz, With Headroom Assumption

- Frequency Step Up 0.03 Hz

- Short Circuit Ratio

Describe How to Enable Headroom for the Frequency Test (IRRs only)

Headroom can be enabled by setting the PowerReserve parameter of the Windtech governor model (CON J+74) to 0.05, for example to indicate a 5% headroom.

Enclosures:

- Plant model files (Turtle.sav, Turtle.dyr, WindTech_2000_33.dll)

FLATSTART (no disturbance test)

The model flatstarted normally with no deviations (Figure 1).

Figure 1:  Flatstart test showing steady generator real (left) and reactive (right) flow indicating correct initialization.

VOLTAGE STEP DOWN

Under the stimulus of a 3% voltage drop at the POI, the plant increased reactive power output and maintained real power (Figure 2).

Figure 2:  The voltage stimulus is shown at top while the plant real and reactive response is shown in the plot beneath.  The plant correctly increased reactive output while maintaining real power.

VOLTAGE STEP UP

Under the stimulus of a 3% voltage rise at the POI, the plant decreased reactive power output and maintained real power (Figure 3).

Figure 3:  The voltage stimulus is shown at top while the plant real and reactive response is shown in the plot beneath.  The plant correctly decreased reactive output while maintaining real power.

HVRT Leading

Running the HVRT curve depicted in Nodal Operating Guide 2.9, the real power is maintained and the reactive power absorption increases as a result of the high voltage transient (Figure 4).  This “leading” test simulates plant initialized to 0.95 power factor leading at the POI.  Note:  Generators initialized to QMIN may not see an increase in reactive absorption for the HVRT leading test.

Figure 4:  For the HVRT stimulus applied at the POI (top figure), the plant reactive power decreased promptly while maintaining real power (bottom figure).

HVRT Lagging

Running the HVRT curve depicted in Nodal Operating Guide 2.9, the real power is maintained and the reactive power absorption increases as a result of the high voltage transient (Figure 5).  This “lagging” test simulates plant initialized to 0.95 power factor lagging at the POI.

Figure 5:  For the HVRT stimulus applied at the POI (top figure), the plant reactive power decreased promptly while maintaining real power (bottom figure).

LVRT Leading

Running the LVRT curve depicted in Nodal Operating Guide 2.9, the plant reactive power very quickly transitions to absorbing as a result of the high voltage transient (Figure 6).  Real power recovery was acceptable.  This “leading” test simulates plant initialized to 0.95 power factor leading at the POI.

Figure 6:  For the LVRT stimulus applied at the POI (top figure), the plant reactive power increased promptly (bottom figure).  The real power started to recover prior to the voltage reaching 0.9 per unit and recovered quickly upon reaching 0.9 per unit and thus was acceptable.

LVRT Lagging

Running the LVRT curve depicted in Nodal Operating Guide 2.9, the plant reactive power very quickly transitions to absorbing as a result of the high voltage transient (Figure 7).  Real power recovery was acceptable.  This “lagging” test simulates plant initialized to 0.95 power factor leading at the POI.  Note:  Generators initialized to QMAX may not see an increase in reactive production for the LVRT lagging test.

Figure 7:  For the LVRT stimulus applied at the POI (top figure), the plant reactive power increased promptly (bottom figure).  The real power started to recover prior to the voltage reaching 0.9 per unit and recovered quickly upon reaching 0.9 per unit and thus was acceptable.

FREQUENCY STEP DOWN, No Headroom Assumed (Power Availability State)

For a 0.03 Hz decrease in frequency, real power is maintained (Figure 8).  Per DWG Procedure Manual, real power was initialized at 80% of nameplate (180×80% = 144 MW).

Figure 8:  For a 0.03 Hz decrease in frequency, real power is maintained (bottom plot) which is correct assuming there is no headroom to increase real power.
Note:  The vertical axis in the top plot depicts Frequency Deviation Per-Unit, thus -0.005×60 = -0.3 Hz.

FREQUENCY STEP DOWN, Headroom Assumed (Curtailed State)

For a 0.03 Hz decrease in frequency, the model did not increase real power (Figure 9) despite having the PowerReserve option enabled to represent a curtailed state.  [Because a shortcoming was identified, please follow the instructions in the Model Quality Guide and work on submitting a corrected model.]

Figure 9:  For a 0.03 Hz decrease in frequency, real power is maintained (bottom plot).
Note:  The vertical axis in the top plot depicts Frequency Deviation Per-Unit, thus -0.005×60 = -0.3 Hz.

FREQUENCY STEP UP

For a 0.03 Hz decrease in frequency, real power decreased 18 MW or about 12% (Figure 10).  Per DWG Procedure Manual, real power was initialized at 80% of nameplate (180×80% = 144 MW).

Figure 10:  For a 0.03 Hz increase in frequency, real power decreased (bottom plot).  Note:  The vertical axis in the top plot depicts Frequency Deviation Per-Unit, thus +0.005×60 = +0.3 Hz.

SHORT CIRCUIT RATIO (SCR) TEST

Running the short circuit ratio test, Figure 11 indicates the model remained online and functional all the way down to a short circuit ratio of 1.2.  This is indicated by stable behavior all the way to the conclusion of the simulation where the final SCR tested was 1.2.  (The decrease in real power is possibly a result of the test inadvertently creating a need for additional reactive power as a result of the increased sending impedance.  Since this is likely a characteristic of the test, it will not be considered objectionable because the model is otherwise behaving in a reliable manner.)

Figure 11:  Short circuit ratio test.  Each pulse represents a new test condition where the POI is briefly faulted and at the same time the sending branch impedance is increased to achieve the new SCR value.  Per DWG Procedure Manual, SCR values of 5, 3, 1.5, and 1.2 were tested.  The test was initialized with SCR = 8, as depicted by the time 0 to 5 seconds prior to the first disturbance.

Please refer to the Model Quality Guide document note on headroom / power availability.  Also per DWG Procedure Manual, separate headroom / no headroom tests are only necessary for IRR (Wind / Solar) resources.