## Slide 1
WMWG
April 26, 2020
Balancing Operations Planning Staff
Update on Intra-Hour Solar Forecast and SCR811

## Slide 2
Discussion Outline
Update on SCR811
Intra-Hour Photo Voltaic Forecast and Predicted Solar Ramp Rate Forecast Performance
Applicability of other parameters in GTBD
Summary & Next Steps

## Slide 3: Background on SCR811
SCR811 will incorporate a intra-hour solar forecast based ramp into Generation To Be Dispatched (GTBD) to give Security Constrained Economic Dispatch (SCED) a indication of how the solar units may ramp.
In absence of this today, SCED dispatches uncurtailed solar units to their HSL.
  This means that SCED assumes output of uncurtailed solar units will persist for the next 5-min at the unit’s HSL that was telemetered at the start of the interval.
  What if solar ramps? or What if an FME occurs as the sun is setting? Regulation deployment is used to make up for gain/loss of solar MW but depending upon the circumstance frequency recovery could potentially be delayed.
Equation
GTBD = Total Gen + K1*10*System Load Frequency Bias + K2*[(net non-conforming Load) – (net filtered non-conforming Load)] + K3*5*PLDRR + K4*Regulation Deployed + K5*ACE Integral – K6*5*PWRR + K7*5*DCTRR – K8*5*PSRR
|PSRR| ≤ Max PSRR Feedback
NEW ADDITIONS

## Slide 4: SCR811 Update
As a part of implementing SCR811, ERCOT is in the process of integrating a 5-min Intra-hour Photo Voltaic Power forecast into ERCOT’s Energy Management System (EMS)
ERCOT’s EMS is being setup to compute a Predicted Solar Ramp Rate (PSRR) using
  Hourly Short-Term Photo Voltaic Power Potential (STPPF) forecast
  5-min Intra-hour Photo Voltaic Power forecast
  Note that at any given 5-min SCED interval only one amongst the above two methods for PSRR calculations will be active for use in GTBD.
ERCOT will on track to complete the software changes associated with SCR811 in the 2021 R3 release (scheduled to be implemented in Production systems between May 25 and May 27).

## Slide 5: Predicted Solar Ramp Error
Chart: Histogram of PSSR Error
| -9999 to -300 | -300 to -250 | -250 to -200 | -200 to -150 | -150 to -100 | -100 to -50 | -50 to 0 | 0 to 50 | 50 to 100 | 100 to 150 | 150 to 200 | 200 to 250 | 250 to 300 | 300 to 9999
Persistence | 19 | 21 | 15 | 18 | 40 | 86 | 266 | 300 | 107 | 35 | 22 | 19 | 7 | 22
Intra-Hour Forecast | 9 | 10 | 9 | 25 | 43 | 94 | 323 | 276 | 102 | 33 | 17 | 14 | 12 | 10
STPPF Method | 11 | 4 | 7 | 12 | 36 | 102 | 321 | 316 | 94 | 36 | 19 | 12 | 5 | 2
Performance Metric | Persistence (4/10 – 4/15) | Intra-Hour Solar Forecast (4/10 – 4/15) | Short-term Solar Forecast (STPPF) (4/10 – 4/15)
MAE (MW) | 72.10 | 62.65 | 52.16
MAE (MW) when 5-Min. Solar Ramp > 100 MW | 207.38 | 136.16 | 127.15
MAE (MW) when 5-Min. Solar Ramp < -100 MW | 213.59 | 119.39 | 128.99
Over Forecast
Under Forecast

## Slide 6: Predicted Solar Ramp Error
Chart: April 10, 2021 – April 15, 2021
Persistence Error | 0 | 0 | 0 | 0 | 0 | 0 | 0.011111 | 64.0667 | 86.5444 | 62.6486 | 31.4014 | 34.05 | 19.4694 | 18.2278 | 4.7257 | -7.9417 | -9.9681 | -41.5097 | -124.6361 | -126.2472 | -10.7111 | 0 | 0 | 0
PSRR Error (Intra-Hour) | 0 | 0 | 0 | 0 | 0 | 0 | 0.0088889 | 51.2533 | 69.2356 | 50.1189 | 25.1211 | 27.24 | 15.5756 | 14.5822 | 3.7806 | -6.3533 | -7.9744 | -33.2078 | -99.7089 | -100.9978 | -8.5689 | 0 | 0 | 0
PSRR Error (STPPF) | 0 | 0 | 0 | 0 | 0 | 0 | -3.9745 | 21.8845 | -9.4482 | -14.8914 | -7.589 | 4.7677 | -1.6346 | 9.0691 | 4.5269 | -3.9209 | -0.55301 | -1.5082 | -19.3242 | -25.3302 | 20.0286 | 0.23167 | 7.2656e-05 | 0
Average Solar HSL | 1.2698 | 1.2754 | 1.3164 | 1.3354 | 1.3416 | 1.3444 | 1.3324 | 90.0318 | 1213.3376 | 2378.7004 | 2807.6908 | 3214.8214 | 3545.5992 | 3755.5131 | 3755.2515 | 3740.055 | 3598.2413 | 3217.3721 | 2347.665 | 700.4344 | 19.4635 | 5.4433 | 4.456 | 1.2532

## Slide 7: Potential Impact of Predicted Solar Ramp in GTBD
Chart: 5-Min. SCED GTBD Error Due to Solar Ramp (4/11/2021 19:05 - 4/11/2021 20:00)
| 44297.798611111109 | 44297.802083333336 | 44297.805555555555 | 44297.809027777781 | 44297.8125 | 44297.815972222219 | 44297.819444444445 | 44297.822916666664 | 44297.826388888891 | 44297.829861111109 | 44297.833333333336
Persistent Error | -325.4316 | -287.0283 | -234.9147 | -307.3648 | -94.9059 | -97.9198 | -66.0851 | -149.0777 | -111.0999 | -62.734 | -58.6094
PSRR Error (STPPF Method) | -129.9766 | -104.2116 | -64.7363 | -149.8248 | 49.9957 | 34.3436 | 53.5399 | -42.091 | -16.7515 | 18.976 | 10.4622
PSRR(Intra-Hour Forecast Method) | -49.7316 | -38.8283 | -20.9147 | -88.9648 | 82.3941 | 71.8802 | 89.2149 | -18.8777 | 14.6001 | 29.366 | 20.5906
Solar HSL | 1529.358 | 1242.3297 | 1007.415 | 700.0502 | 605.1443 | 507.2245 | 441.1394 | 292.0617 | 180.9618 | 118.2278 | 59.6184

## Slide 8
Applicability of Other GTBD Parameters

## Slide 9: Other Parameters in GTBD
During SCR811 discussion last year, ERCOT was requested to share details on applicability of the various parameters in GTBD. Included are some situational examples wherein the a few recently added parameters play a role. Specifically,
  Regulation Deployed Component: K4* Regulation Deployed:
    Account for Regulation deployment in the past 2 minutes
  ACE Integral Component: K5* Ace Integral :
    Account for previous accrued ACE over an extended period of time
  PWRR Component : K6*5*PWRR
    Account for 5-min wind ramp for the next interval using intra-hour wind forecast

## Slide 10: GTBD Introduction
  - K8*5*Predicted Solar Ramp Rate (Using STPPF/IHPPF)
|PSRR| ≤ Max PSRR Threshold
Implementation of SCR811
- K8 *5* PSRR
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 – 10:00 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 – 1:15 PM – Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – 1:10 PM – K5 changed from 0.4 to 0.5, Max Integral ACE feedback changed from 160 to 200, PWRR Threshold changed from 25 to 30
6/17/20 – 10 AM - PWRR Calculation method changed from Direct to Interpolated
9/1/20 – 11 AM - Max Integral ACE Feedback changed from 200 to 250
9/3/20 – 3 PM - Max Integral ACE Feedback changed from 250 to 300
9/4/20 – 3 PM - Max Integral ACE Feedback changed from 300 to 250

## Slide 11: 10/8/2020 11:09 Event
Notes: 10/8/2020 11:09:12 AM
Unit Loss : 365 MW
Recovery time: 8:09

## Slide 12: Example: Impact of Regulation and ACE Integral in GTBD
Chart: Regulation and ACE Integral Feedback during Frequency Recovery (10/8/2020 11:08 Event)
| 44112.465277777781 | 44112.46597222222 | 44112.466666666667 | 44112.467361111114 | 44112.468055555553 | 44112.46875 | 44112.469444444447 | 44112.470138888886 | 44112.470833333333 | 44112.47152777778
Avg_Regulation_Component (1-min) | 7.2599 | 7.3384 | 21.5986 | 36.1804 | 58.0787 | 66.978 | 70.1965 | 71.3605 | 71.7815 | 71.3418
Avg_ACE_Integral_Component (1-min) | 24.8797 | 26.3161 | 30.5595 | 35.0627 | 39.4692 | 43.0058 | 46.435 | 49.5169 | 52.2899 | 53.5932

## Slide 13: Projected Wind Ramp Rate (PWRR) Error
Performance Metric | SCED PWRR (3/1 – 3/31) | Persistence Ramp* (3/1 – 3/31)
Monthly MAE (MW) | 88 | 109
Monthly MAE when 5-Min. Wind Ramp > 100 MW | 129 | 192
* Persistence Ramp assumes using a 0 MW wind ramp in PWRR

## Slide 14: Example: Impact of Projected Wind Ramp in GTBD
Chart: 5-Min. SCED GTBD Error Due to Wind Ramp (4/27/2020 14:00 - 4/27/2020 17:00)
| 43948.583333333336 | 43948.586805555555 | 43948.590277777781 | 43948.59375 | 43948.597222222219 | 43948.600694444445 | 43948.604166666664 | 43948.625 | 43948.628472222219 | 43948.631944444445 | 43948.635416666664 | 43948.638888888891 | 43948.642361111109 | 43948.645833333336 | 43948.649305555555 | 43948.652777777781 | 43948.65625 | 43948.659722222219 | 43948.663194444445 | 43948.666666666664 | 43948.670138888891 | 43948.673611111109 | 43948.677083333336 | 43948.680555555555 | 43948.684027777781 | 43948.6875 | 43948.690972222219 | 43948.694444444445 | 43948.697916666664 | 43948.701388888891 | 43948.704861111109
Persistence Error | -78.4072 | -155.6064 | -201.0352 | -62.5615 | -289.1768 | -191.3594 | -41.1484 | -160.2627 | 13.002 | -115.7812 | -145.7168 | -4.4248 | -4.1143 | -170.0654 | -22.8174 | -64.6768 | 116.8174 | -60.3623 | -135.9268 | -111.0098 | -46.6924 | 35.9014 | -11.5635 | -43.8174 | 78.8262 | 31.3916 | 5.1719 | 30.9688 | 5.043 | 76.082 | 4.4316
SCED PWRR Error | 71.5928 | -5.6064 | -89.4365 | 83.1387 | -139.1768 | -46.6592 | 108.8516 | -130.7627 | 114.2022 | -49.8818 | -38.2158 | 67.4746 | 70.9863 | -103.0654 | 69.9824 | -6.9766 | 162.1172 | 6.9375 | -102.3262 | -90.6104 | 46.9082 | 106.8018 | 59.4365 | -1.6172 | 118.9258 | 4.0908 | -13.9287 | 55.0684 | 10.7422 | 73.3818 | 16.0322
Wind HSL | 10715.1396 | 10636.7324 | 10481.126 | 10280.0908 | 10217.5293 | 9928.3525 | 9736.9932 | 9604.291 | 9444.0283 | 9457.0303 | 9341.249 | 9195.5322 | 9191.1074 | 9186.9932 | 9016.9277 | 8994.1104 | 8929.4336 | 9046.251 | 8985.8887 | 8849.9619 | 8738.9521 | 8692.2598 | 8728.1611 | 8716.5977 | 8672.7803 | 8751.6064 | 8782.998 | 8788.1699 | 8819.1387 | 8824.1816 | 8900.2637

## Slide 15: Summary & Next Steps
ERCOT will implement SCR811 during 2021 R3 between May 25 and May 27.
Initially, K8 will be set to 0 so that it will not impact GTBD calculation.
A market notice will be sent out prior to activation of K8 to a non-zero value.