## Slide 1
ERCOT Winter Storm Review of Emergency Response Service
Mark Patterson
Manager, Demand Integration
TAC
April 28, 2021

## Slide 2: ERS Fleet Performance – Loads and Generators
Note: the ERS fleet performance depicted above is a representation of the aggregate megawatts for ERS resources and does not reflect how they will be assessed for performance during each individual ERS deployment event.

## Slide 3: ERS Fleet Performance – Loads and Generators
Monday February 15th, 2021 most significant day of ERS deployment and obligation during the Winter Event
  The majority of the fleet is deployed and exhausted on the same day within 12 hours of the first deployment. A few ERS Loads remain obligated into subsequent days.
MW baseline significantly higher than MW actuals prior to first ERS VDI
  Baselines account for what demand (MW) would have been under normal operating conditions for the day – most ERS Loads were consuming much lower than normal heading into the event
As an ERS fleet in aggregate, the response generally met or exceeded the aggregate obligation
EEA Level 3 forced outages start ~1:20am and remain in effect throughout the entire event day

## Slide 4: ERS Fleet Performance – Load Only with WS
Note: the ERS fleet performance depicted above is a representation of the aggregate megawatts for ERS resources and does not reflect how they will be assessed for performance during each individual ERS deployment event.

## Slide 5: ERS Fleet Performance – Load Only without WS
Note: the ERS fleet performance depicted above is a representation of the aggregate megawatts for ERS resources and does not reflect how they will be assessed for performance during each individual ERS deployment event.

## Slide 6: ERS Fleet Performance – Load Only
Demand on Sunday February 14th, 2021 shows signs of load reduction prior to the first ERS deployment
  Based on responses to ERCOT RFIs, this was driven by a number of factors including weather related issues, local TDSP outages, closed businesses due to weather, in response to conservation notices, and price response.
As a fleet in aggregate, ERS Loads generally over-provided relative to their combined obligation during the Winter Event
  On average, fleet-level ERS Load reduction was 30%-35% above the combined fleet-level obligation during the first 12 hours after the first deployment (prior to majority of ERS Load fleet exhaustion)
  Preliminary analysis indicates ERS Load portfolios also performed relatively well during the individual deployment events
ERS Loads experiencing forced outages generally performed successfully relative to their baselines and obligations
  Loads still provide reduction during forced outages as their demand goes to zero, which may have also contributed to over-provision

## Slide 7: ERS Fleet Performance – Generator Only
Note: the ERS fleet performance depicted above is a representation of the aggregate megawatts for ERS resources and does not reflect how they will be assessed for performance during each individual ERS deployment event.

## Slide 8: ERS Fleet Performance – Generator Only
Activity on Sunday February 14th, 2021 shows export from ERS Generators prior to the first ERS deployment
As a fleet in aggregate, ERS Generators generally failed to meet their combined obligation during the Winter Event
  On average, fleet-level ERS Generator exports were 50%-55% below the combined fleet-level obligation during the first 12 hours after the first deployment (prior to exhaustion of the ERS Generator fleet)
  Based on responses to ERCOT RFIs, supply constraints, refueling issues, and forced outages were the primary factors affecting performance
Unlike ERS Loads, ERS Generators experiencing forced outages generally failed to perform relative to their obligations
  Generators are unable to perform (export) for ERS during forced outages
  Even prior to the forced outages, the ERS Generator Fleet was only meeting 70%-75% of its combined obligation

## Slide 9: ERS Gen Fuel Type (FebMay2021 SCT)
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Time Period
Distillate Fuel Oil | 167.585 | 167.585 | 167.585 | 167.585 | 167.585 | 167.585 | 167.585 | 167.585
Natural Gas | 63.8 | 52.5 | 51.8 | 62.3 | 61.7 | 63.2 | 61.2 | 55.3
N/A | 85.34 | 77.94 | 77.94 | 85.61 | 85.915 | 85.69 | 85.69 | 80.79
Note: N/A represents ERS Generators not registered with ERCOT and therefore fuel type unknown

## Slide 10: Review of ERS RFP for Jun-Sep SCT
Note: Offers for all subsequent SCTs in 2021 need to take into consideration the reduced spend limits
$7,675,163
$12,455,453