## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
April 29th, 2021

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs & IMFR
    1 FME in the month of February
    2 FMEs in the month of March
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 04/08/2021
  Review of emergency conditions list from ROS
  February cold weather event follow up discussion
  ERCOT reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in February
  2/22/2021 5:38:48
    Loss of 714 MW
    Interconnection Frequency Response: 1082 MW/0.1 Hz
    5 of 46 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    7 of 46 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
There were 2 FMEs in March
  3/3/2021 9:56:28
    Loss of 429 MW
    Interconnection Frequency Response: 913 MW/0.1 Hz
    13 of 51 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    9 of 51 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  3/30/2021 18:01:04
    Loss of load of 673 MW
    Interconnection Frequency Response: 961 MW/0.1 Hz
    10 of 51 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    10 of 51 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 471 MW/0.1 Hz
IMFR Performance currently 1042.53 MW/0.1Hz

## Slide 8: Frequency Control Report
March 2021

## Slide 9: CPS1 Performance
Current 12-Month Rolling Average: 169.30%

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy
Notes: 27,223,416 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes: 10,485,979 MWh

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 38.52%

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 10,410,55 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 3.82%

## Slide 18
Questions?