## Slide 1
ERCOT Frequency Control Report
April 2021
ERCOT
Operations Planning
PDCWG | May 14th, 2021

## Slide 2: Summary of April 2021
CPS1: 164.75%
Current CPS1 12-Month Rolling Average: 168.95%
9 BAAL Exceedance(s)
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2019 BAAL-003 FRM Performance: -811.14
2021 RMS1 Statistics
  Mean: 17.20 mHz
  Min: 12.01 mHz
  Max: 60.59 mHz
Energy Statistics
  Total Energy: 28,071,084 MWh
  Wind Energy: 8,907,804 MWh
  Percent Energy from Wind: 31.73%
  Solar Energy: 982,403 MWh
  Percent Energy from Solar: 3.50%
Minimum System Inertia
  Mean: 158,897 MW*s
  Max: 197,238 MW*s on Apr 14th
  Min: 120,857 MW*s on Apr 3rd
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Apr-21 CPS1 (%): 164.75
Notes: 54.24% @ 04/11/2021 18:00 and -209.23% @ 04/11/2021 19:00
Expected Generation Deviation
Expected gen dev remained negative for entire two hour of period. The largest expected gen dev was -2693 MW @ 19:30 mostly due to wind and solar.
IRR Ramps
Wind generation consistently ramped down during the entire two-hour period from 7285MW to 4980 MW.
Solar generation consistently ramped down during the entire two-hour period from 3952MW to 64 MW.
Regulation: Regulation up exhausted for the majority of the two-hour period
Other
SCED Manual offset of 250 MW @ 18:37
A total of 1350 MW of RRS was deployed at 19:28 and additional 500 MW of RRS was deployed at 20:02.
Approximately 1600 MW of Non-Spin deployed by 20:00.

## Slide 5: BAAL Exceedances & Violations
There were 9 BAAL exceedance(s) in Apr
Notes: Occurred on 04/11/2021 (7) and 4/30/2021 (2)

## Slide 6: 15-Minute Average CPS1%
Apr-21 CPS1 (%): 164.75

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 168.95%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 17.20 mHz
  Min: 12.01 mHz
  Max: 60.59 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2019 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2019 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 28,071,084 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 8,907,804 MWh

## Slide 23: % Energy from Wind Generation
Notes: 31.73%

## Slide 24: Total Energy From Solar Generation
Notes: 982,403 MWh

## Slide 25: % Energy from Solar Generation
Notes: 3.50%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 120,857 MW*s on 4/3/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 158,897 MW*s
Max: 197,238 MW*s on Apr 14th
Min: 120,857 MW*s on Apr 3rd

## Slide 28: Questions?
Thank you!