## Slide 1
Initial Analysis on Regional Solar
Capacity Contributions
Supply Analysis Working Group
Connor Anderson
Resource Adequacy
May 18, 2021

## Slide 2: Outline
Region maps
Current and planned units by region
Capacity contributions by region and season
Effects on summer reserve margins
Next steps

## Slide 3: Region Maps
Region definitions based on CDR zones except for Option 2 Far West region
“Non-West” is every CDR zone except for West and Panhandle
“West” is West and Panhandle CDR zones
Far West in Option 2 is a subset of the West CDR zone
Option 1: Two regions
Option 2: Three regions

## Slide 4: Three-Region Current and Planned Capacities
Chart: Regional Split of Solar Fleet (CDR-eligible as of May 2021)
| Current (May 2021) | End of 2021 | End of 2022 | End of 2023
Non-West | 323.1 | 4083.1 | 13738.4 | 15692.7
West | 813.1 | 2911.3 | 5078.8 | 7247.7
Far West | 2942 | 4790.5 | 5098.5 | 5301.5
 | Non-West (MW) | West (MW) | Far West (MW)
Current (May 2021) | 323 | 813 | 2,942
End of 2021 | 4,083 | 2,911 | 4,791
End of 2022 | 13,738 | 5,079 | 5,099
End of 2023 | 15,693 | 7,248 | 5,302

## Slide 5: Summer and Winter Capacity Contributions
Summer
Winter
3 Region - Summer |  |  |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW | Far West % | Far West MW
2020 | 80% | 204 | 80% | 498 | 85% | 1,740
2019 | 67% | 204 | 78% | 264 | 73% | 1,180
2018 | 73% | 199 | 76% | 208 | 82% | 848
2 Region - Summer |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW
2020 | 80% | 204 | 84% | 2,238
2019 | 67% | 204 | 74% | 1,444
2018 | 73% | 199 | 81% | 1,056
2 Region - Summer 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 74%
West | 80%
System-Wide | 80%
3 Region - Summer 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 74%
West | 79%
Far West | 81%
3 Region - Winter |  |  |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW | Far West % | Far West MW
2020-2021 | 6% | 204 | 8% | 668 | 8% | 2,680
2019-2020 | 9% | 204 | 4% | 294 | 4% | 1,433
2018-2019 | 5% | 199 | 16% | 208 | 9% | 998
2 Region - Winter |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW
2020-2021 | 6% | 204 | 7% | 3,378
2019-2020 | 9% | 204 | 4% | 1,727
2018-2019 | 5% | 199 | 10% | 1,206
2 Region - Winter 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 7%
West | 7%
System-Wide | 7%
3 Region - Winter 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 7%
West | 8%
Far West | 7%

## Slide 6: Spring and Fall Capacity Contributions
Spring
Fall
3 Region - Spring |  |  |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW | Far West % | Far West MW
2020 | 75% | 204 | 75% | 294 | 70% | 1,534
2019 | 46% | 199 | 49% | 258 | 49% | 1,180
2018 | 77% | 199 | 79% | 208 | 81% | 618
2 Region - Spring |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW
2020 | 75% | 204 | 71% | 1,828
2019 | 46% | 199 | 49% | 1,438
2018 | 77% | 199 | 80% | 826
2 Region - Spring 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 66%
West | 65%
System-Wide | 65%
3 Region - Spring 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 66%
West | 67%
Far West | 64%
2 Region - Fall 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 60%
West | 69%
System-Wide | 68%
3 Region - Fall 3-yr Capacity-Weighted Capacity Contributions | 
Non-West | 60%
West | 70%
Far West | 69%
3 Region - Fall |  |  |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW | Far West % | Far West MW
2020 | 62% | 204 | 75% | 498 | 75% | 2,681
2019 | 57% | 204 | 62% | 264 | 65% | 1,180
2018 | 60% | 199 | 66% | 208 | 57% | 997
2 Region - Fall |  |  |  | 
Year | Non-West % | Non-West MW | West % | West MW
2020 | 62% | 204 | 75% | 3,179
2019 | 57% | 204 | 65% | 1,444
2018 | 60% | 199 | 59% | 1,206

## Slide 7: Summer 2022 Reserve Margin Impact

## Slide 8: Summer 2023 Reserve Margin Impact

## Slide 9: Conclusions of Initial Analysis
Planned solar units are significantly more geographically diverse than operational units
Noticeable difference in summer capacity contribution between West and Non-West
Little difference between West and Far West
Downsides to analysis
  Capacity contribution calculations are heavily influenced by the current fleet’s concentration in Far West
  Did not look at the possibility of subdividing Non-West rather than West

## Slide 10: Next Steps
We will receive new solar planning profiles in the near future
Using the new profiles, we will:
  Assign profiles to each CDR-eligible planned unit
  Redo calculations using this larger, more diverse fleet
  Look at the effect of subdividing Non-West rather than West (do not want to have more than 3 zones)