## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2021_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2021 as of 05/18/2021
Data from Seasonal SSWG Base Cases Updated with updates received by 03/12/21
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL |  |  |  |  | LPL (31) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2021_SPG1 | 73440.5 | 71696 | 1620.46 | 1737.89 | 1300.9 | 2430 | 32.02 | 33.8 | 1162.9 | 2935.4 | 4256 | 27.48 | 31.3 | 1351.9 | 562.9 | 356.4 | 2.53 | 3.1 | -203.4 | 61 | 68.8 | 0.22 | 0.2 | 8 | 187.1 | 341.5 | 1.62 | 2 | 156.4 | 99 | 149.8 | 0.2 | 0.4 | 51.2 | 181 | 369 | 3.3 | 3.8 | 191.8 | 0 | 171.9 | 0.18 | 0.2 | 172.1
Spring Off Peak | 2021_SPG2 | 50440.8 | 49274.9 | 1081.8 | 1159.45 | 1137.7 | 1426 | 12.92 | 14.2 | 302.5 | 1305.9 | 2554 | 10.84 | 11.7 | 1259.8 | 103.3 | 172.4 | 0.78 | 0.8 | 69.9 | 24 | 48.3 | 0.07 | 0.1 | 24.4 | 29.8 | 174.1 | 0.42 | 0.5 | 144.8 | 99 | 289.3 | 0.43 | 0.6 | 190.9 | 21.3 | 185.5 | 1.26 | 1.3 | 165.5 | 0 | 51.5 | 0.03 | 0 | 51.5
Summer On Peak | 2021_SUM1 | 92443.7 | 90379.7 | 1867.06 | 2027.2 | 1684.3 | 2879.6 | 49.81 | 52.1 | 1247.4 | 4735.8 | 5362 | 43.53 | 50.9 | 677.1 | 1029.4 | 486.3 | 6.93 | 8.3 | -534.8 | 105.1 | 112.1 | 0.47 | 0.9 | 7.9 | 226 | 379.4 | 2.07 | 2.9 | 156.3 | 104 | 164.3 | 0.22 | 0.4 | 60.7 | 260 | 458.1 | 5.11 | 6 | 204.1 | 0 | 220.9 | 0.33 | 0.3 | 221.2 | 79 | 427.6 | 1.41 | 1.4 | 350
Summer Off Peak | 2021_SUM2 | 59337.9 | 58163.2 | 1083.43 | 1168.56 | 1042.6 | 1612.6 | 14.55 | 15.5 | 585.5 | 2300 | 3006 | 16.02 | 18.1 | 724.1 | 106.3 | 177.2 | 1.39 | 1.4 | 72.3 | 61 | 66.8 | 0.21 | 0.2 | 6 | 74.1 | 193.5 | 0.61 | 0.7 | 120.1 | 96 | 332.7 | 0.64 | 0.8 | 237.5 | 107.8 | 237.3 | 1.05 | 1.2 | 130.7 | 0 | 63.3 | 0.06 | 0.1 | 63.4 | 57.5 | 222.4 | 0.8 | 0.8 | 165.7
Fall On Peak | 2021_FAL1 | 76126.3 | 74518 | 1491.01 | 1605.72 | 897.7 | 2427.1 | 35.12 | 36 | 1565.4 | 2331.7 | 4482 | 22.46 | 24.5 | 2174.8 | 638.2 | 322.4 | 2.74 | 3.5 | -312.3 | 61 | 100.7 | 0.35 | 0.4 | 40.1 | 57.7 | 306.6 | 1.48 | 1.6 | 250.5 | 97 | 294.9 | 0.54 | 0.7 | 198.6 | 84.1 | 432.2 | 4.02 | 4.1 | 352.2 | 0 | 169.3 | 0.35 | 0.3 | 169.6 | 79 | 315.2 | 0.79 | 0.8 | 237
Fall Off Peak | 2021_FAL2 | 50191.9 | 49173.2 | 946.76 | 1016.2 | 713.9 | 1383.4 | 12.26 | 12.7 | 682.2 | 1292 | 2420 | 7.3 | 8.1 | 1136.1 | 96.7 | 161.2 | 0.71 | 0.7 | 65.2 | 24 | 58.6 | 0.09 | 0.1 | 34.7 | 0 | 156.3 | 0.5 | 0.5 | 156.8 | 97 | 302 | 0.49 | 0.7 | 205.7 | 15.1 | 219.5 | 1.44 | 1.4 | 205.8 | 0 | 53.7 | 0.04 | 0 | 53.7 | 6.4 | 210.7 | 0.62 | 0.6 | 204.9
Winter On Peak | 2022_WIN1 | 77954 | 76152.7 | 1667 | 1797.28 | 994.2 | 2221 | 61.64 | 62.9 | 1289.7 | 4077.9 | 4154 | 35.92 | 41.5 | 117.6 | 300.2 | 364.4 | 3 | 3.1 | 67.3 | 0 | 78.1 | 0.13 | 0.1 | 78.2 | 31.7 | 264.1 | 1.11 | 1.1 | 233.5 | 104 | 180.6 | 0.26 | 0.5 | 77.1 | 245.1 | 409.9 | 5.31 | 6.2 | 171 | 0 | 132.1 | 0.31 | 0.3 | 132.4 | 79 | 329.7 | 1.04 | 1 | 251.7
Winter Off Peak | 2022_WIN2 | 57435.4 | 56440.4 | 904.18 | 991.01 | 865.7 | 1847 | 20.93 | 21.7 | 1003 | 2482.6 | 2489 | 12.12 | 14.5 | 20.9 | 105.1 | 175.2 | 1.26 | 1.3 | 71.4 | 0 | 55.5 | 0.06 | 0.1 | 55.6 | 39.9 | 134.8 | 0.49 | 0.6 | 95.5 | 104 | 78.2 | 0.23 | 0.4 | -25.4 | 54.5 | 263 | 1.06 | 1.2 | 209.7 | 0 | 54.3 | 0.08 | 0.1 | 54.4 | 79 | 268.4 | 0.89 | 0.9 | 190.3
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2021_SPG1 | 2669 | 1482.68 | 610 | 42.96 | 169.57 | 0 | 4974.21 |  | 8143.4 | 2890.9 | 5252.5 | 67.55 | 2021_SPG1
Spring Off Peak | 2021_SPG2 | 2669 | 1425.81 | 560 | 0 | 165.22 | 0 | 4820.03 |  | 4901.1 | 2209.3 | 2691.8 | 26.75 | 2021_SPG2
Summer On Peak | 2021_SUM1 | 2669 | 1507.83 | 610 | 43 | 206.39 | 0 | 5036.22 |  | 10490.3 | 2389.9 | 8100.4 | 109.88 | 2021_SUM1
Summer Off Peak | 2021_SUM2 | 2669 | 1434.15 | 518.5 | 10.19 | 206.59 | 0 | 4838.43 |  | 5911.8 | 2105.3 | 3806.5 | 35.33 | 2021_SUM2
Fall On Peak | 2021_FAL1 | 2669 | 1420.31 | 610 | 23.26 | 206.36 | 0 | 4928.93 |  | 8850.4 | 4675.9 | 4174.5 | 67.85 | 2021_FAL1
Fall Off Peak | 2021_FAL2 | 2669 | 1389.17 | 527.4 | 0 | 202.56 | 0 | 4788.13 |  | 4965.4 | 2745.1 | 2220.3 | 23.45 | 2021_FAL2
Winter On Peak | 2022_WIN1 | 2669 | 1452.12 | 610 | 33.76 | 152.28 | 0 | 4917.16 |  | 8133.9 | 2418.5 | 5715.4 | 108.72 | 2022_WIN1
Winter Off Peak | 2022_WIN2 | 2669 | 1428.17 | 536 | 0 | 149.65 | 0 | 4782.82 |  | 5365.4 | 1675.4 | 3690 | 37.12 | 2022_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL |  |  |  |  | LPL NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 68466.29 | 45620.77 | 2.367% | 2.371% |  | 2430 | 1426 | 1.301% | 0.8979% |  | 4256 | 2554 | 0.6415% | 0.4226% |  | 356.4 | 172.4 | 0.7049% | 0.4504% |  | 68.8 | 48.3 | 0.3187% | 0.1447% |  | 341.5 | 174.1 | 0.4721% | 0.2407% |  | 149.8 | 289.3 | 0.1333% | 0.1484% |  | 369 | 185.5 | 0.8864% | 0.6747% |  | 171.9 | 51.5 | 0.1046% | 0.05822%
SUMMER | 87407.48 | 54499.47 | 2.136% | 1.988% |  | 2879.6 | 1612.6 | 1.7% | 0.8942% |  | 5362 | 3006 | 0.8053% | 0.5301% |  | 486.3 | 177.2 | 1.405% | 0.7783% |  | 112.1 | 66.8 | 0.4175% | 0.3134% |  | 379.4 | 193.5 | 0.5426% | 0.3143% |  | 164.3 | 332.7 | 0.1337% | 0.192% |  | 458.1 | 237.3 | 1.103% | 0.4405% |  | 220.9 | 63.3 | 0.1492% | 0.0947% |  | 427.6 | 222.4 | 0.3287% | 0.3584%
FALL | 71197.37 | 45403.77 | 2.094% | 2.085% |  | 2427.1 | 1383.4 | 1.426% | 0.8784% |  | 4482 | 2420 | 0.4986% | 0.3007% |  | 322.4 | 161.2 | 0.8427% | 0.4385% |  | 100.7 | 58.6 | 0.3464% | 0.1533% |  | 306.6 | 156.3 | 0.4804% | 0.3189% |  | 294.9 | 302 | 0.1828% | 0.162% |  | 432.2 | 219.5 | 0.9216% | 0.6518% |  | 169.3 | 53.7 | 0.2063% | 0.07443% |  | 315.2 | 210.7 | 0.25% | 0.2934%
WINTER | 73036.84 | 52652.58 | 2.282% | 1.717% |  | 2221 | 1847 | 2.7% | 1.12% |  | 4154 | 2489 | 0.8573% | 0.4846% |  | 364.4 | 175.2 | 0.8165% | 0.714% |  | 78.1 | 55.5 | 0.1662% | 0.108% |  | 264.1 | 134.8 | 0.4185% | 0.3622% |  | 180.6 | 78.2 | 0.1438% | 0.2933% |  | 409.9 | 263 | 1.279% | 0.4014% |  | 132.1 | 54.3 | 0.2341% | 0.1471% |  | 329.7 | 268.4 | 0.3144% | 0.3305%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL |  |  |  |  | LPL NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | -1.9647e-07 | 2.3803 |  |  |  | 0.00040106 | 0.32599 |  |  |  | 0.00012861 | 0.094166 |  |  |  | 0.001383 | 0.21197 |  |  |  | 0.0084893 | -0.26531 |  |  |  | 0.0013828 | -8.2483e-05 |  |  |  | 0.00010811 | 0.11714 |  |  |  | 0.0011538 | 0.46064 |  |  |  | 0.00038525 | 0.038378
SUMMER | 4.4997e-06 | 1.7427 |  |  |  | 0.00063626 | -0.13183 |  |  |  | 0.0001168 | 0.17901 |  |  |  | 0.0020275 | 0.41904 |  |  |  | 0.0022987 | 0.15983 |  |  |  | 0.0012285 | 0.076535 |  |  |  | 0.00034604 | 0.076867 |  |  |  | 0.0030011 | -0.27163 |  |  |  | 0.00034562 | 0.072819 |  |  |  | -0.00014503 | 0.39068
FALL | 3.4858e-07 | 2.0694 |  |  |  | 0.00052498 | 0.15219 |  |  |  | 9.5961e-05 | 0.06852 |  |  |  | 0.0025074 | 0.034317 |  |  |  | 0.0045847 | -0.11531 |  |  |  | 0.0010746 | 0.15091 |  |  |  | -0.0029281 | 1.0463 |  |  |  | 0.0012684 | 0.37334 |  |  |  | 0.0011408 | 0.013172 |  |  |  | -0.00041518 | 0.38087
WINTER | 2.7725e-05 | 0.25747 |  |  |  | 0.0042243 | -6.6818 |  |  |  | 0.00022385 | -0.072583 |  |  |  | 0.00054179 | 0.61912 |  |  |  | 0.0025746 | -0.034897 |  |  |  | 0.00043582 | 0.30344 |  |  |  | -0.0014599 | 0.40742 |  |  |  | 0.0059731 | -1.1695 |  |  |  | 0.0011184 | 0.086386 |  |  |  | -0.00026187 | 0.40078
EFFECTIVE DATES | SEASON
03/01/2021 - 05/31/2021 | SPRING
06/01/2021 - 09/30/2021 | SUMMER
10/01/2021 - 11/30/2021 | FALL
12/01/2021 - 02/28/2022 | WINTER