## Slide 1: Black Start Working Group Report for ROS
Tony Kroskey – Chair
Freddy Garcia – Vice Chair
June 3, 2021

## Slide 2
BSWG last met on May 18st - 26 participants
Discussed recent updates to Black Start Plans
Discussed Emergency Conditions List item #34
Review availability of blackstart units during February 2021 winter weather event and potential process improvements, including priority for non-curtailment of gas supply, to ensure availability during extreme weather events.

## Slide 3: Black Start Service
13 Procured Black Start Resources
  Selections conducted every 2 years
  All current BS Resources have a primary fuel of Natural Gas
  28 total Resources including all Primary and Alternates
  Alternate Resources are not currently required
Black Start Resource Selection Considerations
  Speed and cost of Resource to restore the Black Start restoration path
  Alternate on-site fuel
  Alternate Black Start Resource
  Resource disclosure of any hot or cold weather limitations
Alternate Fuel
  Not currently a requirement
  13 of the 28 Resources are Alternate Fuel Capable
  Black Start only alternate fuel not currently in requirements
  Alternate fuel information is confidential pursuant to Protocol 1.3.1.1(y)

## Slide 4: Black Start Resource Outage Summary
9 of 13 Primary Black Start Resources experienced an Outage at some point during the winter event
21 of 28 Primary & Alternate experienced and Outage at some point during the winter event
5 Primary and Alternate Resources experienced simultaneous outages
  Outages were not all consecutive
  Max simultaneous outage time: 44.33 total hours
  Min simultaneous outage time: 7.68 total hours
Outage Causes
  Fuel Limitation
  Equipment Issues
  Frozen Equipment
  Fuel Equipment Issues

## Slide 5: Outage Cause
Some Resources experienced multiple outages throughout the event time line with varying causes
  7 Resources: Lack of Fuel
  7 Resources: Frozen Equipment
  7 Resources: General Equipment Issues
  2 Resources: Fuel Switching
  9 Resources: Fuel Equipment Issues
Request For Information
  Weatherization mitigation efforts for units that experience weather related outages

## Slide 6: Improvements proposed at April/May BSWG meetings
  Required on-site alternate fuel storage for Black Start Service
  Required firm gas contracts that would allow priority for non-curtailment of gas supply
  Minimum set of freeze protection for Resource and alternate fuel storage
  BS ESR’s maintain continuous % of charge
  Training for all Black Start Capable Resources
  Add standby generator to stations/new switching stations part of cranking path/sync corridors(supporting SCADA, sub station batteries, breaker control)

## Slide 7: BSWG Future meeting dates
Wednesday September 22, 2021
Wednesday December 15, 2021