## Slide 1
TDSP EPS Meter Inspector Training
April 25, 2024

## Slide 2
Legal Disclaimers and Admonitions Protocol Disclaimer This presentation provides a general overview of the Texas Wholesale Market and is not intended to be a substitute for the ERCOT Nodal Protocols and Settlement Metering Operating Guide (or SMOG), as amended from time to time. If any conflict exists between this presentation and the (most current) ERCOT Nodal Protocols and SMOG, the ERCOT Nodal Protocols and SMOG shall control in all aspects.
This presentation was prepared using the Nodal Protocols and SMOG with effective dates:
      SMOG – 01-01-2024
      Section 10 – 03-01-2024
For more information, please visit:
http://www.ercot.com/mktrules/nprotocols/current
http://www.ercot.com/mktrules/guides/settlement/library

## Slide 3
Antitrust Admonition
To avoid raising concerns about antitrust liability, participants in ERCOT activities should refrain from proposing any action or measure that would exceed ERCOT’s authority under federal or state law. For additional information, stakeholders should consult the Statement of Position on Antitrust Issues for Members of ERCOT Committees, Subcommittees, and Working Groups, which is posted on the ERCOT website. http://www.ercot.com/about/governance/index.html
Disclaimer
All presentations and materials submitted by Market Participants or any other Entity to ERCOT staff for this meeting are received and posted with the acknowledgement that the information will
be considered public in accordance with the ERCOT Websites Content Management Operating Procedure.
Legal Disclaimers and Admonitions

## Slide 4: What Is The Purpose Of This Training?
What this training is about:
An introduction to TDSP EPS Meter Inspectors’ roles and responsibilities.
An overview of ERCOT Nodal Protocols and Settlement Metering Operating Guide (SMOG) covering EPS Metering.
An overview of Processes and Forms that relate to EPS Metering Facilities.
The mechanism by which a TDSP Meter Inspector is approved by ERCOT to
certify EPS Meter installations.
What this Training is NOT about:
A comprehensive technical training, assessment, & certification of Inspector’s technical knowledge and meter certification competency.
A discussion forum for Nodal Protocols issues.
A discussion forum for Settlement Metering Operating Guide issues and other topics (e.g., choice of equipment, vendors, etc.).

## Slide 5: Metering Categories (Who Does What?)
TDSP Metered Entities Protocols 10.2.2
  Responsible for supplying ERCOT with meter data associated with:
    Retail Load*
    Settlement Only Distribution Generation (DG)*
    NOIE Points with Radial Loads*
    Retail Unmetered Load
    Generation participating in a current Emergency Response Service (ERS)
*Indicates EPS Metering is optional

## Slide 6: Metering Categories (Who Does What?) cont.
ERCOT Polled Settlement Meters (EPS Meters) Protocols 10.2.3
  All EPS Meter Points will be placed or compensated at the point of interconnection (POI) except DG and Wholesale Storage Load (WSL)
  Responsible for polling metering facilities that meet the following criteria:
    Generation connected directly to the ERCOT Transmission Grid**
    Auxiliary meters used for generation netting
    Generation 10MW or more**
    Generation participating in any Ancillary Service market
    NOIE points connected bi-directionally
    Direct Current Ties (DC Ties)
    DG with associated WSL
    WSL, if opting to receive WSL treatment
    Metering to determine WSL associated with an Energy Storage Resource (ESR)
    Metering to determine Non-WSL ESR Charging Load
**Except generators participating in Emergency Response Service (ERS) contract. ERS deployment or test can be TDSP-read

## Slide 7: TDSP Data Acquisition in Competitive Areas
TDSP Meter-Reading Entities (TDSP data responsibilities)
Protocols 10.3.3.1
Validate,
Edit and
Estimate Meter Data
Protocols 10.11.3
TDSP
Format & Submit meter data via Texas SET
Protocols 10.3.3.3 & Protocols 10.12.2
Street Light (Unmetered)
Residential
Small Commercial
Large Commercial
Industrial
ERS & Distribution –Connected Generation < 10 MW
NOIE Radial Points of Delivery

## Slide 8: ERCOT EPS Meter Data Acquisition
EPS Metered Entities
Protocols 10.2.3
MV-90
Retrieve
Data
From
Meter
Validate,
Edit, and
Estimate
Output
Data to ERCOT
Settlement
System
Generation connected directly to the ERCOT Transmission Grid, unless the generation is participating in a current ERS Contract Period and the generation only exports energy to the ERCOT Transmission Grid during equipment testing, an ERS deployment, or an ERS test;
Auxiliary meters used for generation netting by ERCOT;
Generation delivering 10 MW or more to the ERCOT System, unless the generation is participating in a current ERS Contract Period and the generation only exports energy to the ERCOT System during equipment testing, an ERS deployment, or an ERS test;
Generation participating in any Ancillary Service market;
NOIE points connected bi-directionally to the ERCOT System, unless the bi-directional energy flows are the sole result of generation interconnected to a TDSP owned Distribution System behind a NOIE point of delivery metering point;
Direct Current Ties (DC Ties);
DG where there is an energy storage Load Resource that has associated Wholesale Storage Load (WSL);
Metering required to determine WSL associated with an Energy Storage Resource (ESR); and
Metering required to determine the Non-WSL ESR Charging Load
Additionally: Resolve data collection problems and maintain master files

## Slide 9: EPS Meters
TDSP Data Responsibilities
Installation and maintenance of meters
Manage meter security and passwords
Provide remote communications
Certification of EPS facilities
Assist in correction of data collection problems
Document any upgrades, changes or tests
ERCOT Responsibilities
Retrieve data directly from meter
Validate, edit, estimate (VEE) data
Time sync of meters (all are IDR)
Work with TDSP to resolve data problems
Move trade day data to Data Aggregation system.
Monitor changes to EPS meter points
Communications
ERCOT will retrieve daily all EPS meter data electronically & automatically.

## Slide 10: Review
Is this class an introduction and overview of the processes, procedures, and your role as an EPS Meter Inspector or a comprehensive training class and forum for discussing protocol changes?
Which entity performs VEE for Non-EPS meter points?
Which entity is responsible for certifying EPS meter points?
Where does meter data for Settlement come from for Non-EPS meter points?
Who performs time setting for EPS Meters?
How often will ERCOT poll EPS meters?

## Slide 11: What Does All This Mean To You?
A TSP or DSP shall have EPS Metering Facilities installed and maintained under the supervision of a TSP or DSP “EPS Meter Inspector.” This requirement does not apply to Resource Entity-owned Metering Facilities used to measure, calculate, or telemeter ESR auxiliary Load pursuant to Section 10.2.4, Resource Entity Calculation and Telemetry of ESR Auxiliary Load Values. {10.2.3.1(1)(b), 10.2.3.1(1)(c)}
A TDSP EPS Meter inspector is defined as an employee or agent of the TDSP who has received EPS training from ERCOT {10.2.3.1(1)(b)}
The TDSP shall ensure that the personnel performing EPS Meter Facility certification duties are approved TDSP EPS Meter Inspectors and comply with Protocol Section 10 and the Settlement Metering Operating Guide {10.5.2.1(1)}
All TDSP EPS Meter inspectors must have the technical expertise to perform EPS Metering Facility certification per statement from the TDSP {10.5.2.1(2)(c)}

## Slide 12: What Does This Mean to ERCOT?
ERCOT shall hold EPS Meter Inspector training sessions on a regularly scheduled basis {10.5.2.2 (1) }
ERCOT shall issue a certificate of attendance to individuals upon completion of the EPS Meter Inspector training sessions {10.5.2.2 (2) }
ERCOT shall maintain a list of TSP and DSP EPS Meter Inspectors, and details related to ERCOT training to become a TSP or DSP EPS Meter Inspector. {10.5.1 }
ERCOT shall have the authority to revoke an individual’s involvement with EPS Metering Facility certification {10.5.2.2 (3) }

## Slide 13
TDSP submits a Design Proposal for new & modified EPS installations
ERCOT reviews/approves the design concept and sends the approved Design Proposal to TDSP
TDSP installs equipment and may certify site/test communication
TDSP submits MDAS Form and TDSP Cutover Form (for install or remove metering point)
TDSP EPS Meter Inspector certifies facility and submits Site Certification documentations.
TDSP submits temporary exemption if EPS metering will not be installed/certified and/or EPS meter communication with ERCOT will not be established on or prior to cutover date.
TDSP maintains EPS metering facility per protocol and SMOG requirements & notify ERCOT of all access to the metering facilities.
ERCOT tests the communication interface with EPS meters
ERCOT reviews Site Certification documentation and communicate with TDSP for issues.
ERCOT approves EPS Metering facility certification and returns approved documents to TDSP

## Slide 14: EPS Design Proposal
What makes an EPS Design Proposal? SMOG Section 3.2.1
1. Facility Information and Contact Information (one per netted site)
2. Metering Facility details (one per metering point)
3. Detailed One Line drawing of facilities showing metering points
4. Auxiliary LOAD Telemetry DETAILS
5. Other Information as required
Should be provided no less than 90 calendar days before the cutover date for new EPS meter point(s).
Why do you need to know this?
EPS Meter inspectors will be certifying the entire metering facility per the latest approved Design Proposal/one-line drawing(s).
As such, EPS Meter Inspectors are required to review the latest approved Design Proposal/one-line drawings and certify that such proposal accurately represents the approved metering Facility.

## Slide 15: Getting Acquainted with EPS Metering Facilities
EPS Meter and Metering Facility Requirements
Must be an Interval Data Recorder or IDR (10.9.1)
Shall have a back-up meter of same quality {10.2.3.1(1)(d)}
TDSP shall provide ERCOT-approved metering communication equipment and connection {10.2.3.1(1)(e) & 10.3.2(1)}
EPS metering facility site shall be certified by TDSP EPS Meter Inspector {10.2.3.1(1)(b) & 10.4.3}
ERCOT site certification documentation shall be reviewed by ERCOT within 45 days of receipt. Any issues with the submitted documents will be communicated to the TDSP {10.4.3.1}

## Slide 16: EPS Back-Up Metering Requirements
Where?
Any Generation Resource
Auxiliary Netting
Bi-directional Metering Points
Protocols 10.2.3.1(1)(d)
What is it?
Redundant revenue quality EPS Meter connected at the same metering point as the primary EPS Meter and meeting the requirements defined in the Settlement Metering Operating Guide.
Protocols 10.2.3.1(1)(d)

## Slide 17: Detailed Metering Information Package
Should be provided to ERCOT no less than 14 calendar days before the requested “cutover” date. SMOG Section 3.2.4
    TDSP cutover form
Should be provided to ERCOT no less than 7 calendar days before the TDSP certification of the facility; for both the primary and back-up metering. SMOG Section 3.2.2
    MDAS configuration form
    Other information as required

## Slide 18: TDSP Meter Inspector & EPS Metering
Some of the activities EPS TDSP Meter Inspectors perform:
Certify that the EPS meter site conforms to Protocols and SMOG.
Certify that the site adheres to approved design proposal and detailed one-line “as built”.
Initial or sign and date drawings used during the metering facility site certification.
Ensure EPS metering site certification documentations are complete.
Facilitate establishing successful communications between ERCOT and EPS Meters.
Ensure access notifications have been submitted before accessing EPS Metering Facilities.
Call into ERCOT MDAS when accessing an EPS metering point.

## Slide 19: TDSP Meter Inspector Certification of EPS Metering Facilities
Minimum documentation necessary during certification of EPS Metering Facility:
Copy of most recent Nodal Protocols Section 10 and SMOG
Copy of approved Design Proposal
Copy of approved detailed one-line drawing
Copy of three-line drawings
Data for verification of instrument transformer

## Slide 20: TDSP EPS Approval Request Package
The TDSP will submit to ERCOT the following data for each EPS Meter Site within 60 Calendar Days after the site has been certified: Protocols 10.4 & SMOG 3.2.3
    Site Certification Form
    EPS Meter Test Report and a copy of meter program file
    Certification of instrument transformers by the TDSP along with pictures of the nameplates with readable data.
      If the instrument transformers are located in an apparatus and nameplate photos cannot be provided, a statement bearing the seal of a professional engineer registered in the State of Texas must be submitted instead of the nameplate photos.
    Redlined or final as-built detailed one-line or three-line drawing detailing the metering circuit. (signed or initialed and dated by an approved TDSP EPS Meter Inspector)
      If a redlined version is supplied, the final as built drawings shall be submitted within 45 days of the submittal of the Site Approval Request Package. SMOG3.2.3(h)
    Resource Entity Auxiliary Load Calculation Attestation Form (Section 11, Appendix D, Resource Entity Attestation for Calculation and Telemetry of Energy Storage Resource (ESR) Auxiliary Load Values), if applicable (SMOG3.2.3(j))
    Other information as required ( Pulse and Meter multiplier sheet, TLC worksheet etc.)
  Note: If the date of the form proceeds the date of the Inspectors approval, the form is not valid.

## Slide 21: ERCOT EPS Facility Approval Process
ERCOT shall review the site certification documentation within 45 days of receipt. If all data is complete, ERCOT shall:
Notify the TDSP of the approval of the metering Facility (10.4.3.1(2))
Return a copy of the schematic drawings and the ERCOT site certification form stamped by ERCOT as approved. ERCOT shall retain a copy of these documents (10.4.3.1(2))
If ERCOT finds that this data is incomplete or demonstrates that the EPS metering Facilities fail to meet the standards, ERCOT shall promptly provide written or electronic notice of the deficiencies to the TDP or DSP. (10.4.3.1(1))
ERCOT :
May elect to issue a provisional approval regarding those metering Facilities (10.4.3.2)
Shall post any provisional approvals on the MIS Public Area on a quarterly basis (10.4.3.2)
Note: Provisional status cannot be maintained indefinitely

## Slide 22: EPS Certification by TDSP Meter Inspector
Some of the activities a EPS TDSP Meter Inspector will need to perform:
EPS Site comply with Nodal Protocols and SMOG - other than approved exemptions.
    At the time of installation (10.9.1(1)) and thereafter (10.4.3.3)
Site adheres to approved design proposal and detailed one-line “as built”.
    Drawings accurately represent the site (10.4.3(2))
    Gen. Netting meets the common switchyard definition (10.3.2.3(2))
Documentation is complete :
    Documentation of any discrepancies for Items 1 and 2 (10.4.3(2))
    Site Certification Form (10.4.3(1))
    EPS Meter Test Report {SMOG Section 1.8 (c)}
    Certification of EPS instrument transformers {SMOG Section 3.2.3 (g)}
    Other Documents (Pulse and Meter Multiplier sheets, TLC worksheet, meter program file etc.) {SMOG Section 3.2.3}

## Slide 23: ERCOT & EPS Metering
ERCOT approves EPS Design Proposals
ERCOT reviews documentation completeness & approves facility
ERCOT audits EPS documentation and facilities
    Performs pre-audit detailed documentation review
    Conducts on-site audit of TDSP EPS-certified facility
    Follows-up outstanding issues

## Slide 24: ERCOT Site Auditing
1. Site audits are a team effort. ERCOT is supplying a second set of eyes.
2. Ensures EPS metering sites comply with Nodal Protocols and SMOG. This will assure Market Participants that settlement quality data is used for Settlements.
3.There is no Pass or Fail. Compliance issues that maybe found are documented and resolved.
Pre-Site Audit
2 Month Conference Call
  ERCOT initiates contact with TDSP regarding the Site Audit and provides a copy of Site Audit Checklist
  Establish date and time for the Site Audit and verify PPE requirements
  ERCOT informs TDSP of any common compliance issues and recommends a mock site audit
  ERCOT and TDSP finalize date and time of 2 Week Conference Call
Detail Review
  ERCOT performs a detail review of the most recently approved documentation
  ERCOT notes any discrepancies that are found and plans to discuss with the TDSP during the 2 Week Conference Call
2 Week Conference Call
  ERCOT informs TDSP of any discrepancies that were found during the Detail Review
  ERCOT answers any questions the TDSP may have at this time

## Slide 25: ERCOT Site Auditing
Site Audit
ERCOT will use the Site Audit Checklist to verify that the Site is meeting all of the requirements of Section 10 of the Protocols and the Settlement Metering Operating Guide (SMOG). Most recently approved documentation will be used for Site Audit.
ERCOT will witness the test of at least one EPS meter and any other test the TDSP may want to perform to satisfy the requirements listed on the Site Audit Checklist.
ERCOT will not ask the TDSP to violate any safety rules. However, the TDSP will have to make all reasonable efforts to provide the information requested.
TDSP will demonstrate for the meter type of the audit is programmed for loss of potential
        Site Audit Follow-Up
ERCOT will document any issues that do not meet the requirements of Section 10 of the Nodal Protocols or the Settlement Metering Operating Guide (SMOG) on the Site Audit Follow-Up Form.
ERCOT will e-mail a copy of the Site Audit Checklist with the auditors comments along with a copy of the Site Audit Follow-Up Form to the TDSP.
The TDSP will update the estimated completion dates on the Site Audit Follow-Up Form and return it to ERCOT to be used for tracking purposes.
Once all of the issues that have been documented on the Site Audit Follow-Up Form have been resolved, ERCOT will send an e-mail to the TDSP informing them that the Site Audit has been completed.

## Slide 26: Review
Who is responsible for supervising the installation and maintenance of EPS meter points?
Can a TDSP EPS meter Inspector utilize any EPS Design Proposal to certify an EPS metering facility?
What documents will a TDSP EPS meter inspector need to have in order to certify an EPS metering facility?
Does a TDSP EPS meter Inspector need to know the contents of the Settlement Metering Operating Guide to certify an EPS metering Facility?
What documents are required to be completed by a TDSP EPS meter inspector?
A site certification was performed on 4-15-2019. The name of the TDSP EPS meter inspector on one of the submitted forms was certified on 6-30-2019. Is the site certification valid?
Does ERCOT have the authority to revoke an individual’s involvement with EPS metering facility certification?

## Slide 27
BREAK

## Slide 28: Some Testing Requirements
TESTING OF EPS METERING FACILITIES:
At a minimum, EPS meters shall be tested annually by the TDSP (10.6.1.2(1)). TDSP shall keep meters’ test records for at least 6 years after the date of test. (SMOG Section 1.7.2)
At a minimum, the Resource Entity shall provide an updated Resource Entity Auxiliary Load Calculation Attestation Form on an annual basis, within the same month of each year as the previous year’s attestation. (10.2.4(2) & SMOG Section 1.7.1(2))
Instrument Transformer Testing Guidelines (SMOG Section 7.6)
Verify secondary wiring integrity upon initial certification and at least every 3 years thereafter {SMOG Section 1.3.4 (2) & 1.4.4 (2)}
Voltage drop calculation on V.T.s at initial certification {SMOG Section 1.4.4 (1)}
Test Equipment:
- Traceable to NIST (SMOG 1.6.2)
  Including the equipment to test ESR auxiliary load calculation
- Accuracy ≥ device (SMOG 1.6.1)
- Certify standard per ANSI or PUCT, i.e., 120 days (SMOG 1.6.2)
Meter Calibration:
Calibration (SMOG 1.6.5)
±0.15% (FL & LL)
±0.30% (PF & VAR)
Test Request:
- ERCOT (10.6.1.1)
- Market Participants (10.6.1.4)
- PUC
Facility Sealing:
- Unique Number (10.10.1.5)

## Slide 29: Failure of Communication Facilities
ERCOT Settlement Communication Failure to EPS Meters: (SMOG Section 2)
During a disruption to the ERCOT Meter Data Acquisition System (MDAS) communication link to EPS meters, ERCOT shall:
    Make all reasonable efforts to provide general information to TDSPs using voice communications; and
    Inform the TDSP of the methods they shall use to provide meter data to ERCOT during the disruption period

## Slide 30: Failure of Communication Facilities
Resource Calculated Auxiliary Load Communication Failure to EPS Meters: (SMOG Section 2)
During a disruption to the Resource communication link to EPS meters, the Resource Entity shall:
    Make all reasonable efforts to provide general information to TDSPs on the restoration efforts and timelines; and
    Provide Operating Day meter data to ERCOT and the TDSPs, via the requested format and delivery method, as required to support settlements during the disruption period.

## Slide 31: Settlement Metering Process – 000 (SMOG Appendix C)
TDSP Notification by ERCOT of Communication Problems with EPS Meters
ERCOT shall:
Manually reschedule calls to try and establish meter communications with failed locations
Identify if Primary or Back-up meter data is available for the metering point
Determine the required time frame for repairs per Protocols
Notify the TDSP repair contact via phone and e-mail as soon as reasonably possible (target timeframe for notification is 0900 hours)
Provide reasonable support to the TDSP to verify the communication problem is resolved. To facilitate this support the TDSP must provide ERCOT an estimated time when such support is required for a site
Send an escalation e-mail to the TDSP EPS metering escalation contact list if EPS meter data has not been provided by 1500, for six-hour notices
Log a record of the phone and e-mail notification
Record repair date and time reported by the TDSP to ERCOT

## Slide 32: Settlement Metering Process – 000 (SMOG Appendix C)
TDSP Notification by ERCOT of Communication Problems with EPS Meters
TDSP shall:
Make reasonable efforts to adhere to the repair timelines in the notices
Notify ERCOT by e-mail in instances where a repair cannot be accomplished in the designated timeframe
Provide communications to ERCOT on the repair timeline by phone or email
For six-hour notices, submit EPS meter data or estimation instructions by email by 1500 on the same day the six-hour was generated, and submit meter data or estimation instructions by email by 1500 on subsequent Mondays, Wednesdays and Fridays until communications are reestablished
Respond to escalation e-mails in a timeframe that supports the provision of data for settlements
Provide confirmation of repairs to ERCOT by phone or email that includes site name, meter serial number, date and time repairs were made, a brief description of the repairs and information on the affects the problem had on the accuracy of the meter data

## Slide 33: Settlement Metering Process – 000 (SMOG Appendix C)
TDSP Notification by ERCOT of Communication Problems with EPS Meters
CONTACT INFORMATION
TDSP shall:
Provide an e-mail notification to ERCOT at mreads@ercot.com when requesting a change to the TDSP repair contact information
  A “temporary” change to the repair contact information shall be identified as such and shall include the beginning and ending date that such change is to be in effect
    The subject line should state “TDSP Name temporary change to TDSP repair contact”
  A “permanent” change to the repair contact information shall be identified as such and shall include the beginning date that such change shall take place
    The subject line should state “TDSP Name permanent change to TDSP repair contact”

## Slide 34: Notification & Repair Timelines
Emergency repairs? (10.8.1.2)
- If an EPS Meter requires repair or replacement to ensure that it operates in accordance with the requirements of this Section, the TSP or DSP shall immediately notify ERCOT of the need for repairing or replacing that meter. {10.8.1.2(1)}
- Where no back-up meter exists or back-up meter data is unavailable, the TSP or DSP shall ensure that the metering point is repaired and operational within 12 hours of problem detection , or within six (6) hours if meter data is required for Real-Time Market (RTM) Settlements on the same day or upcoming ERCOT non-Business Day. {10.8.1.2(1)(a)}
- Where a functional and operational back-up meter exists, the TSP or DSP shall ensure that the metering point is repaired and operational within five (5) business days of problem detection. {10.8.1.2(1)(b)}
Notification for Testing or other Access to EPS Metering Facilities
- SMOG – Testing and Notification (1.6.4)
- SMOG - Settlement Metering Process 020 (Appendix B)
- Planned Maintenance (10.8.1.1)
- Planned Changes (10.4.3.5)
- Emergency Situations (10.8.1.2)

## Slide 35: Settlement Metering Process – 020 (SMOG Appendix B) On Site Work
On Site work to EPS Metering Facilities
Notification of required Access to EPS Metering Facilities
For maintenance or changes to EPS metering Facilities, the TDSP shall notify ERCOT when access is expected to occur by completing the “TDSP Access to EPS Metering Facility Notification Form” and e-mailing the completed form to “mreads@ercot.com”
  The email subject line shall read “EPS Access Required–SITE NAME ”
For “emergency repairs”, The TDSP can notify ERCOT of the need to access EPS metering Facilities by calling the MDAS Operations Center at 512-248-6500 and submit the “TDSP Access to EPS Metering Facility Notification Form” by the end of the next Business Day following such access.

## Slide 36: Settlement Metering Process – 020 (SMOG Appendix B) On Site Work
On Site work to EPS Metering Facilities
Notification of required Access to EPS Metering Facilities
For maintenance or changes to equipment used in the calculation of the Auxiliary Load telemetry provided to an EPS Meter, the Resource Entity shall notify ERCOT and the TDSP when access is expected to occur by completing the “Resource Entity Access to Auxiliary Load Telemetry System Notification Form” and e-mailing the completed form to mreads@ercot.com and an email contact provided to the Resource Entity by the TDSP
  The email subject line shall read “Telemetry Access Required–SITE NAME ”
For “emergency repairs” of equipment used in the calculation of the auxiliary load telemetry provided to an EPS Meter, the Resource Entity can notify ERCOT of the need to access EPS metering Facilities by calling the MDAS Operations Center at 512-248-6500 and submit the “Resource Entity Access to Auxiliary Load Telemetry System Notification Form” by the end of the next Business Day following such access.

## Slide 37: Settlement Metering Process – 020 (SMOG Appendix B) On Site Work
On Site work to EPS Metering Facilities
Examples of Maintenance included in the 5 Business Day Notification Period
EPS Meter Maintenance
Removal of any EPS metering Facility wiring
Maintenance to non-EPS metering equipment that is connected to the EPS metering circuit
Examples of Maintenance included in the 10 Business Day Notification Period
EPS Metering equipment changes or replacements (non emergency)
EPS Metering equipment reprogramming (non emergency)
Upgrade the site from “temporary metering” to “permanent metering”
Changes to equipment used in the calculation of the auxiliary load telemetry provided to an EPS Meter (non emergency)
Planned modifications to the calculation of the auxiliary load in the Resource Entity equipment

## Slide 38: Settlement Metering Process – 020 (SMOG Appendix B) On Site Work
On Site work to EPS Metering Facilities
Examples of Maintenance included in the Immediate Notification Period
This category is for unplanned work being performed to repair EPS metering Facilities due to a failure
  Communication failure to an EPS Meter
  Meter reprogramming
  EPS Meter replacements
  EPS instrument transformer replacements
  Replacement or repair of equipment used in the calculation of the auxiliary load telemetry provided to an EPS Meter
  Immediate modifications to prevent under reporting of the calculation of the auxiliary load in the Resource Entity equipment

## Slide 39: Settlement Metering Process - 020 (SMOG Appendix B) On Site Work to EPS Metering Facilities
BASIC GUIDELINES/RULES
The primary and the backup meters shall not be taken out of service during the same settlement interval (15 minute time interval)
Before removing an EPS meter from service, the TDSP EPS Meter Inspector shall:
  Notify ERCOT that the meter shall be removed from service by calling ERCOT MDAS @ (512) 248-6500. A voice mail message is considered adequate notification.
  If there is not a certified back-up meter, ensure that interval data is downloaded from the meter. This can be accomplished by:
  a. ERCOT polling the meter.
  b. The TDSP polling the meter.
  c. The TDSP downloading the interval data.*
  * Such meter download shall be in a format that allows the creation of an MDAS compatible file format (Example: HHF File, P-File, E-File, CSV file) for such data.

## Slide 40: Settlement Metering Process - 020 (SMOG Appendix B) On Site Work to EPS Metering Facilities (con’t)
BASIC GUIDELINES/RULES
If the EPS meter is the ONLY meter or the changes/maintenance cannot be performed without pulling the Primary and Backup meter(s) out of service during the same 15-minute time interval
  The TDSP shall make arrangements to assist ERCOT in the estimation of meter data for the metering point before the meter is removed from service
  ERCOT will ask the TDSP to provide 15-minute interval data to be utilized to perform the edit in the ERCOT MDAS system
  If the TDSP determines that 15-minute interval data cannot be provided, ERCOT will perform the edit with the assistance of the TDSP so that reasonable data is available as per Protocols for Settlement billing
During normal business hours, the TDSP should request to have ERCOT poll the meters to see that they are back in proper working condition and perform a load verification

## Slide 41: Settlement Metering Process – 030 (SMOG Appendix A) Documentation Requirements after Access to EPS Metering Facilities
Immediate Information Requirements After Site Access
The Transmission and/or Distribution Service Provider (TDSP) or Resource Entity must communicate closely with ERCOT, during access periods to ERCOT-Polled Settlement (EPS) Metering Facilities, to ensure accurate data is available for Initial Settlement. Initial information submitted by the TDSP/Resource Entity to ERCOT must be provided in sufficient detail and in a timeframe to support Initial Settlement.
Such information shall be conveyed using voice communications to ERCOT Meter Data Acquisition System (MDAS) (512-248-6500) at the conclusion of the access period, with a follow-up e-mail sent to mreads@ercot.com and TDSP.

## Slide 42: Settlement Metering Process – 030 (SMOG Appendix A) Documentation Requirements after Access to EPS Metering Facilities (con’t)
Immediate Information Requirements After Site Access (con’t)
Minimum information required following site access
  Site name “as specified on the approved EPS Metering Design Proposal”
  Meter serial number
  Date and time period access occurred
    Including the time the metering was out of service
  Description of the work performed during such access period
  The source the Settlement data will be available for such access period
  Information on the affects the access had on metering accuracy and meter data
    Including the time frames that accuracy or data was affected
  The TDSP will assist ERCOT in the edit of any missing meter data

## Slide 43: Settlement Metering Process – 030 (SMOG Appendix A) Documentation Requirements after Access to EPS Metering Facilities (con’t)
Immediate Information Requirements After Site Access (con’t)
Interval data requirements to support initial settlement after site access
  Primary and Back-up meter existing at the location and only one meter’s data will be affected during the same settlement interval
    ERCOT will use the data from the other meter to fill in missing data
  Primary and Back-up meters exist at the location, BUT data is affected on BOTH meters during the same settlement interval or there is not a certified back-up meter
    The TDSP shall provide other information and data to assist ERCOT in performing edits or estimation for missing intervals of meter data
    Such information or data should be available by close of business the business day following access to EPS Metering Facilities
    ERCOT will perform the edit with the assistance of the TDSP, so that reasonable data is available for Initial Settlement

## Slide 44: Review
A meter test was performed on 5-30-2015 with a standard that was certified traceable to NIST on 1-15-2015. Is the meter test valid?
What is the required notice for accessing an EPS metering Facility for an annual meter test?
Can NON-EPS equipment connected in the EPS metering circuit be accessed without notifying ERCOT?
What is the required notice for accessing NON-EPS equipment connected in the EPS metering circuit for planned maintenance?
Is the TDSP EPS Meter Inspector required to notify ERCOT before an EPS meter is removed from service?
Should a primary and back-up meter for any EPS metering point be removed during the same settlement interval?
For planned testing or maintenance of meter points where a certified back-up EPS meter is not available, is the TDSP required to make arrangements to assist ERCOT in the estimation of meter data for the metering point before the meter is removed from service?

## Slide 45
Lunch

## Slide 46: Settlement Metering Process 030 (SMOG Appendix A) Documentation
Documentation Requirements after Access to EPS Metering Facilities
Documentation Submission Requirements After Site Access
Any access to approved EPS metering Facilities shall be thoroughly documented by the TDSP
  Documentation submitted to ERCOT
  Timeframe for submittal of documentation
    Dependent on the exact nature of the performed work
    And the implications such work has on initial settlement
Example events to assist in understanding the documentation required after access to EPS metering Facilities are provided on the following slides
Other documentation may be required depending on the nature of the performed work

## Slide 47: Settlement Metering Process 030 (SMOG Appendix A) Documentation
Documentation Requirements after Access to EPS Metering Facilities
EPS Meter Test (no changes to the meter)
  EPS Meter Test Report
EPS Meter reprogramming that downloads “meter configuration files”
  EPS Meter Test Report
  MDAS Configuration Form
  Pulse Multiplier Calculation Sheet (if changed)
  Meter Multiplier Calculation Sheet (if changed)
  EPS Meter Program details as downloaded from the certified meter

## Slide 48: Settlement Metering Process 030 (SMOG Appendix A) Documentation
Documentation Requirements after Access to EPS Metering Facilities
EPS Meter reprogramming that uses a specific command to set a specific parameter in the meter that is not used in the calculation of energy or does not map the storage of settlement data in the meter.
  Confirmation that the explanation of the planned work on the “notification e-mail” was the actual work performed
  E-mail confirmation of the date and time period the maintenance was performed
  Confirmation statement that the meter program was not altered, except as specifically documented in the actual work performed

## Slide 49: Settlement Metering Process 030 (SMOG Appendix A) Documentation
Documentation Requirements after Access to EPS Metering Facilities
EPS Meter replacements
  EPS Meter Test Report
  MDAS Configuration Form
  EPS Site Certification Form
  Pulse Multiplier Calculation Sheet (if changed)
  Meter Multiplier Calculation Sheet (if changed)
  EPS Meter Program details in a text file format as downloaded from the certified meter

## Slide 50: Settlement Metering Process 030 (SMOG Appendix A) Documentation
Documentation Requirements after Access to EPS Metering Facilities
EPS instrument transformer replacements
  If no ratios are changed, the following documents are required:
    EPS Site Certification Form
    EPS Meter Test Report (Only phase angle and burden test data required)
    Certification of instrument transformers by the TDSP (Manufacturer Test Report or PE letter) and readable photos of instrument transformer nameplates
  If ratios are changed, following documents are also required:
    EPS Metering Design Proposal
    EPS Meter Program details with EPS Meter Test Report (Accuracy test and phase angle/burden test) or updated multiplier calculation sheets.
    MDAS Configuration Form (if changed)

## Slide 51: Settlement Metering Process 030 (SMOG Appendix A) Documentation
Documentation Requirements after Access to EPS Metering Facilities
Removal of any Facility wiring for site certification or site testing purposes
  EPS Site Certification Form
  Note: To get approval, phase angle data will be required. Otherwise, ERCOT will give provisional approval.
Communication failure that is external to the EPS Meter
  Provide either voice communications to the MDAS Group or e-mail confirmation of repairs to ERCOT at mreads@ercot.com, including the following information:
    Site name
    Meter serial number
    Date and time period the repair was performed
    Explanation of the performed repairs

## Slide 52: Settlement Metering Process 030 (SMOG Appendix A) Documentation
Documentation Requirements after Access to EPS Metering Facilities
Maintenance to non-EPS metering equipment that is connected to the EPS metering circuit
  Testing or programming that does not require the removal of EPS Meter Seals
    Note: The testing of this equipment must not interfere with the accuracy of the energy measured and recorded by the EPS meter, while such equipment is being tested.
    Confirmation that the explanation of the planned work on the “notification e-mail” was the actual work performed
    E-mail confirmation of the date and time period the maintenance was performed
  Replacement, removal or addition of non-EPS metering equipment that is connected to the EPS metering circuit
    Explanation of the planned work on the “notification e-mail”
    Confirmation of the date and time period the maintenance was performed
    EPS Meter Site Certification Form

## Slide 53: Access Notification Tracking
ERCOT will enter the information about the site access in a database and send the TDSP an e-mail which will list the required documentation for the type of access that ERCOT believes has taken place
ERCOT will document the date that they receive the documentation from the TDSP in the database. ERCOT will send another e-mail to the TDSP once all documentation has been received informing them ERCOT has received the documentation and it is pending review by ERCOT
If ERCOT does not receive the documentation within 30 days they will send an e-mail reminding the TDSP about the required documentation and continue to send e-mail reminders every 30 days thereafter until the documentation is received

## Slide 54: Review
Does the ERCOT MDAS Group have a common phone number that rolls over to all MDAS phones?
What extra obligation does the TDSP have, if during an access period for an EPS metering Facility, settlement information is not available from a certified EPS meter?
Is the TDSP required to thoroughly document any access to EPS metering Facilities and submit such documentation to ERCOT?
What documentation is required after an annual meter test where no changes to the meter occurs?
What documentation is required if an EPS meter is replaced?
What documentation is required if any EPS metering Facility wiring is “lifted”?
What documentation is required if replacement of NON-EPS equipment connected in the EPS metering circuit is performed?

## Slide 55: EPS Data Security – TDSP Managed
TDSPs are responsible for data security of the EPS metering Facilities on their system. This responsibility extends to third party contracts and access to EPS metering Facilities. (10.10.1(1))
TDSPs or any Entity authorized to poll EPS Meters may not issue any EPS Meter programming passwords to any Market Participant.(10.10.1(2))
The TDSP shall: {10.10.1.1(1)(a-c)}
  Maintain and modify the passwords for programming and read access to EPS Meters
  Provide the appropriate password access to ERCOT, which will allow ERCOT to synchronize the meter clock
  Establish any other security requirements for accessing the EPS Meters so as to ensure the security of those meters and their meter data

## Slide 56: EPS Data Security – TDSP Managed
The TDSP shall: {10.10.1.1(1)(d-f)}
  Coordinate any EPS Meter programming parameter changes with ERCOT according to this Section, including informing the Load or Resource Entity of any changes to the meter
  Upon request of the Resource Entity that represents an EPS metered Facility, provide the EPS meter “read only” password to such Resource Entity for such Facility and other EPS metered Facility required to calculate their QSE’ load, to the extent that such provision does not violate the Customer Service and Protection Rules of the PUCT
  Modify the “read only” password for EPS meters when a Resource Entity that represents a Facility requests a change due to data security reasons, provided that such modification does not violate the Customer Service and Protection Rules of the PUCT

## Slide 57: EPS Data Security – ERCOT’s Role
Resource Entity must: (10.10.1.3)
Request that the TDSP modify the EPS meter “read only” password for a Facility when the Resource Entity relationships that effect EPS meter data security change. Such request must include the reason for the request
ERCOT may:
Request that TDSP alter the password and other requirements for accessing EPS Meters, as it deems necessary (10.10.1.2)
If, in the reasonable opinion of ERCOT, access granted to a third party in any way interferes with or impedes with ERCOT's ability to poll any EPS Meter, ERCOT may require immediate withdrawal of any access granted to such third party. (10.10.1.4)
  Separate access through additional communications ports may be allowed so long as it does not interfere with ERCOT’s ability to communicate with the meter (10.10.1.4)

## Slide 58: Review
Which entity is responsible for maintaining the data security of EPS meters?
Who is authorized to have the meter programming password for EPS meters?
Who is responsible for maintaining and modifying the passwords for programming and read access to EPS Meters?
Which entities can the TDSP provide a password, that enables them to reset the meter time?
Which entities can the TDSP provide a read only password?
Who is responsible for making a request to the TDSP to modify the EPS meter “read only” password for a Facility when Resource Entity relationships that effect EPS meter data security change?
Under what circumstances can ERCOT request a “read only” password be changed?

## Slide 59: Instrument Transformers (In General)
Shall meet the requirements in the Settlement Metering Operating Guide (SMOG Section 7.3)
Conform to applicable ANSI / IEEE Standards (SMOG Section 7.5.1)
  Meet the minimum BIL Rating as specified in ANSI C12.11 or IEEE standard C57.13-1993 Table 2 appropriate for the designated nominal System voltage or the latest ANSI standard (SMOG Section 7.5.1)
Nameplate information should conform to IEEE C57.13, IEEE Standard Requirements for Instrument Transformers, in effect at the time of instrument transformer manufacture. (SMOG Section 7.5.2)
The TDSP shall ensure that each transformer is subjected to testing as prescribed by the latest ANSI/IEEE C57.13 standards and applicable ANSI/IEEE C57 tests (SMOG Section 7.6)

## Slide 60: Current Transformers
Current Transformers must be wire wound. (SMOG Section 7.5.3)
Accuracy of wire wound: (SMOG Section 7.5.3.5)
Standard – 0.3% accuracy class; or
Optional – 0.15 % accuracy class.
All current transformers shall meet or exceed a continuous current rating factor of: (SMOG Section 7.5.3.7)
    Standard – 1.5 @ 30 degrees C Ambient; or
    Optional – 1.0 @ 30 degrees C Ambient.

## Slide 61: Voltage- Transformers
Transformer windings shall consist of a single primary winding and one or more tapped secondary windings. (SMOG Section 7.5.4.1)
All voltage transformers shall have accuracy of: (SMOG Section 7.5.4.4)
Standard – 0.3% accuracy class; or
Optional – 0.15% accuracy class.
The thermal burden rating of voltage transformers shall meet the standards defined in IEEE Standard C57.13. (SMOG Section 7.5.4.5)
Combination current/voltage transformers shall maintain the same electrical, accuracy and mechanical characteristics as individual CT’s and VT’s. Physical dimensions may vary according to design. (SMOG Section 7.5.5)
Capacitive Coupled Voltage Transformers (CCVTs) must be tested for accuracy periodically. (10.6.1.2(2) & NPRR948)

## Slide 62: EPS Meters
Meters must comply with:
ANSI C12 standards (SMOG Section 6.2)
ERCOT Protocols (10.9.1)
ERCOT Settlement Metering Operating Guide (10.9.1)
Meters must:
be multifunction (SMOG Section 5.2(c))
be capable of remote time sync (SMOG Section 5.2(e))
have battery back-up (SMOG Section 5.2(g))
be capable of remote interrogation (SMOG Section 5.2(h))
have 45 days data storage capability (SMOG Section 5.2(i))
be approved by TDSP (SMOG Section 6.12.2)
Installation must:
have adequate phone surge protection (SMOG Section 5.2(j))

## Slide 63: TDSP EPS Meter Approval
Meter manufacturer must perform the following tests:
(SMOG Section 6.12.1)
Compliance with applicable ANSI/NEMA standards.
Meet the requirements specified in the Protocols & SMOG.
TDSP has the responsibility for assuring accuracy, integrity and MDAS compatibility of EPS Meters.
(SMOG Section 6.12.2)
Maintain the following documentation:
- List of all meter manufacturer(s) and type(s) used:
  Firmware version
  Software version
  Date product was deployed
  Date product was discontinued; including reasoning for discontinuance.
A manufacturer letter certifying compliance.
Manufacturer’s testing certification documentation
Drawings and manufacturer’s instruction booklets
Manufacturer’s technical/maintenance manuals
Software and associated documentation for the following:
  · Programming
  · Diagnostics
  · Data Retrieval (meter reading)
Changes:
See Settlement Metering Guide
(SMOG Section 6.12.3)

## Slide 64: TDSP Approved Meters for EPS Metering
“ERCOT DOES NOT recommend, certify or approve meters”
The TDSP is required to ensure that the meters the TDSP approves for use on EPS metering facilities meet or exceed all of the requirements of:
  ERCOT Protocols “Section 10 Metering”
  Settlement Metering Operating Guide (SMOG)

## Slide 65: EPS Meter Programming
Channel Assignment: (SMOG Section 4.1)
Unidirectional Loads
Bi-directional Meters & All Generation Meters
WSL Meter with Resource Entity Calculated Auxiliary Load.
Display Modes:
Normal: (SMOG Section 4.2.1)
Alternate: (SMOG Section 4.2.2)
Test: (SMOG Section 4.2.3)
Additional Items:
TLC (SMOG Section 4.3 & Section 8)
Power Outage Flagging (SMOG Section 4.4)
Error Event Logging (SMOG Section 4.5 & Section 6.5.4)
IDR Pulse Resolution (SMOG Section 4.6.1)
IDR Clock (Protocols 10.9.1 (2)(g) & SMOG Section 6.8.2)

## Slide 66: Resource Entity-Owned Equipment Used for the Calculation of the Auxiliary Load Telemetry
Detailed Standards: (SMOG 5.5)
(1) Data Recording Function for Calculated Auxiliary Load:
(a) Auxiliary Load calculated data shall be stored in a Resource Entity storage device such that a minimum of 45 days of 15-minute interval energy is available; and
(b) Recording of data shall continue while communicating through any communications port.
(2) Calculated auxiliary Load must be telemetered to both the primary and backup ERCOT-Polled Settlement (EPS) Meter.
(3) The EPS Meters must be updated with an auxiliary Load calculation at least every four seconds.

## Slide 67: Review
What industry standard must all instrument transformers used at EPS metering Facilities be tested to?
Can combination voltage and current transformers be used at EPS metering Facilities?
What industry standard must all EPS meters comply with?
What other documents must all EPS meters comply with?
What organization approves EPS Meters?
Are there specific channel assignments for storage of interval data in EPS meters?
Are there specific error event logging requirements for EPS meters?
What is the IDR pulse resolution requirement for EPS meters?

## Slide 68
BREAK

## Slide 69: EPS Meter Installation Facility Requirements
Metering Facility(SMOG Section 1.5)
Environment {1.5.1 (1)}
Clear Area {1.5.1 (2)}
Test Output {1.5.2}
Enclosure {1.5.2 (a)}
Lighting {1.5.2 (b)}
Voltage Transformers
Quantity (SMOG Section 1.4.1)
Burden (SMOG Section 1.4.2)
Protection (SMOG Section 1.4.3)
Secondary Wiring (SMOG Sec.1.4.4)
Grounding (SMOG Section 1.4.5)
Induced Voltage (SMOG Sec. 1.4.6)
Inactive Potential (SMOG Sec. 6.5.4(1)(k))
Current Transformers (SMOG Sec. 1.3)
  Fault Currents (1.3.1)
  Quantity (1.3.2)
  Burdens (1.3.3)
  No Relays (1.3.4 (3))
  Secondary Wiring (1.3.4)
  Grounding (1.3.5)
  Induced Voltage (1.3.6)
  Paralleling (1.3.7)
  Sizing (1.3.8)
Test Switches {SMOG 1.5.2 (c & d)}

## Slide 70: EPS Meter Installation Facility Requirements
SMOG 1.5.1 Metering Facility Specification
  (1) The environment for the ERCOT-Polled Settlement (EPS) Metering equipment shall be designed such as to maintain at all times the operating characteristics as stated by the meter manufacturer.
  (2) A clear space shall be provided in front of the meter as outlined in the latest revision of Institute of Electrical and Electronics Engineers (IEEE) C2, The National Electric Safety Code, Article 125a applicable at time of original installation.

## Slide 71: EPS Meter Installation Facility Requirements
SMOG 1.5.2 Facilities for Testing
Test switches should be located at, or near the metering devices. Where the test output of the meter is electrical rather than visual, provisions should be made to conveniently measure the test output.
  (a) The meters and test facilities should be located inside an enclosure or structure that provides adequate protection of the equipment from the environment.
  (b) Adequate lighting should be provided in the area of meters as required for testing, maintenance and adjustment.

## Slide 72: EPS Meter Installation Facility Requirements
SMOG 1.5.2 Facilities for Testing Continues
  (c) Test switches shall be wired to allow individual meters to be removed from service for testing without affecting other meters in the circuit.
  (d) When an automatic current shorting “relay” test block is used to test meters, meters shall be wired such that the testing of individual meters does not affect other meters in the circuit.

## Slide 73: EPS Meter Installation Facility Requirements
SMOG 1.3 Current Transformers
  1.3.1 Fault Withstand
    Shall be capable of withstanding available fault current levels.
  1.3.2 Quantity
    Shall be installed - one in each phase for 4-wire wye neutral grounded system, or two phases for three-wire system
    May be installed – in two phases for 3-wire wye neutral grounded system if phase-to-ground loads or phase-to-ground sources are not connected between the metering point and the power transformer primary windings.
      May have power equipment connected to EPS Metering facilities as long as not provide a path for ground current (excl. PT/Surge protestors)
      TDSP shall verify all power transformer connections behind the meter point are ungrounded or phase to phase (verified annually)
      PE shall provide certification of three VT two CT metering accuracy
    May be installed - in two phases for 3-wire wye high or low impedance grounded distribution system if phase-to-ground loads or phase-to-ground sources are not connected behind the metering point and the high or low impedance ground is installed as part of a fault monitoring system for the facility
      TDSP shall verify existence of high/low impedance ground with fault monitoring circuit at initial certification and every three years
      Resource owner provides PE letter stating that phase to ground loads are not supported
  1.3.3 Burden
    Shall be kept as small as practical and shall not exceed the burden rating
    Shall be checked during annual testing.

## Slide 74: EPS Meter Installation Facility Requirements
SMOG 1.3 Current Transformers Continues
  1.3.4 Secondary Wiring
    (1) No splices will be allowed in the current transformer secondary circuit except through the use of terminal block connections.
    (3) The metering circuit should be limited to highly accurate billing meters and load control transducers. Relays shall not be connected to the secondary metering circuit.
(2) The integrity of the secondary wiring of the current transformers shall be verified at initial certification and at least every three years thereafter.

## Slide 75: EPS Meter Installation Facility Requirements
SMOG 1.3 Current Transformers Continues
  1.3.5 Grounding of Current Transformer Secondary Circuits
    (1) A common return conductor shall be utilized for each set of isolated current transformer secondary windings.
    (2) The common terminals of each set of current transformers shall be grounded at only one point.
    (3) It is recommended that the ground connection be located at the meter or at the nearest terminal block to the meter.
    (4) The ground conductor shall be, at a minimum, the same wire size as the smallest polarity conductor in the metering current circuit.

## Slide 76: EPS Meter Installation Facility Requirements
SMOG 1.3 Current Transformers Continues
  1.3.6 Induced Voltage
    (1) Secondary circuits should be designed and routed so as to avoid the possibility of induced voltages and the effects of high ground fault voltages.
    (2) Suitable protection against the effects of fault and switching generated over-voltages should be provided.
  1.3.8 Sizing of Current Transformers
    (1) Current transformers shall be sized for optimum metering accuracy, considering peak, nominal and minimum loads, current transformer rated accuracy, rating factor, and ability to withstand available fault current.
    (2) Optimum metering accuracy may require
      (a) Rating factor greater than 1.0, and/or
      (b) High accuracy, extended range current transformers

## Slide 77: EPS Meter Installation Facility Requirements
SMOG 1.3 Current Transformers Continues
  1.3.7 Paralleling of Current Transformers
  Paralleling of current transformers is not recommended. However, when it is necessary, the following requirements apply.
    (a) Must have the same nominal ratio regardless of the ratings of the circuits in which they are connected.
    (b) Must be connected to the same phase of the primary circuits
    (c) Shall be paralleled at the meter test switch and connected in a configuration to allow for testing of individual
    (d) Only one ground. Recommend ground be located at the meter or at the nearest terminal block to the meter
    (e) Support n times the common burden plus its own individual burden and stay within the accuracy class of the transformers, n = # of CTs in parallel
    (f) A common voltage must be available for the meter
    (g) Meter must have sufficient current capacity to carry the sum of the currents from all CTs
    (h) Maximum possible burden placed on any transformer does not exceed its adjusted burden rating, as defined in (e)

## Slide 78: EPS Meter Installation Facility Requirements
SMOG 1.4 Voltage Transformers
  1.4.1 Quantity
    Three single-phase units or one three-phase unit for 4-wire wye
    Two single-phase units for three-wire ungrounded systems
    Installation three VTs for use with two-stator metering is allowed under the following conditions ensured by TDSP:
      No path for ground current of EPS Metering facilities connected to neutral grounded transmission system
      VTs are connected to the grounding system of the transmission facility for the voltage reference
      Meter potential elements - connected from phase to common phase on secondary of VTs.
      Secondary circuit of metering potentials - connected to the grounding system of the transmission facility.
    VTs may be connected from a phase with a CT to a phase with no CT in a 3-wire wye high/low impedance grounded distribution system with no phase to ground loads/sources connected and ground is used for fault monitoring if:
      TDSP verify existence of high/low impedance ground with fault monitoring circuit at initial certification and every three years
      Resource owner provides PE letter stating that phase to ground loads are not supported

## Slide 79: EPS Meter Installation Facility Requirements
SMOG 1.4 Voltage Transformers Continues
  1.4.2 Burden
    VT burdens shall be kept as small as practical
    Total burden/volt-ampere rating of the voltage transformer shall not be exceeded
  1.4.3 Protection
    Secondary fuses should be of the high-speed, high current interrupting construction with low electrical impedance and the mechanical ruggedness to resist the effects of corrosion and vibration. The main purpose of fuses shall be for protection of personnel, the transformer, and the secondary wiring against accidental faults or shorts, rather than to protect the voltage components of the measuring devices. Fuses shall not be placed in the common secondary return or the ground circuit of instrument transformers
  1.4.4 Secondary Wiring
    All secondary wiring shall be designed such that the maximum voltage drop at the metering devices does not exceed 0.3 Volts. A voltage drop calculation or measurement shall be performed as part of the initial installation.
    The integrity of the secondary wiring of the voltage transformers shall be verified at initial certification and at least every three years thereafter.
    No splices will be allowed in the voltage transformer secondary circuit except through the use of terminal block connections.

## Slide 80: EPS Meter Installation Facility Requirements
SMOG 1.4 Voltage Transformers Continues
  1.4.5 Grounding of Voltage Transformer Secondary
    (1) Each set of voltage transformer secondary windings shall have only one ground.
    (2) It is recommended that the ground connection be located at the meter or at the nearest terminal block to the meter.
  1.4.6 Induced Voltage
    Secondary circuits should be designed and routed so as to avoid the possibility of induced voltages and the effects of high ground fault voltages.
    Suitable protection against the effect of fault and switching generated over-voltages should be provided.

## Slide 81: EPS Meter Event Logging Requirements
SMOG 6.5.4 Event Logging
(1) EPS Meters shall be capable of logging the following events:
  (a) Hardware Errors: Various hardware malfunctions (i.e., modem card/chip, measurement chip, central processing unit (CPU), etc.), whether fatal or not.
  (b) Firmware Errors: Firmware has a checksum error, watchdog time out error, or other problem with the firmware, whether fatal or not.
  (c) Random-Access Memory (RAM) and Read-Only Memory (ROM) Errors: Bad spots in memory identified via checksum or other means.
  (d) Pulse Overflow Errors: The maximum size value for the number of pulses per interval in Load Profile has been exceeded. This does not apply to meters that store/report data in engineering units.
  (e) Low Battery Condition: Low battery has been sensed during initial power up, daily self checks, after power outages, or any other means to check for a low battery condition.
  (f) AC Power Up: When the meter electronics are powered up either via auxiliary power or connected to system power.
  (g) AC Power Down: When the meter electronics loses power either by auxiliary power or connected to system power.

## Slide 82: EPS Meter Event Logging Requirements
SMOG 6.5.4 Event Logging Continues
(1) EPS Meters shall be capable of logging the following events:
  (h) Configuration Changed: Meter has been reprogrammed, or any meter programming where a settlement metering parameter is changed.
  (i) Clock Set/Change: The meter Real-Time clock has been set/changed by external sources.
  (j) Test Mode Activation: Meter going into and out of “test mode.”
  (k) Inactive Potential/Phase Failure: System phase voltage falls below 75% – 85% of the nominal voltage value for 0 – 10 second(s). Nominal value for this event is defined as the primary or secondary voltage rating of the voltage transformer to which the EPS meters are connected, as specified on the name plate, manufacturer test report or Professional Engineer letter. The ability to log subsequent inactive potential events shall occur once voltage is greater than 75% – 95% of nominal for 0 – 10 second(s). The TDSP shall ensure that the meter set points are within the specified ranges for the voltage and time thresholds referenced above.
  (l) Loss of telemetry: For meters that have a telemetered Wholesale Storage Load (WSL) auxiliary Load signal, the loss of the signal shall be recorded.
  (m) Restoration of telemetry: For meters that have a telemetered WSL auxiliary Load signal, the restoration of the signal after a loss shall be recorded.
(2) The events described in paragraph (1) above shall be reported when interrogated by ERCOT MDAS.

## Slide 83: Update Information From the ERCOT.com Website
Navigation of the website will be demonstrated in class. Important links are listed below for reference at a later date.
ERCOT Website: http://www.ercot.com/
Metering related pages:
EPS Metering: http://www.ercot.com/mktinfo/metering/eps/
Competitive Metering: http://www.ercot.com/mktinfo/metering/competitive/
Protocols: http://www.ercot.com/mktrules/nprotocols/current
SMOG: http://www.ercot.com/mktrules/guides/settlement/library
Committees and Groups: http://www.ercot.com/committees/
Metering Working Group: http://www.ercot.com/committees/wms/mwg

## Slide 84
The End