## Slide 1
Resource Integration Topics
Jay Teixeira
ERCOT
Resource Integration Working Group
June 22, 2021

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in previous QSA’s
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic Model Review
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline
PSSE Model Quality Test Required
PSCAD Model Quality Test and Unit Model Validation required for August 1, 2021 QSA
TSAT Model Required – If PSSE model is UDM, then TSAT model should be UDM by November 1, 2021.

## Slide 4: GINR Time Line (Fastest)

## Slide 5: Recent Issues
VSS Tests
  Very low margin at MW4 point
  Shunt devices can only make up losses
  Enter losses in latest reactive test template
Self-Limiting Facilities
  Accepting
  Be aware of Jan 1, 2023 possible slippage

## Slide 6: Battery Registration
Protocol 16.5(6) says
(6) A Resource Entity representing an Energy Storage Resource (ESR) shall register the ESR as both a Generation Resource and a Controllable Load Resource.
[NPRR1002: Replace paragraph (6) above with the following upon system implementation:]
(6) A Resource Entity representing an ESR shall register the ESR as an ESR. ERCOT systems, including the Energy and Market Management System (EMMS) and Settlement system, shall continue to treat the ESR as both a Generation Resource and a Controllable Load Resource until such time as all ERCOT systems are capable of treating an ESR as a single Resource.
NPRR 1002 is part of Passport and will not be implemented at a TBD point sometime after 2024
Batteries will continue to be treated as GR for interconnection process and commissioning testing.
  Charging mode will not be part of AVR and VSS tests for now
  Capability should exist since protocol requirements written
  Charging mode reactive capability could be tested at next AVR or reactive verification test

## Slide 7: Active RR’s
RRGRR028, submitted by John Karlik on behalf of the SPWG on December 23, 2020, Transformer Impedance Clarifications. ROS approved 06/03/2021. Next at TAC.
PGRR091, FIS Application Completion 60-Day Limit. Approved at ROS on June 3, 2021. Next IA review at ROS.
NOGRR223, Add Phasor Measurement Recording Equipment Requirement to Modified Generating Facilities in Interconnection Process. Remains tabled at OWG.
NOGRR227, Add Phasor Measurement Recording Equipment Location for Main Power Transformer for Intermittent Renewable Resource (IRR). OWG consensus back to ROS.

## Slide 8: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department
Mailing List
  RESOURCE_INTEGRATION@LISTS.ERCOT.COM

## Slide 9: Questions?
Thank you!