## Slide 1: DWG Report to ROS
Sam Jung – DWG Chair
July 8th, 2021

## Slide 2: DWG Update
DWG WebEx meeting held on 6/24/2021
TAC Item 30/NOGRR 226/Emergency Condition Item 121
  UFLS Threshold Adjustment

## Slide 3: Under-Frequency Load Shed (UFLS)
Current UFLS stages are:
Stage 1 – 59.3 Hz
Stage 2 – 58.9 Hz
Stage 3 – 58.5 Hz
NOGRR 226 proposes to raise the Stage 1 threshold to 59.4 Hz to align with generator tripping threshold

## Slide 4: DWG Response
DWG believes the threshold adjustment is not necessary
Generator tripping during the winter storm was due to cold weather, not low frequency
Raising the frequency threshold will have a significant impact on field operations
UFLS is designed to be a safety-net, and the system should rely more on its natural inertia
DWG would like a clear understanding on exactly what is expected from DWG (thoughts, studies, etc.)