## Slide 1
ERCOT Frequency Control Report
June 2021
ERCOT
Operations Planning
PDCWG | July 16th, 2021

## Slide 2: Summary of June 2021
CPS1: 172.74%
Current CPS1 12-Month Rolling Average: 168.87%
2 BAAL Exceedance(s)
1 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2019 BAAL-003 FRM Performance: -811.14
2021 RMS1 Statistics
  Mean: 16.89 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 37,331,144 MWh
  Wind Energy: 6,965,821 MWh
  Percent Energy from Wind: 18.66%
  Solar Energy: 1,643,972 MWh
  Percent Energy from Solar: 4.40%
Minimum System Inertia
  Mean: 243,333 MW*s
  Max: 312,057 MW*s on Jun 15th
  Min: 190,893 MW*s on Jun 6th
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jun-21 CPS1 (%): 172.74
Notes: 1. 97.58% @ 06/25/2021 17:00
Expected Generation Deviation
Expected gen dev remained negative for the most part of the hour. The largest expected gen dev was -2300MW @ 17:15 with contribution from thermal, wind and solar.
IRR Ramps
Solar generation ramped down by 800 MW between 17:05 and 17:12.
LOAD:
Increase in non-conforming load by 350 MW which coincided with the solar ramp down.
Regulation: Regulation up was exhausted during the solar ramp down period
Other
SCED was run manually multiple times and Manual offset of 200 MW @ 17:11

## Slide 5: BAAL Exceedances & Violations
There were 2 BAAL exceedance(s) in June
Notes: Occurred on 06/7/2021 (2)

## Slide 6: 15-Minute Average CPS1%
Jun-21 CPS1 (%): 172.74

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 168.87%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.89 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2019 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2019 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 37,331,144 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,965,821 MWh

## Slide 23: % Energy from Wind Generation
Notes: 18.66%

## Slide 24: Total Energy From Solar Generation
Notes: 1,643,972 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.40%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 190,893 MW*s on 6/6/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 243,333 MW*s
Max: 312,057 MW*s on Jun 15th
Min: 190,893 MW*s on Jun 6th

## Slide 28: Questions?
Thank you!