## Slide 1
SODG Feb. Event RFI Summary
TAC Emergency Conditions Item 98
Shane Thomas
ERCOT
7/30/21

## Slide 2: Total Effected Units
305 Registered Units as of Event
  >95% Response to RFI
153 Registered SODGs Effected (~50%)
  371.22MW (~39%)
36.1% of Units Effected by Load Shed
  23% of Registered MW
27.9% of Units Effected by Frequency
  29.7% of Registered MW

## Slide 3: Restoration Issues

## Slide 4: Islanding Units & Communication Issues
Islands
  55 Units
  ~24MW of Islands
Communication Issues
  12 Units with Loss of Cell Service
  1 Unit Receiving Bad Meter Data

## Slide 5: Fuel Supply Issues
Non-Renewable Units
  25 Units
  184 MW
Renewable Units
  15 Units Experienced Icing
  1 Unit Fuel Was Too Cold
  Solar Output Depressed
    Solar Forecast Low Due to Cloud Coverage
    Responses Varied as to Effects From Snow

## Slide 6: Self Dispatched Based on ERCOT Prices
202 Units Dispatched
  66% of Registered Units
357MW Dispatched

## Slide 7: TAC Emergency Conditions Item 98 Discussion
Could more DERs have helped? In addition to settlement-only DERs (between 1 and 10 MWs) is more needed to be done for a heavy-version of DERs so they can compete in energy and ancillary market more directly or is the current DER-light approach good enough?

## Slide 8: Current “DER Heavy*” Status
Protocol Revision Approved by BOD Aug. 2020
Temporary Moratorium Until Revisions Implemented
  Expected to End Q1 2022
  41 Affidavits Received to Proceed with Interconnection During Moratorium
    ~133MW DESR Installed
    26 Units/~228MW Approved to Start Interconnection Process
Recommend Status Update from “Not Started” to “Complete Expected Q1 2022”
*DER Heavy as defined in DER Concept Paper from 2015 - http://www.ercot.com/content/wcm/key_documents_lists/86442/ERCOT_DER_Whitepaper_082015.doc