## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
August 05, 2021

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs & IMFR
    4 FMEs in the month of June
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 07/16/2021
  Review of emergency conditions list from ROS
  February cold weather event follow up discussion
  ROS Action item – Ancillary Service questions
  ERCOT reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 4 FMEs in June
  6/7/2021 15:26:43
    Loss of 1324 MW generation
    Interconnection Frequency Response: 1151 MW/0.1 Hz
    11 of 56 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    11 of 56 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  6/12/2021 13:23:56
    Loss of 503 MW generation
    Interconnection Frequency Response: 1324 MW/0.1 Hz
    13 of 57 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    13 of 57 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  6/14/2021 9:55:52
    Loss of 566 MW of load (lots of evaluations; lots of failures)
    Interconnection Frequency Response: 1230 MW/0.1 Hz
    118 of 262 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    99 of 262 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  6/20/2021 22:53:33
    Loss of 556 MW of generation
    Interconnection Frequency Response: 830 MW/0.1 Hz
    9 of 44 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 44 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: High Frequency FME on 6/14
  Some additional metrics for FME on 6/14/2021 9:55:52
    Of the 118 units that failed Initial Primary Frequency Response, 38 were Wind units (32% of failures), 31 were Combined Cycles (26% of failures), and 26 were Solar units (22% of failures)
    Frequency response of other unit types (non-CC thermals and hydro units) was generally good
    The 38 Wind unit failures represents 30% of the online Wind units
    The 31 Combined Cycle unit failures represents 50% of the online CC units
    The 26 Solar unit failures represents 49% of the online Solar units

## Slide 8: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 471 MW/0.1 Hz
IMFF Performance currently
1080.34 MW/0.1HZ

## Slide 9
Questions?

## Slide 10: Frequency Control Report
June 2021

## Slide 11: CPS1 Performance
Current 12-Month Rolling Average: 168.87%

## Slide 12: RMS1 Performance of ERCOT Frequency

## Slide 13: Frequency Profile Analysis

## Slide 14: Time Error Corrections

## Slide 15: ERCOT Total Energy
Notes: 37,331,144 MWh

## Slide 16: ERCOT Total Energy from Wind Generation
Notes: 6,965,821 MWh

## Slide 17: ERCOT % Energy from Wind Generation
Notes: 18.66%

## Slide 18: ERCOT Total Energy from Solar Generation
Notes: 1,643,972 MWh

## Slide 19: ERCOT % Energy from Solar Generation
Notes: 4.40%