## Summary
| Date | Summary of Changes
DWG Approved: | 2021-06-24 | Creation of document
Link to NERC DER_A Parameterization Guideline:
https://www.nerc.com/comm/PC_Reliability_Guidelines_DL/Reliability_Guideline_DER_A_Parameterization.pdf

## DESR
| DESRs (energy storage DGRs) that meet Nodal Operating Guide requirements |  |  | Expect parameters in blue boxes to change between gen type (solar, energy storage), ERCOT registration type, NOG ride-through exemptions
Base of IEEE 1547-2018 with NOGRR212 updates
| Parameter | Value | Parameter Name | Notes
M | PfFlag | 1 | Power factor flag (1: constant power factor, 0: constant Q control) | NERC default
M+1 | FrqFlag | 1 | Frequency flag (1: enabled, 0: disabled) | NERC default - 2018
M+2 | PQFlag | 0 | Active or reactive current priority (1: priority for current limit, 0: Q priority) | NERC default - 2018
M+3 | GenFlag | 0 | Gen flag (1: unit is a generator, 0: unit is a storage device) | DESR's are storage
M+4 | VtripFlag | 1 | Voltage trip flag (1: enable, 0: disable) | Left out of NERC parameterization guideline table
M+5 | FtripFlag | 1 | Frequency trip flag (1: enable, 0: disable) | Left out of NERC parameterization guideline table
J | Trv | 0.02 | voltage measurement transducer time constant | NERC default
J+1 | Trf | 0.02 | frequency measurement transducer time constant | Left out of NERC parameterization guideline table, but is in other documentation
J+2 | dbd1 | -99 | lower voltage deadband | NERC default
J+3 | dbd2 | 99 | upper voltage deadband | NERC default
J+4 | Kqv | 0 | proportional voltage control gain | NERC default
J+5 | Vref0 | 0 | user specified voltage set-point | NERC default
J+6 | Tp | 0.02 | power measurementtransducer time constant | NERC default
J+7 | Tiq | 0.02 | Q-control time constant | NERC default
J+8 | Ddn | 20 | Downard Frequency Responsiveness for Overfrequency Conditions | NERC default - 2018. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+9 | Dup | 20 | Upward Frequency Responsiveness for Underfrequency Conditions | NERC default - 2018 capability allows for responsiveness. Set to 0 when assuming DERs are operated at Pmax with no room to respond up. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+10 | fdb1 | -0.000283 | Frequency Deadband | ERCOT deadband
J+11 | fdb2 | 0.000283 | Frequency Deadband | ERCOT deadband
J+12 | femax | 0.01 | Frequency Error Limits | Model tuning edit
J+13 | femin | -0.01 | Frequency Error Limits | Model tuning edit
J+14 | Pmax | 1 | Maximum power limit (pu) | NERC default
J+15 | Pmin | -1 | Minimum power limit (pu) | NERC default is 0. But -1 can be used for energy storage
J+16 | dPmax | 1 | Power reference max ramp rate (> 0) | Model tuning edit
J+17 | dPmin | -1 | Power reference min ramp rate (< 0) | Model tuning edit
J+18 | tpord | 1 | Power-order time constant, small lag time associated with frequency flag | Model tuning edit
J+19 | Kpg | 0.1 | PI controller proportional gain | NERC default - 2018
J+20 | Kig | 10 | PI controller integral gain | NERC default - 2018
J+21 | lmax | 1.2 | Maximum converter current (pu) | NERC default
J+22 | vl0 | 0.5 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44. When voltage falls below vl1, a fraction of the DERs will cutout, with a linearly increasing amount of DERs experiencing cutouts down to vl0 where all DERs will have cut out. vl0 can be set to the highest undervoltage point in which momentary cessation starts occurring. In cases where momentary cessation of inverter-based resources needs to be represented, use vl1 and vl0 with extended trip times. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+23 | vl1 | 0.5 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44
J+24 | vh0 | 1.21 | inverter voltage break-point for high voltage cut-out | NERC default is 1.2
J+25 | vh1 | 1.21 | inverter voltage break-point for high voltage cut-out | NERC default is 1.15
J+26 | tvl0 | 10 | low voltage cut-out timer for vl0 | NERC default is 0.16.
J+27 | tvl1 | 1 | low voltage cut-out timer for vl1 | NERC default is 0.16.
J+28 | tvh0 | 12 | low voltage cut-out timer for vh0 | NERC default is 0.16
J+29 | tvh1 | 12 | low voltage cut-out timer for vh1 | NERC default is 0.16
J+30 | Vrfrac | 1 | Fraction of Resources Recovering | NERC default is Vrfrac = 1 for 2018 (all recover), Vrfrac = 0 for 2003 (none recover)
J+31 | fltrp (fl) | 57 | inverter frequency break-point for low frequency cut-out | ERCOT requires ride-through down to = 57 Hz
J+32 | fhtrp (fh) | 61.8 | inverter frequency break-point for high frequency cut-out | ERCOT requires ride-through up to = 61.8 Hz
J+33 | tfl | 0.16 | low frequency cut-out timer for fl | NERC default. ERCOT NOG has minimum ride-through time of 299 seconds when between 57-61.8 Hz
J+34 | tfh | 0.16 | high frequency cut-out timer for fh | NERC default. ERCOT NOG has minimum ride-through time of 299 seconds when between 57-61.8 Hz
J+35 | tg | 0.02 | current control time constant (> 0) | NERC default
J+36 | rrpwr | 2 | Active Current Recovery Ramp Rate | NERC default - 2018
J+37 | Tv | 0.02 | Time constant on the output of the multiplier | NERC default
J+38 | vfth (Vpr) | 0.3 | Low voltage frequency tripping | NERC default - 2018
J+39 | Iqhl | 1 | Reactive current injection limits | NERC default - 2018
J+40 | Iqll | -1 | Reactive current injection limits | NERC default - 2018

## DESR model test - Discharge 80%
DESRs
IEEE 1547-2018 base used with edits made to for voltage/frequency ride-through and model tuning

## DESR model test - Charge 80%
DESRs
IEEE 1547-2018 base used with edits made to for voltage/frequency ride-through and model tuning

## DESR model test - 0% dispatch
DESRs
IEEE 1547-2018 base used with edits made to for voltage/frequency ride-through and model tuning
Notes:
When modeling with Pgen = 0 MW, there were odd VAR responses for LVRT and Frequency tests
This could be a PSSE implementation issue that would need a work around for our flatstart
The following results are "zero" dispatch with Pgen = 0.01 MW (similar results for Pgen = -0.01 MW)

## DESR FRT exemption
| DESRs with FRT exemption |  |  | Expect parameters in blue boxes to change between gen type (solar, wind, energy storage), ERCOT registration type, NOG ride-through exemptions
Base of 1547-2003 but with VRT requirements applied and frequency response enabled
| Parameter | Value | Parameter Name | Notes
M | PfFlag | 1 | Power factor flag (1: constant power factor, 0: constant Q control) | NERC default
M+1 | FrqFlag | 1 | Frequency flag (1: enabled, 0: disabled) | Frequency response is still expected
M+2 | PQFlag | 1 | Active or reactive current priority (1: priority for current limit, 0: Q priority) | NERC default - 2003
M+3 | GenFlag | 0 | Gen flag (1: unit is a generator, 0: unit is a storage device) | The online SODGs are solar and wind (SODG storage will be offline)
M+4 | VtripFlag | 1 | Voltage trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
M+5 | FtripFlag | 1 | Frequency trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
J | Trv | 0.02 | voltage measurement transducer time constant | NERC default
J+1 | Trf | 0.02 | frequency measurement transducer time constant | Left out of NERC parameterization guideline table, but is in other documentation
J+2 | dbd1 | -99 | lower voltage deadband | NERC default
J+3 | dbd2 | 99 | upper voltage deadband | NERC default
J+4 | Kqv | 0 | proportional voltage control gain | NERC default
J+5 | Vref0 | 0 | user specified voltage set-point | NERC default
J+6 | Tp | 0.02 | power measurementtransducer time constant | NERC default
J+7 | Tiq | 0.02 | Q-control time constant | NERC default
J+8 | Ddn | 20 | Downard Frequency Responsiveness for Overfrequency Conditions | Frequency response is still expected. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+9 | Dup | 20 | Upward Frequency Responsiveness for Underfrequency Conditions | Frequency response is still expected. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+10 | fdb1 | -0.000283 | Frequency Deadband | Frequency response is still expected
J+11 | fdb2 | 0.000283 | Frequency Deadband | Frequency response is still expected
J+12 | femax | 0.01 | Frequency Error Limits | Frequency response is still expected. Used when Frequency flag is enabled
J+13 | femin | -0.01 | Frequency Error Limits | Frequency response is still expected. Used when Frequency flag is enabled
J+14 | Pmax | 1 | Maximum power limit (pu) | NERC default
J+15 | Pmin | -1 | Minimum power limit (pu) | DESR
J+16 | dPmax | 99 | Power reference max ramp rate (> 0) | NERC default
J+17 | dPmin | -99 | Power reference min ramp rate (< 0) | NERC default
J+18 | tpord | 1 | Power-order time constant, small lag time associated with frequency flag | Model tuning edit
J+19 | Kpg | 0.1 | PI controller proportional gain
J+20 | Kig | 10 | PI controller integral gain
J+21 | lmax | 1.2 | Maximum converter current (pu) | NERC default
J+22 | vl0 | 0.5 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44. When voltage falls below vl1, a fraction of the DERs will cutout, with a linearly increasing amount of DERs experiencing cutouts down to vl0 where all DERs will have cut out. vl0 can be set to the highest undervoltage point in which momentary cessation starts occurring. In cases where momentary cessation of inverter-based resources needs to be represented, use vl1 and vl0 with extended trip times. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+23 | vl1 | 0.5 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44
J+24 | vh0 | 1.21 | inverter voltage break-point for high voltage cut-out | NERC default is 1.2. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+25 | vh1 | 1.21 | inverter voltage break-point for high voltage cut-out | NERC default is 1.15
J+26 | tvl0 | 10 | low voltage cut-out timer for vl0 | NERC default is 0.16.
J+27 | tvl1 | 1 | low voltage cut-out timer for vl1 | NERC default is 0.16.
J+28 | tvh0 | 12 | low voltage cut-out timer for vh0 | NERC default is 0.16
J+29 | tvh1 | 12 | low voltage cut-out timer for vh1 | NERC default is 0.16
J+30 | Vrfrac | 0 | Fraction of Resources Recovering | NERC default is Vrfrac = 1 for 2018 (all recover), Vrfrac = 0 for 2003 (none recover)
J+31 | fltrp (fl) | 59.3 | inverter frequency break-point for low frequency cut-out | NERC default - 2003
J+32 | fhtrp (fh) | 60.5 | inverter frequency break-point for high frequency cut-out | NERC default - 2003
J+33 | tfl | 0.16 | low frequency cut-out timer for fl | NERC default
J+34 | tfh | 0.16 | high frequency cut-out timer for fh | NERC default
J+35 | tg | 0.02 | current control time constant (> 0) | NERC default
J+36 | rrpwr | 0.1 | Active Current Recovery Ramp Rate | NERC default - 2003
J+37 | Tv | 0.02 | Time constant on the output of the multiplier | NERC default
J+38 | vfth (Vpr) | 0.8 | Low voltage frequency tripping | NERC default - 2003
J+39 | Iqhl | 0 | Reactive current injection limits | NERC default - 2003
J+40 | Iqll | 0 | Reactive current injection limits | NERC default - 2003

## DESR FRT XMT - Discharge 80%
DESRs with frequency ride-through exemption
IEEE 1547-2003 base with edits made to follow voltage ride-through requirements and frequency response

## DESR FRT XMT - 0% dispatch
Notes:
When modeling with Pgen = 0 MW, there were odd VAR responses for LVRT and Frequency tests
This could be a PSSE implementation issue that would need a work around for our flatstart
DESRs with frequency ride-through exemption
IEEE 1547-2003 base with edits made to follow voltage ride-through requirements and frequency response
Notes:
When modeling with Pgen = 0 MW, there were odd VAR responses for LVRT and Frequency tests
This could be a PSSE implementation issue that would need a work around for our flatstart
The following results are "zero" dispatch with Pgen = 0.01 MW (similar results for Pgen = -0.01 MW)

## DESR VRT exemption
| DESRs with VRT exemption |  |  | Expect parameters in blue boxes to change between gen type (solar, wind, energy storage), ERCOT registration type, NOG ride-through exemptions
Base of 1547-2003 but with FRT requirements applied and frequency response enabled
| Parameter | Value | Parameter Name | Notes
M | PfFlag | 1 | Power factor flag (1: constant power factor, 0: constant Q control) | NERC default
M+1 | FrqFlag | 1 | Frequency flag (1: enabled, 0: disabled) | Frequency response is still expected.
M+2 | PQFlag | 1 | Active or reactive current priority (1: priority for current limit, 0: Q priority) | NERC default - 2003
M+3 | GenFlag | 0 | Gen flag (1: unit is a generator, 0: unit is a storage device) | The online SODGs are solar and wind (SODG storage will be offline)
M+4 | VtripFlag | 1 | Voltage trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
M+5 | FtripFlag | 1 | Frequency trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
J | Trv | 0.02 | voltage measurement transducer time constant | NERC default
J+1 | Trf | 0.02 | frequency measurement transducer time constant | Left out of NERC parameterization guideline table, but is in other documentation
J+2 | dbd1 | -99 | lower voltage deadband | NERC default
J+3 | dbd2 | 99 | upper voltage deadband | NERC default
J+4 | Kqv | 0 | proportional voltage control gain | NERC default
J+5 | Vref0 | 0 | user specified voltage set-point | NERC default
J+6 | Tp | 0.02 | power measurementtransducer time constant | NERC default
J+7 | Tiq | 0.02 | Q-control time constant | NERC default
J+8 | Ddn | 20 | Downard Frequency Responsiveness for Overfrequency Conditions | Frequency response is still expected.. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+9 | Dup | 20 | Upward Frequency Responsiveness for Underfrequency Conditions | Frequency response is still expected.. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+10 | fdb1 | -0.000283 | Frequency Deadband | Frequency response is still expected.
J+11 | fdb2 | 0.000283 | Frequency Deadband | Frequency response is still expected.
J+12 | femax | 0.1 | Frequency Error Limits | Frequency response is still expected.. Used when Frequency flag is enabled
J+13 | femin | -0.1 | Frequency Error Limits | Frequency response is still expected.. Used when Frequency flag is enabled
J+14 | Pmax | 1 | Maximum power limit (pu) | NERC default
J+15 | Pmin | -1 | Minimum power limit (pu) | DESR
J+16 | dPmax | 99 | Power reference max ramp rate (> 0) | NERC default
J+17 | dPmin | -99 | Power reference min ramp rate (< 0) | NERC default
J+18 | tpord | 1 | Power-order time constant, small lag time associated with frequency flag | Model tuning edit
J+19 | Kpg | 0.1 | PI controller proportional gain
J+20 | Kig | 10 | PI controller integral gain
J+21 | lmax | 1.2 | Maximum converter current (pu) | NERC default
J+22 | vl0 | 0.49 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44. When voltage falls below vl1, a fraction of the DERs will cutout, with a linearly increasing amount of DERs experiencing cutouts down to vl0 where all DERs will have cut out. vl0 can be set to the highest undervoltage point in which momentary cessation starts occurring. In cases where momentary cessation of inverter-based resources needs to be represented, use vl1 and vl0 with extended trip times. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+23 | vl1 | 0.49 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44
J+24 | vh0 | 1.15 | inverter voltage break-point for high voltage cut-out | NERC default is 1.2. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+25 | vh1 | 1.15 | inverter voltage break-point for high voltage cut-out | NERC default is 1.15
J+26 | tvl0 | 0.16 | low voltage cut-out timer for vl0 | NERC default is 0.16.
J+27 | tvl1 | 0.16 | low voltage cut-out timer for vl1 | NERC default is 0.16.
J+28 | tvh0 | 0.16 | low voltage cut-out timer for vh0 | NERC default is 0.16
J+29 | tvh1 | 0.16 | low voltage cut-out timer for vh1 | NERC default is 0.16
J+30 | Vrfrac | 0 | Fraction of Resources Recovering | NERC default is Vrfrac = 1 for 2018 (all recover), Vrfrac = 0 for 2003 (none recover)
J+31 | fltrp (fl) | 57 | inverter frequency break-point for low frequency cut-out | NERC default - 2003
J+32 | fhtrp (fh) | 61.8 | inverter frequency break-point for high frequency cut-out | NERC default - 2003
J+33 | tfl | 0.16 | low frequency cut-out timer for fl | NERC default
J+34 | tfh | 0.16 | high frequency cut-out timer for fh | NERC default
J+35 | tg | 0.02 | current control time constant (> 0) | NERC default
J+36 | rrpwr | 0.1 | Active Current Recovery Ramp Rate | NERC default - 2003
J+37 | Tv | 0.02 | Time constant on the output of the multiplier | NERC default
J+38 | vfth (Vpr) | 0.8 | Low voltage frequency tripping | NERC default - 2003
J+39 | Iqhl | 0 | Reactive current injection limits | NERC default - 2003
J+40 | Iqll | 0 | Reactive current injection limits | NERC default - 2003

## DESR VRT XMT - Discharge 80%
DESRs with voltage ride-through exemption
IEEE 1547-2003 base with edits made to follow frequency ride-through requirements and frequency response

## DESR VRT XMT - 0% dispatch
DESRs with voltage ride-through exemption
IEEE 1547-2003 base with edits made to follow frequency ride-through requirements and frequency response
Notes:
When modeling with Pgen = 0 MW, there were odd VAR responses for LVRT and Frequency tests
This could be a PSSE implementation issue that would need a work around for our flatstart
The following results are "zero" dispatch with Pgen = 0.01 MW (similar results for Pgen = -0.01 MW)

## DESR FRT and VRT exemption
| DESRs with VRT and FRT exemptions |  |  | Expect parameters in blue boxes to change between gen type (solar, wind, energy storage), ERCOT registration type, NOG ride-through exemptions
Base of 1547-2003 with frequency response enabled
| Parameter | Value | Parameter Name | Notes
M | PfFlag | 1 | Power factor flag (1: constant power factor, 0: constant Q control) | NERC default
M+1 | FrqFlag | 1 | Frequency flag (1: enabled, 0: disabled) | Frequency response is still expected.
M+2 | PQFlag | 1 | Active or reactive current priority (1: priority for current limit, 0: Q priority) | NERC default - 2003
M+3 | GenFlag | 0 | Gen flag (1: unit is a generator, 0: unit is a storage device) | The online SODGs are solar and wind (SODG storage will be offline)
M+4 | VtripFlag | 1 | Voltage trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
M+5 | FtripFlag | 1 | Frequency trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
J | Trv | 0.02 | voltage measurement transducer time constant | NERC default
J+1 | Trf | 0.02 | frequency measurement transducer time constant | Left out of NERC parameterization guideline table, but is in other documentation
J+2 | dbd1 | -99 | lower voltage deadband | NERC default
J+3 | dbd2 | 99 | upper voltage deadband | NERC default
J+4 | Kqv | 0 | proportional voltage control gain | NERC default
J+5 | Vref0 | 0 | user specified voltage set-point | NERC default
J+6 | Tp | 0.02 | power measurementtransducer time constant | NERC default
J+7 | Tiq | 0.02 | Q-control time constant | NERC default
J+8 | Ddn | 20 | Downard Frequency Responsiveness for Overfrequency Conditions | Frequency response is still expected.. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+9 | Dup | 20 | Upward Frequency Responsiveness for Underfrequency Conditions | Frequency response is still expected.. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+10 | fdb1 | -0.000283 | Frequency Deadband | Frequency response is still expected.
J+11 | fdb2 | 0.000283 | Frequency Deadband | Frequency response is still expected.
J+12 | femax | 0.1 | Frequency Error Limits | Frequency response is still expected.. Used when Frequency flag is enabled
J+13 | femin | -0.1 | Frequency Error Limits | Frequency response is still expected.. Used when Frequency flag is enabled
J+14 | Pmax | 1 | Maximum power limit (pu) | NERC default
J+15 | Pmin | 0 | Minimum power limit (pu) | DESR
J+16 | dPmax | 99 | Power reference max ramp rate (> 0) | NERC default
J+17 | dPmin | -99 | Power reference min ramp rate (< 0) | NERC default
J+18 | tpord | 1 | Power-order time constant, small lag time associated with frequency flag | Model tuning edit
J+19 | Kpg | 0.1 | PI controller proportional gain
J+20 | Kig | 10 | PI controller integral gain
J+21 | lmax | 1.2 | Maximum converter current (pu) | NERC default
J+22 | vl0 | 0.49 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44. When voltage falls below vl1, a fraction of the DERs will cutout, with a linearly increasing amount of DERs experiencing cutouts down to vl0 where all DERs will have cut out. vl0 can be set to the highest undervoltage point in which momentary cessation starts occurring. In cases where momentary cessation of inverter-based resources needs to be represented, use vl1 and vl0 with extended trip times. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+23 | vl1 | 0.49 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44
J+24 | vh0 | 1.15 | inverter voltage break-point for high voltage cut-out | NERC default is 1.2. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+25 | vh1 | 1.15 | inverter voltage break-point for high voltage cut-out | NERC default is 1.15
J+26 | tvl0 | 0.16 | low voltage cut-out timer for vl0 | NERC default is 0.16.
J+27 | tvl1 | 0.16 | low voltage cut-out timer for vl1 | NERC default is 0.16.
J+28 | tvh0 | 0.16 | low voltage cut-out timer for vh0 | NERC default is 0.16
J+29 | tvh1 | 0.16 | low voltage cut-out timer for vh1 | NERC default is 0.16
J+30 | Vrfrac | 0 | Fraction of Resources Recovering | NERC default is Vrfrac = 1 for 2018 (all recover), Vrfrac = 0 for 2003 (none recover)
J+31 | fltrp (fl) | 59.3 | inverter frequency break-point for low frequency cut-out | NERC default - 2003
J+32 | fhtrp (fh) | 60.5 | inverter frequency break-point for high frequency cut-out | NERC default - 2003
J+33 | tfl | 0.16 | low frequency cut-out timer for fl | NERC default
J+34 | tfh | 0.16 | high frequency cut-out timer for fh | NERC default
J+35 | tg | 0.02 | current control time constant (> 0) | NERC default
J+36 | rrpwr | 0.1 | Active Current Recovery Ramp Rate | NERC default - 2003
J+37 | Tv | 0.02 | Time constant on the output of the multiplier | NERC default
J+38 | vfth (Vpr) | 0.8 | Low voltage frequency tripping | NERC default - 2003
J+39 | Iqhl | 0 | Reactive current injection limits | NERC default - 2003
J+40 | Iqll | 0 | Reactive current injection limits | NERC default - 2003

## DESR FRT VRT XMT -Discharge 80%
DESRs with voltage AND frequency ride-through exemption
IEEE 1547-2003 base with edits made to allow frequency response

## DESR FRT VRT XMT - 0% dispatch
DESRs with voltage AND frequency ride-through exemption
IEEE 1547-2003 base with edits made to allow frequency response
Notes:
When modeling with Pgen = 0 MW, there were odd VAR responses for LVRT and Frequency tests
This could be a PSSE implementation issue that would need a work around for our flatstart
The following results are "zero" dispatch with Pgen = 0.01 MW (similar results for Pgen = -0.01 MW)

## SODG_IBR
| Inverter-based SODGs |  |  | Expect parameters in blue boxes to change between gen type (solar, wind, energy storage), ERCOT registration type, NOG ride-through exemptions
Base of 1547-2003
| Parameter | Value | Parameter Name | Notes
M | PfFlag | 1 | Power factor flag (1: constant power factor, 0: constant Q control) | NERC default
M+1 | FrqFlag | 0 | Frequency flag (1: enabled, 0: disabled) | NERC default - 2003
M+2 | PQFlag | 1 | Active or reactive current priority (1: priority for current limit, 0: Q priority) | NERC default - 2003
M+3 | GenFlag | 1 | Gen flag (1: unit is a generator, 0: unit is a storage device) | The online SODGs are solar and wind (SODG storage will be offline)
M+4 | VtripFlag | 1 | Voltage trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
M+5 | FtripFlag | 1 | Frequency trip flag (1: enable, 0: disable) | left out of NERC parameterization guideline table
J | Trv | 0.02 | voltage measurement transducer time constant | NERC default
J+1 | Trf | 0.02 | frequency measurement transducer time constant | Left out of NERC parameterization guideline table, but is in other documentation
J+2 | dbd1 | -99 | lower voltage deadband | NERC default
J+3 | dbd2 | 99 | upper voltage deadband | NERC default
J+4 | Kqv | 0 | proportional voltage control gain | NERC default
J+5 | Vref0 | 0 | user specified voltage set-point | NERC default
J+6 | Tp | 0.02 | power measurementtransducer time constant | NERC default
J+7 | Tiq | 0.02 | Q-control time constant | NERC default
J+8 | Ddn | 0 | Downard Frequency Responsiveness for Overfrequency Conditions | NERC default - 2003. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+9 | Dup | 0 | Upward Frequency Responsiveness for Underfrequency Conditions | NERC default - 2003. PSSE manual documentation has a potential error. Other documentation says ≥ 0
J+10 | fdb1 | -99 | Frequency Deadband | NERC default - 2003
J+11 | fdb2 | 99 | Frequency Deadband | NERC default - 2003
J+12 | femax | 0 | Frequency Error Limits | NERC default - 2003. Used when Frequency flag is enabled
J+13 | femin | 0 | Frequency Error Limits | NERC default - 2003. Used when Frequency flag is enabled
J+14 | Pmax | 1 | Maximum power limit (pu) | NERC default
J+15 | Pmin | 0 | Minimum power limit (pu) | NERC default
J+16 | dPmax | 99 | Power reference max ramp rate (> 0) | NERC default
J+17 | dPmin | -99 | Power reference min ramp rate (< 0) | NERC default
J+18 | tpord | 0.02 | Power-order time constant, small lag time associated with frequency flag | NERC default - 2003
J+19 | Kpg | 0 | PI controller proportional gain | NERC default - 2003
J+20 | Kig | 0 | PI controller integral gain | NERC default - 2003
J+21 | lmax | 1.2 | Maximum converter current (pu) | NERC default
J+22 | vl0 | 0.49 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44. When voltage falls below vl1, a fraction of the DERs will cutout, with a linearly increasing amount of DERs experiencing cutouts down to vl0 where all DERs will have cut out. vl0 can be set to the highest undervoltage point in which momentary cessation starts occurring. In cases where momentary cessation of inverter-based resources needs to be represented, use vl1 and vl0 with extended trip times. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+23 | vl1 | 0.49 | inverter voltage break-point for low voltage cut-out | NERC default is 0.44
J+24 | vh0 | 1.15 | inverter voltage break-point for high voltage cut-out | NERC default is 1.2. We are currently going to model individually instead of aggregated, so this is unnecessary to utilize.
J+25 | vh1 | 1.15 | inverter voltage break-point for high voltage cut-out | NERC default is 1.15
J+26 | tvl0 | 0.16 | low voltage cut-out timer for vl0 | NERC default is 0.16.
J+27 | tvl1 | 0.16 | low voltage cut-out timer for vl1 | NERC default is 0.16.
J+28 | tvh0 | 0.16 | low voltage cut-out timer for vh0 | NERC default is 0.16
J+29 | tvh1 | 0.16 | low voltage cut-out timer for vh1 | NERC default is 0.16
J+30 | Vrfrac | 0 | Fraction of Resources Recovering | NERC default is Vrfrac = 1 for 2018 (all recover), Vrfrac = 0 for 2003 (none recover)
J+31 | fltrp (fl) | 59.3 | inverter frequency break-point for low frequency cut-out | NERC default - 2003
J+32 | fhtrp (fh) | 60.5 | inverter frequency break-point for high frequency cut-out | NERC default - 2003
J+33 | tfl | 0.16 | low frequency cut-out timer for fl | NERC default
J+34 | tfh | 0.16 | high frequency cut-out timer for fh | NERC default
J+35 | tg | 0.02 | current control time constant (> 0) | NERC default
J+36 | rrpwr | 0.1 | Active Current Recovery Ramp Rate | NERC default - 2003
J+37 | Tv | 0.02 | Time constant on the output of the multiplier | NERC default
J+38 | vfth (Vpr) | 0.8 | Low voltage frequency tripping | NERC default - 2003
J+39 | Iqhl | 0 | Reactive current injection limits | NERC default - 2003
J+40 | Iqll | 0 | Reactive current injection limits | NERC default - 2003

## SODG model test
SODG (IBR)
IEEE 1547-2003base used

## UDG
Unregistered Distributed Generation (UDG) dynamics will not be explicitly represented in DWG base cases. DWG will not modify UDG representation from the SSWG case - UDG will be embedded or reflected in the load according to current TSP conventions.