## Slide 1
Public Utility Commission of Texas (PUCT) Oversight Project No. 46304 Relating to DC Tie Project Proposed by Southern Cross Transmission, LLC
Directive #9 : Ancillary Services
July TAC, 2021
ERCOT Staff

## Slide 2: Background of Project and PUCT Directives
Southern Cross Transmission LLC/Pattern Power Marketing LLC received FERC approval (FERC Docket No. TX 11-1-001) to interconnect DC Tie line.
PUCT imposed conditions for interconnection of the SCT DC Tie line in two PUCT proceedings:
  City of Garland docket – Docket No. 45624
  Oversight proceeding arising out of City of Garland docket – Project No. 46304
As part of the oversight proceeding, PUCT issued 14 Directives to ERCOT, requiring certain studies and determinations be made to accommodate the SCT DC Tie.

## Slide 3: Summary of Directive 9 Related to Ancillary Services
Directive 9 requires ERCOT to evaluate what modifications to existing and additional ancillary services, if any, are necessary for reliable interconnection of the Southern Cross DC Tie (SCT DC Tie).
Determination (summarized from the whitepaper):
  Procurement of additional new Ancillary Services is unnecessary because NPRR1034, Frequency-Based Limits on DC Tie Imports and Exports, gives ERCOT authority to establish limits on DC Tie transfers and to curtail DC Tie Schedules when necessary to address the risk of unacceptable frequency deviations.
  No adjustment to Responsive Reserve Service (RRS) or Non-Spinning Reserve Service is necessary if SCT DC Tie is implemented with the proposed design as a bi-pole DC Tie that is capable of operating in single-pole mode. This is based on NERC Reliability Standard BAL-003-2, which clarifies that the loss of a bi-pole DC Tie that is capable of operating in single-pole mode would count as two separate contingencies. While the loss of the Southern Cross DC Tie at its maximum import of 2,000 MW would exceed ERCOT’s single largest contingency of 1,430 MW, this reliability standard treats the Tie as 2 – 1000MW contingencies.
  No changes to Regulation Service are necessary because DC Tie ramp will be adequately addressed by SCR 800, Addition of DC Tie Ramp to GTBD Calculation, and NPRR 999, DC Tie Ramp Limitations.

## Slide 4: Summary of Directive 9 Related to Ancillary Services
Basis for Determination (summarized from the whitepaper):
  Between October 2018 and February 2019, ERCOT studied the potential Ancillary Service needs associate with the interconnection of the Southern Cross DC Tie. This study and its findings are based on protocols, standards, and limits in effect at that time. ERCOT’s determination reflects protocols, standards, and limits now in effect.
Ancillary Services for Significant Frequency Excursions
  When importing energy over the SCT DC Tie, studies initially determined that ERCOT would need to procure additional RRS to address the potential negative impact on frequency.
  Subsequently, NERC BAL-003-2 went into effect on December 1, 2020 and clarified that the loss of a bi-pole DC Tie that is capable of operating in single-pole mode would count as two separate contingencies.
  Because Southern Cross has informed ERCOT that the SCT DC Tie project will be built using this bi-pole configuration, BAL-003-2 will apply assuming this design is implemented
  As a result, the interconnection of SCT DC Tie is not expected to impact ERCOT’s RLPC or require additional RRS to address the risk of an import-side frequency deviation.
  When exporting energy over the SCT DC Tie, studies identified the risk of unacceptable frequency overshoot in the event of the loss of the SCT DC Tie when exporting above certain levels under certain low-inertia conditions.
  ERCOT determined that a new Ancillary Service (or a new form of RRS) would be necessary.
  ERCOT also determined that if the SCT DC Tie were subject to an export limit during those certain hours, then a new Ancillary Service (such as a new form of RRS) would not be necessary.
  Southern Cross submitted NPRR 1034, Frequency-Based Limits on DC Tie Imports and Exports, which addresses the risk to exporting from ERCOT and negates the need for procuring additional Ancillary Services.

## Slide 5: Summary of Directive 9
Basis for Determination (summarized from the whitepaper):
Non-Spinning Reserve Service
  Since the time of the study, ERCOT has modified its procurement practices to eliminate the Non-Spin procurement floor which was 1,375MW, equal to the MSSC, at the time of the study. Therefore, interconnection of the SCT DC Tie will not impact the Non-Spin quantities that are procured.
Regulation Service
  ERCOT has determined that tow changes to ERCOT rules and systems also make the procurement of additional Regulation Service due the interconnection of the SCT DC Tie unnecessary:
    SCR800, Addition of DC Tie Ramp to GTBD Calculation, which was approved in December 2019, will integrate scheduled DC Tie ramp into the Generation to be Dispatched (GTBD) value used by SCED
    NPRR 999, DC Tie Ramp Limitations, which was approved in October 2020, clarifies ERCOT’s authority to curtail DC Tie Schedules that would otherwise exceed the ramp capability of the system, and potentially impact system frequency

## Slide 6: Next Steps
Request that TAC endorse the Directive 9 whitepaper as presented and posted with the TAC materials.
Upon endorsement of the whitepaper, ERCOT will take it to the ERCOT Board for approval at its August 10, 2021 meeting.
ERCOT staff continues to work with stakeholders on remaining Directives
  http://www.ercot.com/mktrules/puctDirectives/southernCross