## Slide 1
ERCOT Frequency Control Report
July 2021
ERCOT
Operations Planning
PDCWG | August 11th, 2021

## Slide 2: Summary of July 2021
CPS1: 171.81%
Current CPS1 12-Month Rolling Average: 168.87%
0 BAAL Exceedance(s)
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2021 RMS1 Statistics
  Mean: 16.75 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 39,555,014 MWh
  Wind Energy: 5,369,386 MWh
  Percent Energy from Wind: 18.66%
  Solar Energy: 1,826,325 MWh
  Percent Energy from Solar: 4.62%
Minimum System Inertia
  Mean: 270,728 MW*s
  Max: 307,668 MW*s on Jul 27th
  Min: 229,166 MW*s on Jul 10th
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jul-21 CPS1 (%): 171.81
Notes: 1. 87.93% @ 07/16/2021 HE 20:00
Expected Generation Deviation
Expected gen dev remained negative for the most part of the hour. The largest expected gen dev was -1645MW @ 19:40 with significant contribution from solar
IRR Ramps
Solar generation ramped down by 2850 MW during this hour.
Regulation: Regulation up was exhausted for most part of the hour
Other
SCED was run manually multiple times and Manual offset of 250 MW @ 19:38
2. 70.02% @ 07/26/2021 HE 20:00
Expected Generation Deviation
Expected gen dev remained negative for the most part of the hour. The largest expected gen dev was -1690MW @ 19:43 with significant contribution from solar
IRR Ramps
Solar generation ramped down by 3300 MW during this hour.
Regulation: Regulation up was exhausted for most part of the hour
Other
SCED was run manually multiple times and Manual offset of 200 MW @ 19:39

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance(s) in July

## Slide 6: 15-Minute Average CPS1%
Jul-21 CPS1 (%): 171.81

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 169.16%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.75 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 39,555,014 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 5,369,386 MWh

## Slide 23: % Energy from Wind Generation
Notes: 13.57%

## Slide 24: Total Energy From Solar Generation
Notes: 1,826,325 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.62%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 229,116 MW*s on 7/10/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 270,728 MW*s
Max: 307,668 MW*s on Jul 27th
Min: 229,166 MW*s on Jul 10th

## Slide 28: Questions?
Thank you!