## Sheet1
Item Number | Originating Entity | Item Description | Timing | Owner | TAC Priority | Status | PUCT Project | ROS Leadership Notes | Memo from Magness | PDCWG Item (Y/N), Notes | PDCWG Priority
6 | ERCOT/ROS | Resource Telemetry: Ensure accurate exchange of Resource telemetry information related to Physical Responsive Capability (available operating reserves in real time) to enhance situational awareness during EEA events.* | Near-Term Stakeholder Items | ROS |  | Not Started |  | OWG and PDCWG? These items could start being reviewed. | Item 6 | Yes, This is important and critical data. | High
30 | ROS | Frequency Relay Points: Analyze load shed responsibilities related to frequencies for generation and load and ensure alignment | Near-Term Stakeholder Items | ROS |  | Not Started | Project No . 51888, Review of Critical Load Standards and Processes | SPWG and PDCWG? Starting reviewing soon; What protocol or operating guide revisions would be required? |  | Yes, Important. This ties in with PRC-024. David Penney suggest a coordinated meeting with SPWG. Impact of UFLS should be reviewed. A joint meeting of DWG and PDCWG is strongly suggested. Perhaps, discuss with generators in closed session and take low frequency issues to DWG. | High
44 | ROS | Ancillary Service Products: Review existing ancillary service products and determine if existing suite of products and amounts is adequate based on lessons learned from the February 2021 winter weather event. | Long-Term Stakeholder Items | ROS/WMS |  | Not Started |  | Need to understand how generators offering AS performed: PDCWG to review what happened; Joint meeting with WMWG to discuss market impacts; Review may take some time |  | Yes, understand AS deliverability by the generators during adverse conditions. Further analysis is needed in a closed session. Load shed needs to occur before PRC is exhausted. ERCOT will bring slides to a future discussion. A thorough review of AS services is needed. Perhaps meet jointly with OWG to better understand. From the morning of Feb 15, it is believed that RRS and Reg Up were exhausted about 90 minutes before the big frequency event. We don’t know if ERCOT had the authority to begin Load Shed at that point (when RRS & Reg Up were exhausted), but if they didn’t, that should be addressed. If/when our reserves are exhausted, we should begin to shed load in order to recover a reserve margin. | High
45 | ROS | Frequency: Analyze system frequency leading up to Energy Emergency Alert conditions and determine impact of low frequency on generation and load tripping. | Long-Term Stakeholder Items | ROS |  | Not Started |  | PDCWG; Ties into Item 30; Start reviewing in the near term |  | Yes. Question needs clarity, before and during EEA? Prior to EEA frequency was not an issue. Prior to EEA frequency was noisy, is this an indicator? PDCWG should analyze impact of swinging frequency on unit response. Closed session review is needed. | Medium
90 | WMS | Are the existing suite of Ancillary Service products and quantities adequate to ensure reliability or are changes needed? | Long-Term Stakeholder Items | WMS |  | Not Started |  |  |  | Any distinction between this and #44?
91 | WMS | Could fast frequency response play a bigger role? | Long-Term Stakeholder Items | ROS/WMS |  | Not Started |  | PDCWG to review; WMWG on WMS side to lead |  | Yes, further evaluation is needed. FFR deploys at 59.85, If there was more available frequency might not have reached the minimum value that it did. Most effective FFR design needs to be adjusted. FFR duration needs to be understood. | Medium/Low
100 | WMS | How did batteries providing FFR perform? Were FFR providers allowed to charge and if not, what penalties did they get charged? | Near-Term Stakeholder Items | WMS |  | Not Started |  |  |  | Yes, How can batteries be utilized effectively? | Medium/Low
10X | Lori Simpson (Constellation) | how batteries qualify for AS and the impact of their duration limits. | [5 empty] | Additional item to add? (Lori Simpson/Constellation) |  | I think we missed this one this one but it seems to fit with other battery discussion points.
10Y | Eric Easton (CNP) | Assessment of dynamic stability had the underfrequency relays asserted during the winter storm event. Given the amount of non-underfrequency load shed, the percentage of underfrequency load in-service had increased. If the increased percentage of underfrequency load had been shed would generation remain stable? | [5 empty] | Additional item to add? (Eric Easton/CNP) |  | I think we missed this one this one but it seems to fit with other battery discussion points.