## Public Submissions (MTE 2021)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Addition, Removal, or Correction | Reason for Addition, Removal, or Correction | Requestor | OCITF Consensus | Decision | Discussion Items
AEN | Ashton Woods Aen - Jollyville | LN | 138 | 20/12 | DCKT Austro-Daffin&Dunlap-Decker 138kV | Mcneil Aen - Howard Lane Aen 138 kV | Removal | This overload occured because the Onion Creek - Pilot Knob (CKT948) and the Onion Creek to Stoney Ridge (CKT1026) planned outages overlapped and increased the flow through CKT972 McNeil to Howard Lane. Closing the McNeil tie breaker CB950 resolves the thermal violation on CKT972. This tie breaker was permanently closed in March 2021. | AEN
AEN | Lytton Springs - Slaughter Lane | LN | 138 | 21/2 | DCKT Garfield (AEN)-Stoney Rose & Hicross (AEN) 138kV | Lytton Springs - Pilot Knob 138 kV | Removal | This overload occurred due to the overlapping outages of LCRA's Buda to Turnersville (T380), LCRA's Turnersville to Hicross (T143) with Lytton Springs - Slaughter Lane (CKT988) planned outage and in addition to the high loading due to February 2021 winter event. The overload would not have occurred if the outages had not overlapped and with the additional system conditions due to seveare weather conditions. | AEN
AEN | Onion Creek - Stoney Ridge | LN | 138 | 20/12 | DCKT Austro-Daffin&Dunlap-Decker 138kV | Mcneil Aen - Howard Lane Aen 138 kV | Removal | This overload occured because the Onion Creek - Pilot Knob (CKT948) and the Ashton Woods to Jollyville (CKT961) planned outages overlapped and increased the flow through CKT972 McNeil to Howard Lane. Closing the McNeil tie breaker CB950 resolves the thermal violation on CKT972. This tie breaker was permanently closed in March 2021. | AEN
AEP | Abilene Elmcreek - … - Abilene Mulberry Creek | LN | 138 | 21/2 | DCKT Central Bluff Sw-Brown Sw & Bluff Creek 345 kV | Abilene Mulberry Creek - Abilene Northwest 138 kV | Removal | Remove. Relay replacement will result in line rating increase of overloaded element | AEP
AEP | Abilene Mulberry Creek - Bluff Creek | LN | 138 | 21/2 | DCKT Central Bluff Sw-Brown Sw & Bluff Creek 345 kV | Abilene Mulberry Creek - Abilene Northwest 138 kV | Removal | Remove. Relay replacement will result in line rating increase of overloaded element | AEP
AEP | Aransas Pass Auto 138_69A1 138/69 | XF | 138 | 21/3 | Melon Creek-Rincon line 1 138 kV | Bonnieview - Rincon 69 kV | Removal | Remove. Bonnieview to Rincon was re-built with increased rating. | AEP
AEP | Aspermont Aep - Paint Creek | LN | 138 | 16/4 | Scurry Sw to Sun Sw 138 kV | Paint Creek Auto 69-2 138/69 kV | Removal | Remove. Paint Creek auto has been replaced. | AEP
AEP | Big Three - Victoria Dupont Switch | LN | 138 | 20/12 | Melon Creek-Rincon line 1 138 kV | Bonnieview - Rincon 69 kV | Removal | Remove. Bonnieview to Rincon was re-built with increased rating. | AEP
AEP | Closner - … - Pharr Magic Valley | LN | 138 | 20/8 | DCKT North Edinburg-West Ednburg 138 kV | Hidalgo Energy Center - Azteca Sub 138 kV | Removal | Remove. Stewart Road 345 kV was completed | AEP
AEP | Coleto Creek - Victoria | LN | 138 | 20/12 | Melon Creek-Rincon line 1 138 kV | Bonnieview - Rincon 69 kV | Removal | Remove. Bonnieview to Rincon was re-built with increased rating. | AEP
AEP | Joslin - North Carbide | LN | 138 | 21/1 | Melon Creek-Rincon line 1 138 kV | Bonnieview - Rincon 69 kV | Removal | Remove. Bonnieview to Rincon was re-built with increased rating. | AEP
AEP | Mvec (Rangerville) - Wesmer | LN | 138 | 21/3 | DCKT North Edinburg-Lon Hill & North Edinburg -…-El Trueno WInd 345 kV, DCKT South Santa Rosa-Rio Hondo 138 kV | Haine Drive - La Palma 138 kV | Removal | Remove. Stewart Road 345 kV completed | AEP
AEP | North Edinburg - … - North Pharr | LN | 138 | 20/8, 20/7 | DCKT North Edinburg-West Ednburg 138 kV, West Ednburg Sub-Alton Sub 138 kV | Hidalgo Energy Center - Azteca Sub 138 kV | Removal | Remove. Stewart Road 345 kV completed | AEP
AEP | North Edinburg - North McAllen | LN | 138 | 20/8, 20/7 | DCKT North Edinburg-West Ednburg 138 kV | Hidalgo Energy Center - Shell, Hidalgo Energy Center - Shell | Removal | Remove. Stewart Road 345 kV completed | AEP
AEP | North Pharr - Pharr Magic Valley | LN | 138 | 20/8, 20/7 | West Ednburg Sub-Alton Sub 138 kV, West Ednburg Sub-Alton Sub 138 kV | Weslaco Switch - North Alamo 138 kV | Removal | Remove. Stewart Road 345 kV completed | AEP
CNP | Greens Bayou Auto AT2 | XF | 345 | 16/2 | DCKT Greens Bayou to King 345 kV | Greens Bayou Auto AT1 345/138 kV | Removal | NEW AUTO - Addition of DPW AT1 in January 2021 should alleviate this issue. | CNP
CNP | Bailley - Hillje | LN | 345 | 21/3 | DCKT Jones Creek-South Texas Project & Refuge 345 kV | South Texas Project - Wa Parish 345 kV | Removal | NEW LINES - As of 12/31/21, the new Baily to Jones Creek double circuit 345kV lines should mitigate this issue. | CNP
CNP | Blessing - South Texas Project | LN | 345 | 18/12 | DCKT Wa Parish - Bailey & Hillje 345 kV | Jones Creek - South Texas Project 345 kV | Removal | NEW LINES - As of 12/31/21, the new Baily to Jones Creek double circuit 345kV lines should mitigate this issue. | CNP
CNP | Dow Chemical - Oasis (DOWOAS27) | LN | 345 | 21/4 | DCKT Jones Creek-South Texas Project & Refuge 345 kV | Oasis - Dow Chemical 345 kV | Removal | NEW LINES - As of 12/31/21, the new Baily to Jones Creek double circuit 345kV lines should mitigate this issue. | CNP
CNP | Hillje - Wa Parish (HLJWAP64) | LN | 345 | 21/4, 21/3, 16/3, 21/3, 21/4 | DCKT Jones Creek-South Texas Project & Refuge 345 kV, DCKT Jones Creek-South Texas Project & Refuge 345 kV, DCKT South Texas Project to Jones Creek & Refuge 345 kV | South Texas Project - Zapata, South Texas Project - Zapata, South Texas Project - Wa Parish 345 kV | Removal | NEW LINES - As of 12/31/21, the new Baily to Jones Creek double circuit 345kV lines should mitigate this issue. | CNP
CNP | Rufuge - South Texas Project | LN | 345 | 19/9, 19/10 | DCKT WA Parish to Bailey & Hillje 345 kV | Jones Creek - South Texas Project 345 kV | Removal | NEW LINES - As of 12/31/21, the new Baily to Jones Creek double circuit 345kV lines should mitigate this issue. | CNP
CNP | Coretz - Jones Creek | LN | 138 | 21/3 | Dow Chemical-Jones Creek (Ln 27) 345 kV | Jones Creek - Velasco 138 kV | Removal | NEW LINES - New Ckt 36 reconfiguration completed in April 2021 should alleviate this issue. | CNP
CNP | Jones Creek - … - Surfsi | LN | 138 | 21/3 | Dow Chemical-Jones Creek (Ln 27) 345 kV | Jones Creek - Velasco 138 kV | Removal | NEW LINES - New Ckt 36 reconfiguration completed in April 2021 should alleviate this issue. | CNP
CNP | Chambers - King | LN | 345 | 21/4 | Center-PH Robinson 138 kV | Texas - Cedar Bayou 138 kV | Removal | NEW LINES - The Texas - Cedar Bayou 138 kV line has been upgraded as of 4/15/21. Additionally as of 12/31/21, the Chambers - King line should be looped into Jordan substation. | CNP
CNP | Dow Chemical - Jones Creek (DOWJCK18) | LN | 345 | 21/3 | Dow Chemical-Jones Creek (Ln 27) 345 kV | Jones Creek - Velasco 138 kV | Removal | UPGRADE OVERLOADED ELEMENT - As of 12/31/21, upgrades to Dow Chemical-Jones Creek (Ln 18) 345 kV should mitigate this issue. New Ckt 36 reconfiguration completed in April 2021 should also alleviate this issue. | CNP
CNP | Dow Chemical - Jones Creek (DOWJCK27) | LN | 345 | 21/2 | DCKT Wa Parish-Jeanetta 345 kV | Dow Chemical - Jones Creek 345 kV | Removal | UPGRADE OVERLOADED ELEMENT - As of 12/31/21, upgrades to Dow Chemical-Jones Creek (Ln 27) 345 kV should mitigate this issue. | CNP
CNP | Fort Bend - Reading | LN | 138 | 20/10 | Wa Parish Gen WAP_G5 138 kV | Britmoore - Hayes 138 kV | Removal | UPGRADE OVERLOADED ELEMENT - The Britmoore - Hayes 138 kV line has been upgraded as of 5/28/21. | CNP
AEP, CNP | South Texas Project - Whitepoint | LN | 345 | 17/9, 17/11, 17/12, 18/1, 18/3 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV, Dyann to Wharton 138 kV, Danevang Switching Station to Blessing 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Blessing Auto 69A1 138/69 kV, El_Campo - Lane City Pump 138 kV | Removal | MTE element should be "South Texas Project - Angstrom" | CNP
CPS | Elmcreek - Skyline (E5_P4_1) | LN | 345 | 21/1 | DCKT Hill Country-Marion 345 kV | Cibolo - Schertz 138 kV | Removal | Should be removed, unless there are external limitations, CPS cannot duplicate this overload | CPS
CPS | Elmcreek - Skyline (E5_P4_2) | LN | 345 | 21/1 | DCKT Hill Country-Marion 345 kV | Cibolo - Schertz 138 kV | Removal | Should be removed, unless there are external limitations, CPS cannot duplicate this overload | CPS
AEP | Barney Davis - Naval Base | LN | 138 | 20/5 | Gila-…-Whitpoint 138 kV | Nueces Bay - Whitepoint 138 kV | Removal | This MTE should be removed because there were other impactul outages: T564 Big Hill-Twin Buttes, T558 Big Hill-Oersted-Edison-Kendall, T559 Big Hill-Oersted-Edison-Kendall, T238 Bergheim-Fairoaks. | LCRA
LCRA | Bergheim - Hays Energy | LN | 345 | 21/2 | DCKT Cagnon-Kendall 345 kV & Txresch-Tally_Rd 138 kV | Helotes - Ranchtwn 138 kV | Removal | This MTE should be removed because there were other impactul outages: T564 Big Hill-Twin Buttes, T558 Big Hill-Oersted-Edison-Kendall, T559 Big Hill-Oersted-Edison-Kendall, T238 Bergheim-Fairoaks. | LCRA
LCRA | Buda - Turnersville | LN | 138 | 21/2 | McCarty Lane-Zorn Ln1 138 kV | Crosswinds - Turnersville 138 kV | Removal | This MTE should be removed because there were other impactul outages: CKT988 Lytton-Slaughter, T262 McCarty Lane-Redwood. | LCRA
LCRA | Burnet - ... - Naruna | LN | 138 | 21/2 | DCKT Brownwood Sw-Goldthwaite & Brownwood Sw -…- Brownwood 138 kV | Killeen Switch - Trimmier 138 kV | Removal | This MTE should be removed because there were other impactul outages: T311 Burnet-Bertram, T187 Ferguson-Sherwood Shores, T188 Ferguson-Wirtz. | LCRA
CPS, LCRA | Cagnon - Kendall | LN | 345 | 20/10 | DCKT Bergheim-Hays Energy 345kv & River Oaks-Henne 138 kV | Cranes Mill - Sattler 138 kV | Removal | This MTE should be removed because there was another impactful outage: T148 Comfort-Cico. | LCRA
LCRA | Cico - Comfort | LN | 138 | 21/2, 20/10 | DCKT Cagnon-Kendall 345 kV & Txresch-Tally_Rd 138 kV, DCKT Bergheim-Kendall 345kv & Welfare-Boerne 138 kV | Helotes - Ranchtwn, Mason Creek - Bandera | Removal | This MTE should be removed because there were other impactful outages: T187 Ferguson-Sherwood Shores, T188 Ferguson-Wirtz, T192 Ferguson-Gillespie, T448 Gillespie-Horseshoe Bay, T651 Fort Mason-Mason CTEC. | LCRA
LCRA | Cico - Pipe Creek | LN | 138 | 20/10 | DCKT Bergheim-Kendall 345kv & Welfare-Boerne 138 kV | Mason Creek - Bandera 138 kV | Removal | This MTE should be removed because there were other impactful outages: R5-Kendal Cagnon-Kendall and T148 Comfort-Cico. | LCRA
LCRA | Coronado - Fairland | LN | 138 | 21/2 | DCKT Brownwood Sw-Goldthwaite & Brownwood Sw -…- Brownwood 138 kV | Killeen Switch - Trimmier 138 kV | Removal | This MTE should be removed because there were other impactful outages: T187 Ferguson-Sherwood Shores, T188 Ferguson-Wirtz, T192 Ferguson-Gillespie, T448 Gillespie-Horseshoe Bay, T651 Fort Mason-Mason CTEC. | LCRA
LCRA | Fayette Plant 3 - Lytton Springs | LN | 345 | 21/2 | DCKT Lostpines (AEP) -Austrop &Dunlap 345 kV & Dunlap (AEP) - Austrop 345 kV | Sim Gideon - Winchester 138 kV | Removal | This MTE should be removed because there were other impactful outages: CKT_3121 Holman-Lytton & T170 Winchester-Warda. | LCRA
LCRA | Ferguson - Sherwood Shores | LN | 138 | 21/2 | DCKT Brownwood Sw-Goldthwaite & Brownwood Sw -…- Brownwood 138 kV | Killeen Switch - Trimmier 138 kV | Removal | This MTE should be removed because there were other impactful outages: T187 Ferguson-Sherwood Shores, T188 Ferguson-Wirtz, T192 Ferguson-Gillespie, T448 Gillespie-Horseshoe Bay, T651 Fort Mason-Mason CTEC. | LCRA
LCRA | Flatonia - Plum | LN | 138 | 21/2 ,20/12 | Schulenburg-…-Glidden 138 kV, DCKT Lockhart-Luling & Red Rock 138 kV | Margruder - Fort Stockon Switch, Deer Creek ATH 138 kV | Removal | This MTE should be removed because there were other impactful outages: T208 Plum-Riverside, T170 Winchester-Warda, T466 Buda-Centex, T380 Buda-Turnersville, Buda AT2, T356 Nixon-Smiley GOAB | LCRA
LCRA | Gabriel - Glasscock | LN | 138 | 21/2 | Roundrock-Spanish Oaks 138 kV | Blockhouse - Whitestone 138 kV | Removal | This MTE should be removed because there were other impactful outages: T457 Gabriel-Rivery and T311 Bertram-Burnet | LCRA
LCRA | Hi Cross - Turnersville | LN | 138 | 21/2 | DCKT Lytton Springs-Slaughter Lane & Turnersville 138 kV | Mccarty Lane - Zorn 138 kV | Removal | This MTE should be removed because there were other impactful outages: T389 Bergheim-Hays Energy, T148 Comfort-Cico, T201 McCarty Lane-Beback | LCRA
LCRA | Henne - River Oaks | LN | 138 | 20/10 | Hays Energy-Zorn 345 kV | Welfare - Kendall 138 kV | Removal | This MTE should be removed because there was another impactful outage: T148 Comfort-Cico | LCRA
LCRA | Lampasas - … - San Saba | LN | 138 | 17/5 | Comanche Sw (Oncor) to Mercers Gap Sw | Holder Auto FMR1 138/69 kV | Removal | This MTE should be removed because many area transmission additions were made and the constraint does not exist: T311 Burnet-Bertram, T427 Bertram-Andice, T616 Leander-Ridgmar, T641 Ridgmar-Spanish Oak, T642 Spanish Oak-Round Rock | LCRA
LCRA | Medina Lake - Pipe Creek | LN | 138 | 20/10 | DCKT Hays Energy-Zorn 345 kV | Mason Creek - Bandera 138 kV | Removal | This MTE should be removed because there were other impactful outages: R5-Kendal Cagnon-Kendall and T148 Comfort-Cico. | LCRA
LCRA | Moore Lcra DSC MOS_13021 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | Removal | This MTE should be removed because the switch 13021 at Moore has been upgraded to 2000 A | LCRA
LCRA | Pooley Road - Zorn | LN | 138 | 20/12 | DCKT Lockhart-Luling & Red Rock 138 kV | Deer Creek Auto ATH 138/69 kV | Removal | This MTE should be removed because there was another impactful outage: T356 Nixon-Smiley GOAB | LCRA
ONCOR | Hicks Switch - … - Roanoke Switch | LN | 345 | 20/1, 20/4 | DCKT Hicks Switch to Saginaw Switch 138 kV | Eagle Mountain SES - Morris Dido 138 kV, Eagle Mountain SES - Rosen Heights Tap 1 138 KV | Correction | Remove these two overload elements due to completion of upgrading Eagle Mountain SES - Morris Dido 138 kV and Eagle Mountain SES-Rosen Heights Tap 1 - ISD 05/2021 as part of TPIT# 6273 upgrade Saginaw Sw-Eagle Mountain 138 kV double ckt line. The congestion shifts to the next line segment (Rosen Heights Tap2-Deen Switch 138 kV) on Eagle Mountain-Morris Dido-Deen Switch line so add "Rosen Heights Tap2-Deen Switch 138 kV" as the new overload element. Change Contingency to "DCKT Hicks Switch to Deen Switch 138 kV" and Change Congestion Year/Month to "2021". | ONCOR
ONCOR | Hicks Switch - Roanoke Switch | LN | 345 | 20/1, 20/4 | DCKT Hicks Switch to Saginaw Switch 138 kV | Eagle Mountain SES - Morris Dido 138 kV, Eagle Mountain SES - Rosen Heights Tap 1 38 KV (6265_A) | Correction | Remove these two overload elements due to completion of upgrading Eagle Mountain SES - Morris Dido 138 kV and Eagle Mountain SES-Rosen Heights Tap 1 - ISD 05/2021 as part of TPIT# 6273 upgrade Saginaw Sw-Eagle Mountain 138 kV double ckt line. The congestion shifts to the next line segment (Rosen Heights Tap2-Deen Switch 138 kV) on Eagle Mountain-Morris Dido-Deen Switch line so add "Rosen Heights Tap2-Deen Switch 138 kV" as the new overload element. Change Contingency to "DCKT Hicks Switch to Deen Switch 138 kV" and Change Congestion Year/Month to "2021". | ONCOR
ONCOR | Cedar Hill Switch - Courtland | LN | 345 | 18/5, 18/9, 19/10 | DCKT Navarro - Watermill Switch 345 kV, DCKT Everman Switch to Venus Switch 345 kV | Britten Road - Venus Switch 345 kV, Cedar Hill Switch - Fish Crek Switch (3180) 138 kV | Correction | Change contingency from "DCKT Navarro - Watermill Switch 345 kV" to "DCKT Big Onion - Watermill Switch 345 kV& Elrod Switch - Watermill Switch 345 kV" due to tapping of Elron Switch and Big Onion stations on Navarro - Watermill Switch 345 kV lines | ONCOR
ONCOR | Liggett Switch - Venus Switch (528) | LN | 345 | 19/11 | Venus Switch Auto MR2 345/138 kV & Liggett Switch to Venus Switch 345 kV | Britton Road - Venus Switch 345 kV | Correction | Change contingency to "Liggett Switch to Venus Switch 345 kV" as VENSW Auto MR2 is no longer taken out for this line contingency due to addtition of new BKR 15655 at Venus Switch. | ONCOR
ONCOR | Liggett Switch - Venus Switch (529) | LN | 345 | 19/9 | DCKT Navarro to Watermill Switch 345 kV | Britton Road - Venus Switch 345 kV | Correction | Change contingency from "DCKT Navarro - Watermill Switch 345 kV" to "DCKT Big Onion - Watermill Switch 345 kV& Elrod Switch - Watermill Switch 345 kV" due to tapping of Elron Switch and Big Onion stations on Navarro - Watermill Switch 345 kV lines | ONCOR
ONCOR | Tri Corner - Watermill Switch (215) | LN | 345 | 19/9, 19/10, 20/2 | DCKT Navarro to Watermill Switch 345 kV, DCKT Centerville Road Switch to Parkdale Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Britton Road - Venus Switch 345 kV, Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV | Correction | Change contingency from "DCKT Navarro - Watermill Switch 345 kV" to "DCKT Big Onion - Watermill Switch 345 kV& Elrod Switch - Watermill Switch 345 kV" due to tapping of Elron Switch and Big Onion stations on Navarro - Watermill Switch 345 kV lines | ONCOR
ONCOR | Johnson Switch - Venus Switch | LN | 345 | 19/10, 19/11 | DCKT Everman Switch to Venus Switch 345 kV, DCKT Everman Switch to Comanche Peak SES & Decordova SES 345 KV, Concord Auto CRD1 345/138 kV | Cedar Hill Switch - Fish Creek Switch 138 kV (3180), Hemphill - Mistletoe Heights 138 kV, Concord Auto CRD1 345/138 kV | Correction | Change contingency from "DCKT Everman Switch to Comanche Peak SES & Decordova SES 345 KV" to "DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV" Concord Auto CRD1 345/138 kV is listed as Contingency as well as Overload. Please review. | ONCOR
ONCOR | Comanche Peak Ses - Comanche Switch | LN | 345 | 21/4, 18/11 | DCKT Brown Switch - Killen Switch 345 kV, DCKT Brown Switch - Killen Switch 345 kV | Comanche Tap - Comanche Switch 138 kV, Comanche Tap - Comanche Switch 138 kV | Correction | Overload element is listed twice, remove one entry. Change contingency to "DCKT Brown Switch to Buckhorn Switch & Killen Switch 345 kV DCKT Buckhorn Switch to Killen Switch & Brown Switch to Killen Switch" due to tapping of Buckhorn Switch | ONCOR
ONCOR | Mitchell Bend Switch - Rocky Creek | LN | 345 | 19/10, 19/11 | DCKT Comanche Peak SES to Johnson Switch & Everman Switch 345 kV, DCKT Everman Switch to Comanche Peak SES & Decordova SES 345 kV | Decordova SES - Mitchell Bend Switch 345 kV, Hemphill - Mistletoe Heights 138 kV | Correction | Change contingency from "DCKT Everman Switch to Comanche Peak SES & Decordova SES 345 KV" to "DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV" Change overload element from "Decordova SES - Mitchell Bend Switch 345 kV" to "Carmicheal Bend Switch - Mitchell Bend Switch 345 kV" | ONCOR
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | Correction | Change Contingency to "DCKT Elkton to Tri Corner & Tyler Grande to Tri Corner 345 kV" due to tapping of Elkton - Forney Switch at Tri Corner. | ONCOR
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | Correction | Change Contingency to "DCKT Elkton to Tri Corner & Tyler Grande to Tri Corner 345 kV" due to tapping of Elkton - Forney Switch at Tri Corner. | ONCOR
ONCOR | Elkton - … - Forney Switch | LN | 345 | 2017, 17/11, 18/11, 18/12 | Trinidad - Enterprise and - Stryker DCKT, DCKT Martin Lake Ses - Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV auto, Lufkin Switch - Nacogdoches South Tap 138 kV | Correction | Change MTE to "Elkton - Tri Corner" Change Contingency from "Trinidad - Enterprise and - Stryker DCKT" to "Trinidad Ses- Mt Enterprise & Stryker Creek Ses DCKT" Change Overload element from "Elkton 345/138 kV auto" to "Elkton 345/138 kV Auto MR3" | ONCOR
ONCOR | Centerville Road Switch - Forney Switch | LN | 345 | 2017 | Forney - Royse DCKT | Forney 345/138 auto | Correction | Change Contingency from "Forney - Royse DCKT" to "Forney Switch - Royse Switch 345 kV DCKT" Change Overload element from "Forney 345/138 auto" to "Forney Switch 345/138 kV Auto MR3" | ONCOR
ONCOR | Forney Switch - Royse Switch (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | Correction | Change Overload element to "Forney Switch 345/138 kV Auto MR3" | ONCOR
ONCOR | Forney Switch - Royse Switch (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | Correction | Change Overload element to "Forney Switch 345/138 kV Auto MR3" | ONCOR
ONCOR | Lufkin Switch - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | Correction | Change overload element from "Herty North Switch to Nacogdoches Se 138 kV" to "Redland Switch to Nacogdoches Se 138 kV" | ONCOR
ONCOR | Gresham Road Switch - Stryker Creek Ses | LN | 138 | 18/6 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Herty North Switch - Nacogdoches Se 138 kV | Correction | Change overload element from "Herty North Switch to Nacogdoches Se 138 kV" to "Redland Switch to Nacogdoches Se 138 kV" | ONCOR
ONCOR | Gresham Road Switch - … - Nacogdoches Se | LN | 138 | 17/12, 18/7, 18/8, 18/10, 18/12, 19/1 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV, DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Herty North Switch - Nacogdoches Se 138 kV, Lufkin Switch - Nacogdoches South Tap 138 kV | Correction | Change overload element from "Herty North Switch to Nacogdoches Se 138 kV" to "Redland Switch to Nacogdoches Se 138 kV" | ONCOR
AEP, ONCOR | Clear Crossing - … - Dermott Switch (DMTSW_KIRCHH1) | LN | 345 | 18/4, 18/5, 18/6, 18/7, 18/8, 18/9, 18/11, 18/12 | DCKT Dermott Sw to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | Correction | Change MTE to "Clear Crossing-…-Dermott Switch (CLEARC_KIRCHH1)" | ONCOR
AEP, ONCOR | Clear Crossing - … - Dermott Switch (DMTSW_KIRCHH2) | LN | 345 | 18/4, 18/5 | DCKT Dermott Switch to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | Correction | Change MTE to "Clear Crossing-…-Dermott Switch (CLEARC_KIRCHH2)" | ONCOR
ONCOR | Dermott Switch - Scurry County South Switch (34540) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figafo & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | Correction | Change station name in contingency from Figafo to Figaro. | ONCOR
ONCOR | Dermott Switch - Scurry County South Switch (34550) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figafo & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | Correction | Change station name in contingency from Figafo to Figaro. | ONCOR
ONCOR | Herty North Switch - Nacogdoches Se | LN | 138 | 18/12 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Lufkin Switch - Nacogdoches South Tap 138 kV | Correction | Change MTE from "Herty North Switch to Nacogdoches Se 138 kV" to "Redland Switch to Nacogdoches Se 138 kV" | ONCOR
ONCOR | Benbrook Swith - … - Everman Switch | LN | 345 | 20/10, 17/2, 17/3, 19/11 | DCKT Wedgewood Sw-…-Benbrook 138 kV, DCKT Everman Switch to Comanche Peak SES & Decordova SES 345 kV | Mistletoe heights - Hemphill, Hemphill - Mistletoe Heights 138 kV | Correction | Change contingency from "DCKT Everman Switch to Comanche Peak SES & Decordova SES 345 KV" to "DCKT Everman Switch to Comanche Peak SES & Carmichael Bend Switch 345 KV" Overload element is listed twice. Remove "Mistletoe heights - Hemphill" | ONCOR
ONCOR | China Grove Switch - Snyder | LN | 138 | 19/5 | DCKT Dermott Switch to Golden Switch & Bluff Creek Switch 138 kV | Morgan Creek SES - Sun Switch 138 kV | Correction | Change contingency to "DCKT Dermott Switch to Ennis Creek Switch & Bluff Creek Switch 138 kV" | ONCOR
ONCOR | Snyder - Sun Switch | LN | 138 | 21/4 | DCKT Dermott Sw-…- Bluff Creek Sw & Ennis Creek Sw 345 kV | Morgan Creek Ses - Sun Switch 138 kV | Correction | Change MTE to "Snyder-…-Sun Switch (6240)" due to tapping of Deep Creek Sub. Change contingency to "DCKT Dermott Sw-…- Bluff Creek Sw & Ennis Creek Sw 138 kV" | ONCOR
ONCOR, ETT | Bowman Switch - Riley (34560) | LN | 345 | 21/3 | DCKT Clear Crossing-Coulomb & Clear Crossing-Smoky Hill 345 kV | Fisher Road Switch - Riley 345 kV | Correction | Change MTE to 'Bowman-…-Riley' due to tapping of Byrd Road Switch Station | ONCOR
ONCOR | Trinidad Ses - Watermill Switch (515) | LN | 345 | 19/9, 19/10, 20/2 | DCKT Parkdale Switch to Centerville Road Switch 138 kV, DCKT Navarro to Watermill Switch 345 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Prairie Creek - Scyene Road 138 kV, Britton Road - Venus Switch 345 kV, Kleberg Tap - Seagoville 138 kV | Correction | Change contingency from "DCKT Navarro - Watermill Switch 345 kV" to "DCKT Big Onion - Watermill Switch 345 kV& Elrod Switch - Watermill Switch 345 kV" due to tapping of Elron Switch and Big Onion stations on Navarro - Watermill Switch 345 kV lines Change MTE from "Trinidad Ses - Watermill Switch (515)" to " Tri Corner - Watermill Switch (515)" | ONCOR
ONCOR | Midland County Northwest Switch - Midland East | LN | 138 | 20/10 | DCKT Falcon Seaboard-Morgan Creek SES & Midline East 345 kV | Tall City - Sharyland Utilities - Telephone Road - Sharyland Utilities 138 kV | Correction | Change MTE to "Midland County Northwest Switch - … - Midland East (6462)" | ONCOR
ONCOR | Lewisville Switch - Roanoke Switch | LN | 345 | 19/3, 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV | Ti Tnp - West Tnp 138 kV, Argyle - Highlands Tap 138 kV | Correction | Remove Ti Tnp - West Tnp 138 kV overload element as the MTE is reducing the flow on this line for the identified contingencies. Keep Argyle-Highlands Tap 138 kV overload element. | ONCOR
ONCOR | Brown Switch - Corn Trail Switch | LN | 345 | 20/10 | Comamche Sw (Oncor)-Comanche Peak 345 kV | Comanche Tap - Comanche Switch (oncor) 138 kV | Removal | Oncor's LODF analysis showed that this MTE is reducing the flow on the constraint. | Oncor (LODF Analysis)
ONCOR | Argyle - … - Pockrus Substation | LN | 138 | 20/12 | Carrollton Northwest-Lakepoint Tnp 138 kV | South Tnp - Carrollton Northwest 138 kV | Removal | Oncor's LODF analysis showed that this MTE is reducing the flow on the constraint. | Oncor (LODF Analysis)
ONCOR | Anna Switch - Krum West Switch | LN | 345 | 20/11, 20/10 | DCKT Central Bluff Sw-Brown Sw & Bluff Creek 345 kV | Ti Tnp - West Tnp 138 kV | Removal | Oncor's LODF analysis showed marginal impact on the constraint due to this MTE. This MTE does not appear to be linked to the contingency/constraint and can be removed. | Oncor (LODF Analysis)
ONCOR | China Grove Switch - … - Paint Creek | LN | 138 | 21/2 | Abilene Northwest - Abilene Mulberry Creek 138 kV | Anson - Radium 69 kV | Removal | The congestion experienced in February 2021 is due to multiple simultaneous outages in the area: * Paint Creek - Radium 138 kV (ONC00435484, AEP00302373 - 09/16/2020-03/05/2021) * Paint Creek - California Creek Tap 138 kV (AEP00302388 - 09/16/2020-03/05/2021) * Paint Creek 138/69 kV xfmr (AEP00302376 - 09/16/2020-03/05/2021) * Paint Creek - Haskell Tap #1 69 kV (AEP00290875 - 09/16/2020-03/01/2021) | Oncor (Multiple Outages)
ONCOR | Liggett Switch - Norwood Switch | LN | 345 | 21/4 | DCKT Trinidad SES-Richland Chambers 345 kV | Britton Road - Venus Switch 345 kV | Removal | The congestion experienced in April 2021 is due to multiple simultaneous outages in the area: * Navarro - Watermill Sw. 345 kV (36010_A) (ONC00450212 - 04/19/2021-04/21/2021) * Navarro - Watermill Sw. 345 kV (36020_A) (ONC00450208 - 04/19/2021-05/13/2021) * Comanche Peak - Comanche Sw 345 kV (ONC00449091 - 04/19/2021-04/23/2021) * Liggett Sw. - Norwood Sw. 345 kV (ONC00464986 - 04/19/2021-04/22/2021) * Krum West Sw. - Riley 345 kV (ONC00461308, ONC00461309 - 04/19/2021-04/22/2021) | Oncor (Multiple Outages)
LSTR, ONCOR | Navarro - Watermill Switch (36010) | LN | 345 | 21/4 | DCKT Trinidad SES-Richland Chambers 345 kV | Britton Road - Venus Switch 345 kV | Removal | The congestion experienced in April 2021 is due to multiple simultaneous outages in the area: * Navarro - Watermill Sw. 345 kV (36010_A) (ONC00450212 - 04/19/2021-04/21/2021) * Navarro - Watermill Sw. 345 kV (36020_A) (ONC00450208 - 04/19/2021-05/13/2021) * Comanche Peak - Comanche Sw 345 kV (ONC00449091 - 04/19/2021-04/23/2021) * Liggett Sw. - Norwood Sw. 345 kV (ONC00464986 - 04/19/2021-04/22/2021) * Krum West Sw. - Riley 345 kV (ONC00461308, ONC00461309 - 04/19/2021-04/22/2021) | Oncor (Multiple Outages)
LSTR, ONCOR | Navarro - Watermill Switch (36020) | LN | 345 | 21/4 | DCKT Trinidad SES-Richland Chambers 345 kV | Britton Road - Venus Switch 345 kV | Removal | The congestion experienced in April 2021 is due to multiple simultaneous outages in the area: * Navarro - Watermill Sw. 345 kV (36010_A) (ONC00450212 - 04/19/2021-04/21/2021) * Navarro - Watermill Sw. 345 kV (36020_A) (ONC00450208 - 04/19/2021-05/13/2021) * Comanche Peak - Comanche Sw 345 kV (ONC00449091 - 04/19/2021-04/23/2021) * Liggett Sw. - Norwood Sw. 345 kV (ONC00464986 - 04/19/2021-04/22/2021) * Krum West Sw. - Riley 345 kV (ONC00461308, ONC00461309 - 04/19/2021-04/22/2021) | Oncor (Multiple Outages)
ONCOR | Cedar Hill Switch - Cedar Hill Tu (932) | LN | 138 | 21/3 | Desoto Sw TRX MR1 345/138 kV | Lancaster - Watermill Switch 138 kV | Removal | The congestion experienced in March 2021 is due to multiple simultaneous outages in the area: * Cedar Hill Sw. - Eagle Ford 138 kV (932_B) (ONC00455356 - 02/27/2021-04/05/2021) * Venus Sw. Auto Transformer #3 & BKR 15660 345 kV (ONC00455313 , ONC00455316 - 03/08/2021-03/12/2021) * Watermill - Willmer 138 kV ( ONC00440436 - 02/27/2021-03/13/2021) | Oncor (Multiple Outages)
ONCOR | Everman Switch - Venus Switch (495) | LN | 345 | 21/4 | DCKT Cedar Hill Sw-…-Evernman Sw & Cedar Hill Sw-…-Venus Sw 345 kV | Park Row - Sherry Switch 138 kV | Removal | The congestion experienced in April of 2021 is due to multiple simultaneous outages in the area: * Everman Switch - Venus Switch (495_A)345 kV (ONC00433389 - 03/15/2021-05/10/2021) * Everman Switch - Venus Switch (61_A) 345 kV (ONC00433408 - 03/15/2021-05/10/2021) * Sherry Switch Auto1 (ONC00457020 - 04/27/2021-05/02/2021) *Handley SES - Randol Mill Tap West (6405_C) (ONC00465768 - 04/21/2021-05/14/2021) * Handley SES - Randol Mill Tap East (6400_C) (ONC00465781 - 04/21/2021-05/14/2021) | Oncor (Multiple Outages)
ONCOR | Everman Switch - Venus Switch (61) | LN | 345 | 21/4 | DCKT Cedar Hill Sw-…-Evernman Sw & Cedar Hill Sw-…-Venus Sw 345 kV | Park Row - Sherry Switch 138 kV | Removal | The congestion experienced in April of 2021 is due to multiple simultaneous outages in the area: * Everman Switch - Venus Switch (495_A)345 kV (ONC00433389 - 03/15/2021-05/10/2021) * Everman Switch - Venus Switch (61_A) 345 kV (ONC00433408 - 03/15/2021-05/10/2021) * Sherry Switch Auto1 (ONC00457020 - 04/27/2021-05/02/2021) *Handley SES - Randol Mill Tap West (6405_C) (ONC00465768 - 04/21/2021-05/14/2021) * Handley SES - Randol Mill Tap East (6400_C) (ONC00465781 - 04/21/2021-05/14/2021) | Oncor (Multiple Outages)
ONCOR | Sherry Switch - … - Webb Sub | LN | 345 | 21/4 | DCKT Cedar Hill Sw-…-Evernman Sw & Cedar Hill Sw-…-Venus Sw 345 kV | Park Row - Sherry Switch 138 kV | Removal | The congestion experienced in April of 2021 is due to multiple simultaneous outages in the area: * Everman Switch - Venus Switch (495_A)345 kV (ONC00433389 - 03/15/2021-05/10/2021) * Everman Switch - Venus Switch (61_A) 345 kV (ONC00433408 - 03/15/2021-05/10/2021) * Sherry Switch Auto1 (ONC00457020 - 04/27/2021-05/02/2021) *Handley SES - Randol Mill Tap West (6405_C) (ONC00465768 - 04/21/2021-05/14/2021) * Handley SES - Randol Mill Tap East (6400_C) (ONC00465781 - 04/21/2021-05/14/2021) | Oncor (Multiple Outages)
ONCOR | Calmont Switch - … - North Main Switch | LN | 138 | 21/4 | Deen Sw-Fossil Creek-…-Hicks Sw 138 kV | Wagley Robertson - Hicks Switch 138 kV | Removal | The congestion experienced in April of 2021 is due to multiple simultaneous outages in the area: * Morris Dido - Rosen Heights Tap2 138 kV (ONC00452736 - 03/13/2021-04/15/2021) * Eagle Mountain - Rosen Heights Tap1 138 kV (ONC00458058 - 04/01/2021-05/11/2021) * Park Vista POI - Keller Tap 138 kV (ONC00462257 - 04/06/2021-04/13/2021) * Park Vista POI - Latigo POI 138 kV (ONC00462260 - 04/06/2021-04/13/2021) * Blackstone SWT 956 138 kV (ONC00464369, ONC00464556 - 04/08/2021-04/16/2021) * Lewisville Sw. - Roanoke Sw 345 kV (ONC00464509 - 04/09/2021) | Oncor (Multiple Outages)
ONCOR | Deen Switch - … - Eagle Mountatin | LN | 138 | 21/4 | Deen Sw-Fossil Creek-…-Hicks Sw 138 kV | Wagley Robertson - Hicks Switch 138 kV | Removal | The congestion experienced in April of 2021 is due to multiple simultaneous outages in the area: * Morris Dido - Rosen Heights Tap2 138 kV (ONC00452736 - 03/13/2021-04/15/2021) * Eagle Mountain - Rosen Heights Tap1 138 kV (ONC00458058 - 04/01/2021-05/11/2021) * Park Vista POI - Keller Tap 138 kV (ONC00462257 - 04/06/2021-04/13/2021) * Park Vista POI - Latigo POI 138 kV (ONC00462260 - 04/06/2021-04/13/2021) * Blackstone SWT 956 138 kV (ONC00464369, ONC00464556 - 04/08/2021-04/16/2021) * Lewisville Sw. - Roanoke Sw 345 kV (ONC00464509 - 04/09/2021) | Oncor (Multiple Outages)
ONCOR | Deen Switch - Eagle Mountain Ses & Rosen Heights | LN | 138 | 20/1 | DCKT Hicks Switch to Alliance & Roanoke Switch 345 kV | Blue Mound - Saginaw Switch 138 kV | Removal | Overloaded line termination changed from Saginaw Switch to Deen Switch due to completion of TPIT 6780 Deen Sw station (Rebuild existing Saginaw 138 kV Switching station) with ISD 01/2021. Blue Mound-Deen Switch 138 kV line has been rerated to higher rating in May 2021 as part of TPIT 6273 (Upgrade the Saginaw - Eagle Mountain 138 kV Double Circuit Line). With higher rating, congestion is not expected on this overload element. | Oncor (Transmission Project Complete)
ONCOR | Davis - … - Bowen Tate Tap - Handley Ses & - … - Everman Switch | LN | 138 | 19/9 | DCKT Hicks Switch to Saginaw Switch 138 kV | Eagle Mountain SES - Morris Dido 138 kV | Removal | Remove this MTE due to completion of upgrading Eagle Mountain SES - Morris Dido 138 kV - ISD 05/2021 as part of TPIT# 6273 upgrade Saginaw Sw-Eagle Mountain 138 kV double ckt line. | Oncor (Transmission Project Complete)
BPUB, ONCOR, SHARYLAND | Loma Alta - Stillman | LN | 138 | 2020 | DCKT North Edinburt - West Edinburg Sub & Palmhurst Sub 138kV | North Edinburg - North McAllen 138 kV | Removal | The N. Edinburgh to Palmito line has been tapped by Stewart, which provides another connection down to the 138 kV system on west side of the valley. Further, there will be additional lines connecting to Stillman in the near future. This change in topology should result in removing this MTE. | SHARYLAND
AEP, ONCOR, SHARYLAND | North Edinburg - Palmito | LN | 345 | 18/1 | Basecase | Valley GTC | Removal | The N. Edinburgh to Palmito line has been tapped by Stewart, which provides another connection down to the 138 kV system on west side of the valley. This change in topology should result in removing this MTE. Add "Sharyland" to the TDSP list for this MTE. | SHARYLAND
STEC | Bevo - ... - Coutulla Sub | LN | 69 | 21/2, 19/9 | Asherton to Bevo 138 kV | Hamilton Road - Maverick 138 kV | Removal | Bevo-Brundage being rebuilt Mid-2021 | STEC
STEC | Bevo - … - Turtle Creek Switching Station | LN | 69 | 19/8 | Asherton to Bevo 138 kV | Hamilton Road - Maverick 138 kV, Big Wells Sub - Brundage Sub 69 kV | Removal | Bevo-Brundage being rebuilt Mid-2021 | STEC
LCRA, STEC | Big Hill - Schneeman Draw | LN | 345 | 2018 | Basecase | McCamey GTC | Removal | RPG Project 2023 | STEC
CPS, STEC | Calaveras - Pawnee Switching Station | LN | 345 | 17/8, 19/2, 20/3 | DCKT Calaveras to Skyline 345 kV, DCKT Elmcreek - Skyline 345 kV, San Miguel Gen - Pawnee Switching Station 345 KV | Braunig - Cagnon 345 kV, Hill Country - Marion 345 kV, Pawnee Switching Station Auto XF1 345/138 kV, San Miguel Gen Auto ATB 345/138 kV | Removal | auto has internal fault and being replace | STEC
AEP, STEC | George West Switching Station - Orange Grove Switching Station | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | Removal | Both Smiguel Auto has been upgrade and should not see issue | STEC
AEP, STEC | Lon Hill - Orange Grove Switching Station | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | Removal | Both Smiguel Auto has been upgrade and should not see issue | STEC
STEC | Paloduro Sub - Pearsall Switching Station | LN | 138 | 21/2 | DCKT Dilley Sw (AEP)-San Miguel Sw & Dilley Sw (AEP)-Cotulla Sub 138 kV | Dilley Switch Aep - Cotulla Sub 69 kV | Removal | Both Smiguel Auto has been upgrade and should not see issue | STEC
TNMP | Ih 20 Tnp Auto Iht1 138/69 kV | XF | 138 | 18/3, 18/4 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV, Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | Removal | Should be removed. This element is out of service and retired from the model as part of 69kV to 138kV upgrades. | TNMP
TNMP | Wink Sub - Wink Tnp (6920_E) | LN | 69 | 21/4 | Yucca Drive Sw-Lotebush 138 kV | Wickett Tnp - Pyote Tnp 138 kV | Removal | Should be removed. This element is out of service and retired from the model as part of 69kV to 138kV upgrades. | TNMP
TNMP | Wink Sub - Wink Tnp (9025_A) | LN | 138 | 21/4 | Yucca Drive Sw-Lotebush 138 kV | Wickett Tnp - Pyote Tnp 138 kV | Removal | Completion of a new 138kV LN TNMP WINK- ONCOR WINKS (138_WNK_WKO). These lines are in parallel but separate contingencies and so would eliminate the need for this facility (9025_A) to remain on the MTE list. | TNMP