| RRGRR Number | 030 | RRGRR Title | Allow New Voltage Levels in Resource Registration Information |
| --- | --- | --- | --- |
| Date of Decision |  | August 5, 2021 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Resource Registration Glossary Sections Requiring Revision |  | Section 2 – Transformer Data (as applicable) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Resource Registration Glossary Revision Request (RRGRR) removes the hard coding of voltage levels for certain Resource Registration information related to Transformer Data. This will allow Resources connected to other voltage levels to submit their Resource Registration data without receiving validation errors. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This RRGRR will eliminate validation errors when Resource Registration data is submitted that uses a voltage level not in the list. |  |
| ROS Decision |  | On 7/8/21, ROS voted unanimously via roll call to recommend approval of RRGRR030 as submitted. All Market Segments participated in the vote. On 8/5/21, ROS voted unanimously via roll call to endorse and forward to TAC the 7/8/21 ROS Report and the Revised Impact Analysis for RRGRR030. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 7/8/21, ERCOT staff provided an overview of RRGRR030. On 8/5/21, there was no discussion. |  |

| Sponsor |  |
| --- | --- |
| Name | James Teixeira |
| E-mail Address | Jay.Teixeira@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6582 |
| Cell Number | 512-656-6734 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Phillip Bracy |
| E-Mail Address | Phillip.Bracy@ercot.com |
| Phone Number | 512-248-6917 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

Please note that the following RRGRR(s) also proposes revisions to the following section(s):

- RRGRR028, Transformer Impedance Clarifications

  - Section 2: Transformer Data (as applicable)

Proposed Guide Language Revision

| SECTION 2: RESOURCE REGISTRATION GLOSSARY - Effective March 1, 2021 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Resource Registration Data |  | Wind |  | Solar Photovoltaic (PV) | [RRGRR023: Insert column "Energy Storage Resource (ESR)" upon system implementation of NPRRs 1002, 1026, and 1029] |  | Conventional Generation (Gen) |  | Combined Cycle (CC) |  | Load Resources |  | Distributed Generation | Notes |  | Field Name |  | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) |  |  | Full Interconnect Study (FIS) - Steady-State, Short Circuit, and Facility (R, C, O, A) |  | FIS - Stability Study (R, C, O, A) |  | Planning Model (R, C, O, A) |  | Full Registration (R, C, O, A) |  |
| Transformer Data (as applicable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Description of Change |  | Select: description of change from drop down list: Add, Change or Delete |  |  |  |  |  |  |  |  |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | enter all caps | Transformer Name |  | Transformer name must be 14 characters or less and contain no special characters other than an underscore "_". |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | enter all caps | ERCOT Station Name (Station Code or Station Mnemonic) |  | ERCOT Station Code/Mnemonic where the transformer is located. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Automatic | Transformer Code |  | Concatenated code automatically provided |  |  |  |  |  |  |  | A |  | A |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | Transformer Test Report Attached? |  | Is the Transformer test report attached to this Resource Registration? Submit the Transformer Test Report via the approved Resource Registration process. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | Is This Transformer In a Master-follower Current Balancing Configuration? |  | Select Y or N whether this transformer is part of a master - following configuration |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | enter all caps | Master Name (can Be Same As this transformer) |  | The registered name of the transformer designated as the master in a parallel transformer control system scheme. |  |  |  |  |  |  |  |  |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | enter all caps | Follower Name (can Be Same As this transformer) |  | The registered name of the transformer designated as the follower in a parallel transformer control system scheme. |  |  |  |  |  |  |  |  |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | Generator Step up Transformer? |  | Select Y or N whether this transformer is a generator step up transformer |  |  |  | R |  | R |  | R |  | R |  |  |
| [RRGRR022 and RRGRR023: Replace applicable portions of "Transformer Data" above upon system implementation of NPRR973, or NPRRs 1002, 1026, and 1029:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | Main Power Transformer (MPT)? |  | Select Y or N whether this transformer is a Main Power Transformer (MPT) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  |  | Zero Sequence Data Winding Connect code (1-5) |  | Enter zero sequence data winding connect code 1 - 5 as noted below. Transformer Connection Codes: Two Winding Transformers (in order of Voltage highest first) 1 -- Wye-Wye Bank Both Neutrals Grounded 2 -- Wye - Delta Bank Grounded Wye 3 -- Delta - Wye Bank Grounded Wye 4 -- Delta - Delta Bank; Wye-Delta Bank Ungrounded Wye; Delta-Wye Bank Ungrounded Wye; Wye-Wye Bank Either Wye Grounded 5 -- Three Winding only (Test Reports needed for Code 5) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | p.u. | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer in P.u. (100 MVA Base) |  | Zero Sequence Grounding Resistance For An Impedance Grounded Generator in p.u. (100 MVA Base) and the nominal system voltage (eg. 69 kV, 138 kV, 345 kV) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | p.u. | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 MVA Base) |  | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 MVA Base) and the nominal system voltage (eg. 69 kV, 138 kV, 345 kV) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | p.u. | Zero Sequence Resistance In p.u. (100 MVA Base) |  | Zero Sequence Resistance In p.u. (100 MVA Base) and the nominal system voltage (eg. 69 kV, 138 kV, 345 kV) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | p.u. | Zero Sequence Reactance In P.u. (100 MVA Base) |  | Zero Sequence Reactance In P.u. (100 MVA Base) and the nominal system voltage (eg. 69 kV, 138 kV, 345 kV) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | p.u. | Positive Sequence Resistance (100 MVA Base) |  | Positive Sequence Resistance (100 MVA Base) and the nominal system voltage (eg. 69 kV, 138 kV, 345 kV) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | p.u. | Positive Sequence Reactance (100 MVA Base) |  | Positive Sequence Reactance (100 MVA Base) and the nominal system voltage (eg. 69 kV, 138kV, 345 kV) |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | MVA | Normal Rating |  | The continuous MVA rating of the transformer, including substation terminal equipment in series with the transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating indefinitely without damage, or violation of NESC clearances. |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | MVA | 2-hr Emergency Rating |  | The two-hour MVA rating of the transformer, including substation terminal equipment in series with the transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure. |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | MVA | 15-min Rating |  | The 15-minute MVA rating of the transformer, including substation terminal equipment in series with the transformer, at the applicable ambient temperature and with a step increase from a prior loading up to 90% of the Normal Rating. The transformer can operate at this rating for 15 minutes, assuming its pre-contingency loading up to 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure. This rating takes advantage of the time delay associated with heating of the transformer following a sudden increase in current. |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | MVA | Relay loadability limit |  | Enter the rating in MVA that would cause the circuit to trip within 15 minutes of exceeding that value. If no overload trip relay exists, enter "99999" |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | enter all caps | Unit(s) Associated With This Transformer (Must be entered as SITECODE_UNITNAME) |  | Enter the Unit(s) Associated With This Transformer (name must match unit names provided on the unit info tab) |  |  |  |  |  |  |  |  |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | High Side Voltage Level (no-Load) |  | Enter the voltage level of the high side for this transformer system nominal voltage (eg. 69 kV, 138 kV, 345 kV) |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | # | High Side PTI Bus Number |  | Enter the PTI bus number for the high side of this transformer |  |  |  |  |  |  |  | O |  | O |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | List | High Side Voltage Connection - Wye or Delta |  | Select whether this high side connection is a Wye or Delta connection |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Device 1 | High Side Voltage Connected Devices |  | Enter a device connected to the high side of this transformer |  |  |  |  |  |  |  |  |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | High Side Manufactured Nominal Voltage |  | Enter the high side manufactured nominal voltage for this transformer |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | Low Side Voltage level (no-Load) |  | Enter the voltage level of the low side for this transformer |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | # | Low Side PTI Bus Number |  | Enter the PTI bus number for the low side of this transformer |  |  |  |  |  |  |  | O |  | O |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Low Side Voltage Connection - Wye or Delta |  | Select whether this low side connection is a Wye or Delta connection |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Device 1 | Low Side Voltage Connected Devices |  | Enter a device connected to the low side of this transformer |  |  |  |  |  |  |  |  |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | Low Side Manufactured Nominal Voltage |  | Enter the low side manufactured nominal voltage for this transformer |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | On-Load Voltage Regulation |  | Select Y or N whether this transformer will change tap settings automatically while online to control voltage. |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | Does Transformer have an On-Load Tap Changer? |  | Select Y or N whether this transformer has an On-Load Tap changer |  |  |  | R |  | R |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Location of On-Load Tap Changer - Primary (High) or Secondary (Low) side |  | If this transformer has an On-Load Tap changer, select whether it is on Primary (High) or Secondary (Low) side. |  |  |  | C |  | C |  | C |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | Base kV of Regulated Side |  | Base kV of Regulated Side |  |  |  |  |  |  |  | C |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | Target kV of Regulated Side |  | Target kV of Regulated Side |  |  |  |  |  |  |  | C |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | % | Acceptable Deviation of Target Voltage |  | Acceptable Deviation from Target Voltage before tap change, in percent (enter 1% as 0.01). |  |  |  |  |  |  |  | C |  | C |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  |  | Comments |  | Enter any comments regarding this transformer data |  |  |  |  |  |  |  |  |  | O |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Ohms/Phase | DC Resistance of Winding 1 |  | Using manufacturer's data, enter the DC resistance of the Primary/high voltage winding (or for autotransformers, the series winding). |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Ohms/Phase | DC Resistance of Winding 2 |  | Using manufacturer's data, enter the DC resistance of the Secondary/low voltage winding (or for autotransformers, the common winding). For physical three-winding transformers modeled as three 2-winding transformers, enter "99999"for each transformer row. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | GIC Blocking device on Winding 1 |  | Answer Yes or No whether a Geomagnetic Induced Current blocking device exists on the Primary/high voltage winding (or for autotransformers, the series winding). |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | GIC Blocking device on Winding 2 |  | Answer Yes or No whether a Geomagnetic Induced Current blocking device exists on the Secondary/low voltage winding, (or for autotransformers, the common winding). For physical three-winding transformers modeled as three 2-winding transformers, select "N" for each transformer row. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Vector Group Identifier |  | Manufacturer-supplied alphanumeric identifier specifying vector group based on transformer winding connections and grounding. For physical three-winding transformers modeled as three 2-winding transformers, enter the same Vector Group Identifier for each transformer row. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Transformer Core Design Type |  | Manufacturer-supplied Transformer Core Design Type (Three Phase shell Form, Unknown, 3@Single Phase (separate cores), Three Phase 3-Legged Core Design, Three Phase 5-Legged Core Design, Three Phase 7-Legged Core Design). For physical three-winding transformers modeled as three 2-winding transformers, enter the same Transformer Core Design Type for each transformer row. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Number | K Factor |  | Value supplied by transformer manufacturer. If data is unavailable from the manufacturer, enter 0. For physical three-winding transformers modeled as three 2-winding transformers, enter the same K Factor for each transformer row. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Ohms | Winding 1 Grounding DC Resistance |  | Enter the Primary/high voltage winding Grounding DC Resistance in Ohms for any grounding device, (for a solidly grounded winding, enter 0, enter "99999" for ungrounded). |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | Ohms | Winding 2 Grounding DC Resistance |  | Enter the Secondary/low voltage winding Grounding DC Resistance in Ohms for any grounding device, (for a solidly grounded winding, enter 0, enter "99999" for ungrounded). For physical three-winding transformers modeled as three 2-winding transformers, enter "99999" for each transformer row. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Transformer Model |  | Enter 0 except for a phase-shifting transformer, which should be entered as a 1. For physical three-winding transformers modeled as three 2-winding transformers, enter the same model for each transformer row. |  |  |  |  |  |  |  | R |  | R |  |  |
| Transformer Data | X |  | X |  | X | X |  | X |  |  |  |  |  | mm/dd/yyyy | Effective Date: |  | Date this transformer was added, removed or updated in the model |  |  |  |  |  |  |  |  |  | R |  |  |