## Slide 1: Operations Working Group
Chair- Rickey Floyd
Vice-Chair- Shawn McCreary
HITE List Sub-Chair – Pushkar Chhajed
09/02/2021

## Slide 2: NOGRR215 – Limited Use of RAS
Tabled pending new comments from ERCOT

## Slide 3: NOGRR226 - Revision to 5% Transmission Operator (TO) Load Shedding Relay Set Point
LCRA presented data on the number of units that are set to trip after 9 minutes if frequency falls below 59.4.
ERCOT agreed to discuss internally on possible studies that may be needed to determine how to approach a solution
 | Conventional Resources |  | IBR’s |  | Total | 
Frequency (Hz) | Capacity (MW) | Unit Count | Capacity (MW) | Unit Count | Capacity (MW) | Unit Count
59.4 | 18198 | 76 | 5812 | 52 | 24010 | 128
59.3 | 398 | 2 | 35 | 2 | 433 | 4
59.2 | 0 | 0 | 372 | 3 | 372 | 3
59.1 | 400 | 1 | 0 | 0 | 400 | 1
59 | 102 | 1 | 1430 | 10 | 1532 | 11
58.8 | 0 | 0 | 16 | 2 | 16 | 2
58.5 | 608 | 2 | 1040 | 28 | 1648 | 30
58.4 | 150 | 2 | 0 | 0 | 150 | 2
Total | 19856 | 84 | 8705 | 97 | 28561 | 181
 | Conventional Resources | IBR’s | Total
Capacity | 15442 | 1560 | 17002
Unit Count | 54 | 12 | 66
Conventional Units during February Event set to trip after 9 minutes
Conventional Units set to trip after 9 minutes

## Slide 4: NPRR1077 Extension of Self-Limiting Facility Concept to Settlement Only Generators (SOGs) and Telemetry Requirements for SOGs.
PGRR092, Related to NPRR1077, Extension of Self-Limiting Facility Concept to Settlement Only Generators (SOGs) and Telemetry Requirements for SOGs.
RRGRR029, Related to NPRR1077, Extension of Self-Limiting Facility Concept to Settlement Only Generators (SOGs) and Telemetry Requirements for SOGs.
  OWG has consensus to support these three items

## Slide 5: NPRR1056, Market Impact Generic Transmission Constraint (GTC) Notification
Tabled pending new comments

## Slide 6: Emergency Condition list #5 NPRR1084
Improvements to Reporting of Resource Outages and Derates.
Concerns raised on having enough personnel to provide the updates in the timeline required in the comments filed
Tabled pending comments

## Slide 7: Emergency Condition list #6 NPRR1085
Ensuring Continuous Validity of Physical Responsive Capability (PRC) and Dispatch through Timely Changes to Resource Telemetry and Current Operating Plans (COPs)
Concerns raised on personnel being able to provide accurate information to ERCOT as required in the comments
Concerns were discussed about keeping COP updated and compliance risk if information was wrong
Recommendations were reiterated on adding an “ON-HOLD” option when a units is experiencing issues ford a long term solution and possibly locking the HSL or using “ONTEST” as a interim solution
Tabled pending comments

## Slide 8: Emergency Condition list # 122
Dynamic Load Shed Tables
ERCOT agreed to look for data on load diversity during the February event.
ERCOT commented that if a dynamic approach is used, it would require:
  Each TSP to provide real-time load telemetry to ERCOT
  Determine load share amounts for each TO
  Develop a method of notifying TSPs of their load share during an event

## Slide 9: Emergency Condition list # 49, 73
No update

## Slide 10: Emergency Condition list # 86
Operating GTCs during EEA
ERCOT provided an update from the workshop that included confirmation the GTCs could not be relaxed during an EEA event.
Discussed the possibility of constraining to the 15 minute rating if it is different than the 2 hour rating.
Possibly disable double circuit contingencies.

## Slide 11: Emergency Condition list #128
Using Instant Messaging during EEA Events
No objection from OWG
AEP to take the lead with other TSPs to create a SCR

## Slide 12: TAC Assignment: Remaining KTCs from Battery Energy Storage Task Force (BESTF)
KTC 15-3 Switchable Resources
KTC 15-4 Provisions Associated with Delayed Outages
  ERCOT provided a response to the following questions

## Slide 13: KTC 15-3 Switchable Resources
Question 1:
  Does ERCOT see any reliability issues with having a switchable ESR?
Answer
  In general, did not identify any major issues, if current rules for SWGR apply to ESRs
  One thing we will have to address is the current SWGR definition.
    Limited to Generation Resources,
    Will need to be modified to maybe Switchable Resource and include GR’s and ESRs
    Extend to coordination plans with SPP and MISO, in place 2019

## Slide 14: KTC 15-3 Switchable Resources
Question 2:
  How will ERCOT be informed of the State of Charge of the battery when it is operating in a Non-ERCOT control area?
Answer:
  ESRs should continue to telemeter and provide COP information that reflects state of charge even when interconnected to non-ERCOT area.
  This should provide Operator situational awareness needed to maintain reliability

## Slide 15: KTC 15-3 Switchable Resources
Question 3:
  Is there a limit on how many SWGRs and switchable ESRs that the ERCOT Control Room can handle?
Answer:
  We haven’t identified a hard limit
  ERCOT staffing levels will likely need to be increased if there’s a significant increase of Switchable Resources.
  As the number increases, this becomes a larger management and coordination process with SPP & MISO that pull operators away from their other responsibilities
  Currently have 5 sites with capability, manageable with current staff
  May want to consider initially limiting the total number of new switchable resources
  Would also need to discuss with SPP & MISO and adjust coordination plans as necessary

## Slide 16: KTC 15-4 Provisions Associated with Delayed Outages
Question 1:
  Does ERCOT staff have any concerns from a reliability or operational perspective?
Answer:
  Currently ERCOT does not have or didn’t initially identify any concerns with delaying Outages through the Outage Schedule Adjustment process
  Its ERCOT’s intent to omit ESR’s from the Outage Adjustment Evaluation since they are limited duration.

## Slide 17: Review HITE List Addition and Removals
OWG reached consensus and recommends approving the MTE list with the removals and changes
There were no additions to review
The MTE list has been provided to ROS