## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
September 02, 2021

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 08/11/2021
  Review of emergency conditions list from ROS
  ERCOT Ancillary Service Methodology (Part1, Introduction)
  ERCOT reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in July
  7/20/2021 08:46:05
    Loss of 801 MW generation
    Interconnection Frequency Response: 1313 MW/0.1 Hz
    6 of 52 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 52 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 471 MW/0.1 Hz
IMFR Performance currently
1119.24 MW/0.1HZ

## Slide 7
Questions?

## Slide 8: Frequency Control Report
July 2021

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy
Notes: 37,331,144 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes: 6,965,821 MWh

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 18.66%

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 1,643,972 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 4.40%