## Summary
Release Date: September 3, 2021
Final
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Fall 2021
SUMMARY
The ERCOT region is expected to have sufficient installed generating capacity to serve peak demands in the upcoming fall season, October – November 2021, under normal system conditions and several of the capacity reserve risk scenarios examined.
Based on expected fall peak weather conditions, the preliminary fall SARA anticipates a seasonal peak demand of 62,662 MW, which is unchanged from the preliminary SARA released on May 6th. This demand forecast has been adjusted downward by 120 MW to account for the load reduction impact of incremental forecasted rooftop solar capacity.
ERCOT is projecting a decrease in reserve capacity of 868 MW since the release of the preliminary fall SARA in May, based on data provided by resource owners and developers. The decrease is mostly due to an extended outage for a coal unit. Planned resource capacity totaling 5,277 MW is expected to be available to meet the fall peak demand. The planned projects are comprised of gas-fired units, wind and utility-scale solar. Another 644 MW of battery energy storage capacity is also expected to be available, although this capacity is currently assumed to provide Ancillary Services rather than sustained capacity for meeting system peak loads.
The report includes a thermal outage forecast of 14,774 MW based on historical outage data from the past three fall seasons (starting with 2018). Due to a change in categorizing a type of outage called an Unavoidable Extension, unplanned outages (previously called forced outages) increased while planned outages (previously called maintenance outages) decreased by a like amount. This change resulted in greater unplanned outage amounts for the high and extreme unplanned outage cases. The Background tab now includes more outage accounting information as well as details regarding the change in categorizing Unavoidable Extension outages.
Starting with this SARA report, ERCOT expanded the low wind output scenario adjustment to include low solar output as well. Similar to the preliminary fall SARA report, the final fall SARA includes a tab that provides a set of extreme scenarios. These extreme scenarios assume that multiple severe system conditions occur simultaneously, resulting in very low probability, high impact system outcomes.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2021 - Final
Release Date: September 3, 2021
Forecasted Capacity and Demand
Resources, MW
| Operational Resources (thermal and hydro) | 64654.9956 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Switchable Capacity Total | 3639 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
| Less Switchable Capacity Unavailable to ERCOT | -558 | Based on survey responses of Switchable Resource owners
| Available Mothballed Capacity | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
| Capacity from Private Use Networks | 2742.667 | Average grid injection during the top 20 fall peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocol Section 10.3.2.4.
| Coastal Wind, Peak Average Capacity Contribution | 1471.785 | Based on 35% of installed capacity for coastal wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Panhandle Wind, Peak Average Capacity Contribution | 1939.388 | Based on 44% of installed capacity for panhandle wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Other Wind, Peak Average Capacity Contribution | 6906.198 | Based on 37% of installed capacity for other wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Solar Utility-Scale, Peak Average Capacity Contribution | 3640.788 | Based on 68% of rated capacity for solar resources (fall season) per Nodal Protocols Section 3.2.6.2.2
| Storage, Peak Average Capacity Contribution | 0 | Based on 0% of rated capacity (fall season); resources assumed to provide Ancillary Services rather than sustained capacity available to meet peak loads
| RMR Capacity to be under Contract | 0 | Based on the capacity of Resources providing Reliability Must Run (RMR) Service during the fall season
| Capacity Pending Retirement | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
| Non-Synchronous Ties, Capacity Contribution | 719.8 | Based on import flows during most recent Energy Emergency Alert (EEA) intervals for the winter season (Used as a proxy for the fall season due to lack of EEA intervals.)
| Planned Thermal Resources with Signed IA, Air Permits and Adequate Water Supplies | 856.28 | Based on in-service dates provided by developers
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution | 256.34 | Based on in-service dates provided by developers and 35% fall capacity contribution for coastal wind resources
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution | 0 | Based on in-service dates provided by developers and 44% fall capacity contribution for panhandle wind resources
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution | 1713.1 | Based on in-service dates provided by developers and 37% fall capacity contribution for other wind resources
| Planned Solar Utility-Scale, Peak Average Capacity Contribution | 2450.992 | Based on in-service dates provided by developers and 68% fall capacity contribution for solar resources
| Planned Storage, Peak Average Capacity Contribution | 0 | Based on in-service dates provided by developers and 0% fall capacity contribution for storage resources
[a] Total Resources, MW |  | 90433.3336
Peak Demand, MW |  | 62782 | Based on average weather conditions at the time of the fall peak demand from 2005 – 2019, and updated based on a revised economic growth forecast prepared in April 2020
Rooftop PV Forecast, MW |  | 120 | Based on rooftop solar PV capacity during the peak load hour that is not already included in the peak load forecast
[b] Adjusted Peak Demand, MW |  | 62662
[c] Reserve Capacity [a - b], MW |  | 27771.3336
Reserve Capacity Risk Scenarios
|  | Expected Peak Load/ Expected Generation Outages/ Expected Renewable Output | Expected Peak Load/ High Generation Outages/ Expected Renewable Output | Expected Peak Load/ Expected Generation Outages/ Low Renewable Output | High Peak Load/ Expected Generation Outages/ Expected Renewable Output
| Scenario Adjustments |  |  |  |  | Description
| Seasonal High Peak Load Adjustment | 0 | 0 | 0 | 12737 | Based on the assumption that peak weather conditions from September 28, 2005, could occur in early October; the high fall forecast is 75,519 MW
| Typical Planned Outages, Thermal | 4103.2222 | 4103.2222 | 4103.2222 | 4103.2222 | Based on historical average of Planned outages for October through November weekdays, hours ending 3 pm - 8 pm, for the last three years (2018 - 2020). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. See the Background tab for more information on thermal outage accounting practices.
| Typical Unplanned Outages, Thermal | 10670.9066 | 10670.9066 | 10670.9066 | 10670.9066 | Based on historical average of Unplanned outages for October through November weekdays, hours ending 3 pm - 8 pm, for the last three years (2018 - 2020). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators.
| High Unplanned Outage Adjustment, Thermal | 0 | 4965.0434 | 0 | 0 | Based on the 95th percentile of historical Unplanned outages for October through November weekdays, for the last three years (2018 - 2020); the adjustment is the 95th percentile value, 15,636 MW, less the typical Unplanned outage amount of 10,671 MW. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators
| Low Renewable Output Adjustment | 0 | 0 | 13684.591 | 0 | Based on the 5th percentile of joint hourly wind and solar capacity factors (output as a percentage of installed capacity) associated with the 100 highest Net Load hours (Load minus wind output minus solar output) for the 2016-2020 fall Peak Load seasons; this low output level is 4,694 MW, and reflects a contribution of 3,033 MW from wind and 1,661 MW from solar.
[d] Total Uses of Reserve Capacity |  | 14774.1288 | 19739.1722 | 28458.7198 | 27511.1288
Capacity Available For Operating Reserves (n/a = not applicable for the risk scenario)
[e] Capacity Available for Operating Reserves, Normal Operating Conditions (c-d), MW |  | 12997.2048 | 8032.1614 | -687.3862 | 260.2048 | See the Background tab for additional details
Less than 2,300 MW indicates risk of EEA1
[f] EEA Resources deployed by ERCOT |  | n/a | n/a | 2212 | 2212 | Consists of the sum of expected Load Resources Available for Responsive Reserves for the fall season (1,292 MW, which reflects a 2% gross-up to account for avoided transmission losses), Emergency Response Service (820 MW, which reflects a 2% gross-up to account for avoided transmission losses), and TDSP Voltage Reduction (100 MW). Other resources that may be available include voluntary customer Demand Response, switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports.
[g] Capacity Available for Operating Reserves, Emergency Conditions (e+f), MW |  | n/a | n/a | 1524.6138 | 2472.2048 | See the Background tab for additional details
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Extreme Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2021 - Final
Release Date: September 3, 2021
Extreme Reserve Capacity Risk Scenarios (Combinations of high and/or extreme risk assumptions resulting in low probability, high impact outcomes)
|  | High Peak Load/ High Generation Outages/ Expected Renewable Output | High Peak Load/ High Generation Outages/ Low Renewable Output | High Peak Load/ Extreme Generation Outages/ Low Renewable Output
| Scenario Adjustments |  |  |  | Description
| Seasonal High Peak Load Adjustment based on 2005 Fall Weather | 12737 | 12737 | 12737 | Based on the assumption that peak weather conditions from September 28, 2005, could occur in early October; the high fall forecast is 75,519 MW
| Typical Planned Outages, Thermal | 4103.2222 | 4103.2222 | 4103.2222 | Based on historical average of Planned outages for October through November weekdays, hours ending 3 pm - 8 pm, for the last three years (2018 - 2020). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. See the Background tab for more information on thermal outage accounting practices.
| Typical Unplanned Outages, Thermal | 10670.9066 | 10670.9066 | 10670.9066 | Based on historical average of Unplanned outages for October through November weekdays, hours ending 3 pm - 8 pm, for the last three years (2018 - 2020). Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. See the Background tab for more information on thermal outage accounting practices.
| High Unplanned Outage Adjustment, Thermal | 4965.0434 | 4965.0434 | 4965.0434 | Based on the 95th percentile of historical Unplanned outages for October through November weekdays, for the last three years (2018 - 2020); the adjustment is the 95th percentile value, 15,636 MW, less the typical Unplanned outage amount of 10,671 MW. Outage history excludes units that are not expected to be available for the peak period of the upcoming seasons. These unavailable units are comprised of units that have retired, have announced upcoming retirements, are under extended outage, are mothballed, or are unavailable switchable generators. See the Background tab for more information on thermal outage accounting practices.
| Low Renewable Output Adjustment | 0 | 13684.591 | 13684.591 | Based on the 5th percentile of joint hourly wind and solar capacity factors (output as a percentage of installed capacity) associated with the 100 highest Net Load hours (Load minus wind output minus solar output) for the 2016-2020 fall Peak Load seasons; this low output level is 4,694 MW, and reflects a contribution of 3,033 MW from wind and 1,661 MW from solar.
| Extreme Unplanned Outage Adjustment, Thermal | 0 | 0 | 1460.0523 | Based on the highest hourly Unplanned Outage amount experienced during the fall seasons for 2011-2020 as a percentage of the aggregate fall capacity ratings for thermal resources. This percentage is 25.4%. The extreme Unplanned Outage amount is 17,096 MW, which is 25.4% times the net thermal capacity (the sum of capacities in rows 7 through 9 on the Scenarios tab minus Hydro resources). The adjustment is 17,096 MW less the sum of the typical plus high Unplanned Outage scenario amounts. See the Background tab for more information on thermal outage accounting practices.
[d] Total Uses of Reserve Capacity |  | 32476.1722 | 46160.7632 | 47620.8155
Capacity Available For Operating Reserves
[e] Capacity Available for Operating Reserves, Normal Operating Conditions (Scenarios tab c-d), MW |  | -4704.8386 | -18389.4296 | -19849.4819 | See the Background tab for additional details
Less than 2,300 MW indicates risk of EEA1
[f] EEA Resources deployed by ERCOT |  | 2212 | 2212 | 2212 | Consists of the sum of expected Load Resources Available for Responsive Reserves for the fall season (1,292 MW, which reflects a 2% gross-up to account for avoided transmission losses), Emergency Response Service (820 MW, which reflects a 2% gross-up to account for avoided transmission losses), and TDSP Voltage Reduction (100 MW). Other resources that may be available include voluntary customer Demand Response, switchable generation resources currently serving the Eastern Interconnection, and additional DC tie imports.
[g] Capacity Available for Operating Reserves, Emergency Conditions (e+f), MW |  | -2492.8386 | -16177.4296 | -17637.4819 | See the Background tab for additional details
Less than 1,000 MW indicates risk of EEA3 Load Shed

## Fall Capacities
Unit Capacities - Fall
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1222
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1209
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 603
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 444
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 19
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 161
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 161
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 322
37 | BASTROP ENERGY CENTER CTG 1 | 21INR0541 | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
38 | BASTROP ENERGY CENTER CTG 2 | 21INR0541 | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
39 | BASTROP ENERGY CENTER STG | 21INR0541 | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 236
40 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 160.5
41 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 160.5
42 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 159.5
43 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 83.3
44 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 221.5
45 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 168
46 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 168
47 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 270
48 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 77
49 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 77
50 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 71
51 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.5
52 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.5
53 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.5
54 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.5
55 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
56 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
57 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 182
58 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 745
59 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 749
60 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 83.9
61 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 76.9
62 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 82.9
63 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 77.2
64 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 107
65 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 110
66 | COLORADO BEND II CTG 7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 332.5
67 | COLORADO BEND II CTG 8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 338.2
68 | COLORADO BEND II STG 9 | 18INR0077 | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 482.8
69 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2008 | 168
70 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2008 | 163
71 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2008 | 163
72 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2008 | 128
73 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 46.5
74 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 48.5
75 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 108.5
76 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
77 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
78 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
79 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
80 | DECKER CREEK STG 2 |  | DECKER_DPG2 | TRAVIS | GAS-ST | SOUTH | 1978 | 420
81 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 72
82 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 71
83 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 70
84 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 71
85 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 194
86 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 206
87 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 194
88 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 206
89 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 179
90 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 290
91 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.5
92 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.5
93 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.5
94 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.5
95 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 153.6
96 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 153.6
97 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 195
98 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 212
99 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 117
100 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
101 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
102 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
103 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
104 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 173
105 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 173
106 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 186
107 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 169
108 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
109 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
110 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 169
111 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
112 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
113 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 409
114 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 409
115 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 155.2
116 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 155.2
117 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 155.4
118 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 155.4
119 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 177.6
120 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 176.5
121 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 119
122 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 234
123 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 390
124 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
125 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
126 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
127 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 50
128 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
129 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
130 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.2
131 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.2
132 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.2
133 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
134 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
135 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
136 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
137 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
138 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
139 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395
140 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435
141 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435
142 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 214
143 | HAYS ENERGY FACILITY CSG 2 | 21INR0527 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 216
144 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 215
145 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 218
146 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 145
147 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 145
148 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 173
149 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 150
150 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 150
151 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 150
152 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 150
153 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 285
154 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 285
155 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 163
156 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 106
157 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 392
158 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 523
159 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 161
160 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 153
161 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 153
162 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 161
163 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 204
164 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 204
165 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 93
166 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 90.2
167 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 46
168 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 46
169 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 46
170 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 46
171 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 178
172 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 172
173 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 188
174 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 212.5
175 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 212.5
176 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 254.9
177 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 233
178 | MIDLOTHIAN ENERGY FACILITY CTG 2 | 21INR0534 | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 231
179 | MIDLOTHIAN ENERGY FACILITY CTG 3 | 22INR0543 | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 230
180 | MIDLOTHIAN ENERGY FACILITY CTG 4 | 21INR0534 | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 233
181 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 245
182 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 247
183 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 68
184 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 67
185 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 67
186 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 68
187 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 69
188 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 69
189 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122
190 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118
191 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568
192 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 161
193 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 161
194 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 322
195 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 420
196 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 410
197 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 167.5
198 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 159
199 | ODESSA-ECTOR POWER CTG 21 | 20INR0282 | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 167.5
200 | ODESSA-ECTOR POWER CTG 22 | 20INR0282 | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 159
201 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 207.2
202 | ODESSA-ECTOR POWER STG 2 | 20INR0282 | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 207.2
203 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 217
204 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 216
205 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 307
206 | PANDA TEMPLE I POWER CTG 1 | 22INR0533 | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 218.5
207 | PANDA TEMPLE I POWER CTG 2 | 22INR0533 | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 218.5
208 | PANDA TEMPLE I POWER STG 1 | 22INR0533 | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1
209 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 218.5
210 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 218.5
211 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1
212 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 86
213 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 86
214 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 87
215 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
216 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
217 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
218 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.6
219 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.6
220 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.6
221 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.6
222 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 64
223 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 66
224 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 65
225 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 65
226 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 66
227 | PES 1 POWER PLANT CTG 1 |  | PES1_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.4
228 | PES 1 POWER PLANT CTG 2 |  | PES1_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.4
229 | PES 1 POWER PLANT CTG 3 |  | PES1_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.4
230 | PES 1 POWER PLANT CTG 4 |  | PES1_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.4
231 | PES 1 POWER PLANT CTG 5 |  | PES1_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.4
232 | PES 1 POWER PLANT CTG 6 |  | PES1_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 45.4
233 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 61
234 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 62
235 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 52
236 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
237 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
238 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 55
239 | POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 17.5
240 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 23.5
241 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 39.5
242 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 81
243 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 81
244 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 80
245 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 80
246 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98
247 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98
248 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
249 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
250 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 75
251 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 120
252 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 208
253 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 95
254 | RAY OLINGER STG 1 |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78
255 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 107
256 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 146
257 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
258 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
259 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
260 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
261 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 164
262 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 164
263 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 164
264 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 307
265 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
266 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 51
267 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
268 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 40
269 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
270 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
271 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
272 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
273 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
274 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
275 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 151
276 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
277 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
278 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 148
279 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 46
280 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 38
281 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 20
282 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 130
283 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 135
284 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 336
285 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
286 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
287 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 167
288 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 502
289 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 14
290 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
291 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
292 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
293 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
294 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
295 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
296 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
297 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
298 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
299 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
300 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
301 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
302 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
303 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
304 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 110
305 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 110
306 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 99.1
307 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 99.1
308 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 99.1
309 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 131.5
310 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 235
311 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 48
312 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 48
313 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 48
314 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 47
315 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 217
316 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 230
317 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 412
318 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.5
319 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.5
320 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.5
321 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.5
322 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 171
323 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 132
324 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 13
325 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
326 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
327 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 246
328 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 536
329 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20
330 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20
331 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20
332 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 17
333 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
334 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
335 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
336 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
337 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 245.4
338 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 245.4
339 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 298
340 | WOLF HOLLOW 2 CTG 4 | 18INR0076 | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 330.8
341 | WOLF HOLLOW 2 CTG 5 | 18INR0076 | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 331.3
342 | WOLF HOLLOW 2 STG 6 | 18INR0076 | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 470.8
343 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 245.3
344 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 245.3
345 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 270
346 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
347 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
348 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
349 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
350 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
351 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
352 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
353 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
354 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
355 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
356 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 65207.6
357
358 | Operational Resources (Hydro)
359 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
360 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
361 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
362 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
363 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
364 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
365 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
366 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 49.5
367 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 49.5
368 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
369 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
370 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
371 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
372 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
373 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
374 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
375 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
376 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
377 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
378 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 34
379 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
380 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36
381 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22
382 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22
383 | Operational Capacity Total (Hydro) | [6 empty] | 555.4
384 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 414.179
385
386 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
387 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
388 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
389 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
390 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
391 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
392 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7
393 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 14.6909
394
395 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -981.4744
396 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 64654.9956
397
398 | Operational Resources (Switchable)
399 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56
400 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56
401 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56
402 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 195
403 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 195
404 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 180
405 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 180
406 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 180
407 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400
408 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 162
409 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179
410 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 178
411 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 389
412 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 154
413 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 151
414 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 312
415 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 149
416 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 150
417 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 317
418 | Switchable Capacity Total | [6 empty] | 3639
419
420 | Switchable Capacity Unavailable to ERCOT
421 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
422 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
423 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
424 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
425 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
426 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -558
427
428 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 0
429
430 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 2779.667
431 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | -37
432
433 | Operational Resources (Wind)
434 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
435 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
436 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
437 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
438 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
439 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.3
440 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
441 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
442 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 98
443 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 96
444 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2
445 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6
446 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6
447 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
448 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
449 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.4
450 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
451 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6
452 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
453 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
454 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8
455 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9
456 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
457 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
458 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
459 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
460 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
461 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2
462 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
463 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.1
464 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201
465 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
466 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.8
467 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1
468 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4
469 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
470 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
471 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2
472 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4
473 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8
474 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9
475 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100
476 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.2
477 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.6
478 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
479 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
480 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
481 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
482 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150
483 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
484 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
485 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2
486 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
487 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
488 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.2
489 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6
490 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150
491 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64
492 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110
493 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102
494 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98
495 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5
496 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8
497 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 161
498 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98
499 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96
500 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.9
501 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.3
502 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 57
503 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7
504 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8
505 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7
506 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.8
507 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.1
508 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.6
509 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.3
510 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120
511 | BLUE SUMMIT WIND 1 A |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 8.8
512 | BLUE SUMMIT WIND 1 B |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 124.3
513 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 89.7
514 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.7
515 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.4
516 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 182.4
517 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162
518 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9
519 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7
520 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6
521 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5
522 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117
523 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2
524 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 88
525 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 90
526 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2
527 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4
528 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1
529 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 130.5
530 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 120
531 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7
532 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5
533 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9
534 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | COKE | WIND-O | WEST | 2008 | 121.5
535 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75
536 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75
537 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5
538 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5
539 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5
540 | DESERT SKY WIND 1 | 17INR0070 | INDNENR_INDNENR | PECOS | WIND-O | WEST | 2002 | 85.1
541 | DESERT SKY WIND 2 | 17INR0070 | INDNENR_INDNENR_2 | PECOS | WIND-O | WEST | 2002 | 85.1
542 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 118.7
543 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 98.9
544 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 131.1
545 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200
546 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8
547 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6
548 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5
549 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8
550 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2
551 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80
552 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6
553 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6
554 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82
555 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76
556 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 21INR0532 | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99
557 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 21INR0532 | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61
558 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
559 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
560 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.9
561 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 163.5
562 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5
563 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5
564 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52
565 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98
566 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100
567 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4
568 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46
569 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 52
570 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3
571 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.5
572 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3
573 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.6
574 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.6
575 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 131.1
576 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 98.9
577 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230
578 | HORSE HOLLOW WIND 2 | 17INR0053 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184
579 | HORSE HOLLOW WIND 3 | 17INR0053 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4
580 | HORSE HOLLOW WIND 4 | 17INR0053 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115
581 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95
582 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102
583 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8
584 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.7
585 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230
586 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96
587 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74
588 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30
589 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110
590 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7
591 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7
592 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5
593 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7
594 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 160
595 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7
596 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.3
597 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.8
598 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194
599 | LONE STAR WIND 2 (POST OAK) U1 | 22INR0479 | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98
600 | LONE STAR WIND 2 (POST OAK) U2 | 22INR0479 | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100
601 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48
602 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51
603 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5
604 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24
605 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200
606 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200
607 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110
608 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.6
609 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.6
610 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6
611 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.6
612 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60
613 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8
614 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5
615 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5
616 | PANTHER CREEK WIND 3 | 21INR0449 | PC_SOUTH_PANTHER3 | HOWARD | WIND-O | WEST | 2009 | 199.5
617 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7
618 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86
619 | PYRON WIND 1 |  | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5
620 | PYRON WIND 2 |  | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5
621 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150
622 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150
623 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.3
624 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 103
625 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6
626 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9
627 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.4
628 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114
629 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95
630 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160
631 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9
632 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9
633 | SAND BLUFF WIND | 20INR0296 | MCDLD_SBW1 | GLASSCOCK | WIND-O | WEST | 2008 | 90
634 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78
635 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.2
636 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150
637 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1
638 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132
639 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8
640 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 98.2
641 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 120
642 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 211.2
643 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 164.7
644 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5
645 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8
646 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8
647 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6
648 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6
649 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 85
650 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112
651 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125
652 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150
653 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150
654 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.7
655 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6
656 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150
657 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23
658 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5
659 | TRENT WIND | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 156.5
660 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4
661 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6
662 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 169.5
663 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6
664 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12
665 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2
666 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8
667 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22
668 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8
669 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.3
670 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.6
671 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30
672 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125
673 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125
674 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5
675 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5
676 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2
677 | Operational Capacity Total (Wind) | [6 empty] | 27278.2
678
679 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 4205.1
680 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 35
681
682 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4407.7
683 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 44
684
685 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 18665.4
686 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 37
687
688 | Operational Resources (Solar)
689 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
690 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
691 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30
692 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100
693 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15
694 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
695 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50
696 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
697 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7
698 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144
699 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 150
700 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
701 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
702 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 124.6
703 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 130.4
704 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2
705 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3
706 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5
707 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1
708 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5
709 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8
710 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7
711 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180
712 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
713 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
714 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100
715 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
716 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112
717 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.1
718 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 128.1
719 | PROSPERO SOLAR 1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6
720 | PROSPERO SOLAR 2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150
721 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5
722 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5
723 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5
724 | QUEEN SOLAR PHASE II |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5
725 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 200
726 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
727 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
728 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
729 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8
730 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
731 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
732 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9
733 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9
734 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182
735 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
736 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100
737 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10
738 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
739 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
740 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
741 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5
742 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5
743 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5
744 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5
745 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5
746 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5
747 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10
748 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10
749 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5
750 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10
751 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
752 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5
753 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3
754 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
755 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5
756 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10
757 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3
758 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10
759 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2
760 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
761 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
762 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6
763 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2
764 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10
765 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
766 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
767 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
768 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
769 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
770 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5
771 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5
772 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5
773 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10
774 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10
775 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5
776 | Operational Capacity Total (Solar) | [6 empty] | 5354.1
777 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 68
778
779 | Operational Resources (Storage)
780 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
781 | BRP ALVIN (DGR) |  | BRPALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
782 | BRP ANGELTON (DGR) |  | BRPANGLE_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
783 | BRP BRAZORIA (DGR) |  | BRP_BRAZ_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
784 | BRP DICKINSON (DGR) |  | BRP_DIKN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2021 | 10
785 | BRP HEIGHTS (DGR) |  | BRHEIGHT_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
786 | BRP MAGNOLIA (DGR) |  | BRPMAGNO_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
787 | BRP SWEENY (DGR) |  | BRP_SWNY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2021 | 10
788 | BRP ODESSA SW (DGR) |  | BRPODESA_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 10
789 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2019 | 9.9
790 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10
791 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2021 | 40.3
792 | FLAT TOP BATTERY (DGR) |  | FLTBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
793 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2021 | 9.9
794 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 100
795 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2021 | 2
796 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
797 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.3
798 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
799 | OCI ALAMO 1 |  | OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
800 | PORT LAVACA BATTERY (DGR) |  | PTLBES_BESS1 | CALHOUN | STORAGE | COASTAL | 2020 | 9.9
801 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.9
802 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
803 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9
804 | SNYDER (DGR) |  | SNY_BESS_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.9
805 | SWOOSE BATTERY (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9
806 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
807 | TRIPLE BUTTE (DGR) |  | TRIPBUT1_BELU1 | PECOS | STORAGE | WEST | 2021 | 7.5
808 | WESTOVER BESS (DGR) |  | WOV_BESS_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.9
809 | WORSHAM BATTERY (DGR) |  | WRSBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
810 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5
811 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5
812 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2
813 | Operational Capacity Total (Storage) | [6 empty] | 432.6
814 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0
815
816 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
817
818 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
819
820 | Non-Synchronous Tie Resources
821 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600
822 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220
823 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100
824 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300
825 | Non-Synchronous Ties Total | [6 empty] | 1220
826 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 59
827
828 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
829 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2022 | 0
830 | BRAES POWER PLANT | 20INR0221 |  | FORT BEND | GAS-GT | HOUSTON | 2022 | 0
831 | BRANDON (LP&L) (DGR) | 21INR0201 |  | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 20
832 | CHAMON 2 | 19INR0056 |  | HARRIS | GAS-GT | HOUSTON | 2021 | 93
833 | MARK ONE POWER STATION | 22INR0369 |  | BRAZORIA | GAS-GT | COASTAL | 2022 | 0
834 | MIRAGE | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2022 | 0
835 | OLD BLOOMINGTON ROAD | 19INR0057 |  | VICTORIA | GAS-GT | SOUTH | 2021 | 93
836 | PES 2 POWER STATION | 22INR0371 |  | HARRIS | GAS-GT | HOUSTON | 2021 | 90.88
837 | R MASSENGALE (LP&L) | 21INR0202 |  | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 74
838 | TOPAZ POWER PLANT* | 20INR0231 |  | GALVESTON | GAS-GT | HOUSTON | 2021 | 454.4
839 | TY COOKE (LP&L) | 21INR0506 |  | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 31
840 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 856.28
841
842 | Planned Wind Resources with Executed SGIA
843 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2021 | 220
844 | EL ALGODON ALTO W | 15INR0034 |  | SAN PATRICIO | WIND-C | COASTAL | 2021 | 0
845 | EL SUAZ RANCH | 20INR0097 |  | WILLACY | WIND-C | COASTAL | 2022 | 0
846 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2021 | 272.6
847 | MONTE ALTO I | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2022 | 0
848 | WEST RAYMOND (EL TRUENO) WIND | 20INR0088 |  | WILLACY | WIND-C | COASTAL | 2021 | 239.8
849 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2022 | 0
850 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2022 | 0
851 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2023 | 0
852 | AJAX WIND | 20INR0142 |  | WILBARGER | WIND-O | WEST | 2021 | 366.6
853 | ANCHOR WIND | 21INR0387 |  | EASTLAND | WIND-O | NORTH | 2021 | 0
854 | ANCHOR WIND II | 21INR0539 |  | EASTLAND | WIND-O | NORTH | 2021 | 0
855 | APOGEE WIND | 21INR0467 |  | HASKELL | WIND-O | WEST | 2022 | 0
856 | APPALOOSA RUN WIND_ | 20INR0249 |  | UPTON | WIND-O | WEST | 2023 | 0
857 | AQUILLA LAKE 2 WIND | 20INR0256 |  | HILL | WIND-O | NORTH | 2021 | 0
858 | AQUILLA LAKE WIND | 19INR0145 |  | HILL | WIND-O | NORTH | 2021 | 0
859 | BAIRD NORTH WIND | 20INR0083 |  | CALLAHAN | WIND-O | WEST | 2021 | 345
860 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND-O | WEST | 2021 | 160.7
861 | BLACKJACK CREEK WIND | 20INR0068 |  | BEE | WIND-O | SOUTH | 2022 | 0
862 | BOARD CREEK WP | 21INR0324 |  | NAVARRO | WIND-O | NORTH | 2022 | 0
863 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND-O | WEST | 2021 | 148.4
864 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2022 | 0
865 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND-O | WEST | 2021 | 242.6
866 | CRAWFISH | 19INR0177 |  | WHARTON | WIND-O | SOUTH | 2022 | 0
867 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND-O | WEST | 2022 | 0
868 | FOXTROT WIND | 20INR0129 |  | KARNES | WIND-O | SOUTH | 2022 | 0
869 | GRIFFIN TRAIL WIND | 20INR0052 |  | KNOX | WIND-O | WEST | 2021 | 225.6
870 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND-O | WEST | 2021 | 162.1
871 | HUTT WIND | 21INR0005 |  | MIDLAND | WIND-O | WEST | 2022 | 0
872 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
873 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
874 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2023 | 0
875 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2022 | 0
876 | MARYNEAL WINDPOWER | 18INR0031 |  | NOLAN | WIND-O | WEST | 2021 | 182.4
877 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND-O | WEST | 2021 | 373.2
878 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND-O | WEST | 2021 | 118.8
879 | MESTENO WIND | 16INR0081 |  | STARR | WIND-O | SOUTH | 2021 | 201.6
880 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2021 | 0
881 | OVEJA WIND | 18INR0033 |  | IRION | WIND-O | WEST | 2021 | 302.4
882 | PRAIRIE HILL WIND | 19INR0100 |  | MCLENNAN | WIND-O | NORTH | 2021 | 300
883 | PRIDDY WIND | 16INR0085 |  | MILLS | WIND-O | NORTH | 2021 | 0
884 | RELOJ DEL SOL WIND | 17INR0025 |  | ZAPATA | WIND-O | SOUTH | 2021 | 209.3
885 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2022 | 0
886 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND-O | WEST | 2020 | 338.4
887 | TG EAST WIND | 19INR0052 |  | KNOX | WIND-O | WEST | 2021 | 0
888 | VENADO WIND | 16INR0111 |  | STARR | WIND-O | SOUTH | 2021 | 201.6
889 | VORTEX WIND | 20INR0120 |  | THROCKMORTON | WIND-O | WEST | 2022 | 0
890 | WHITE MESA WIND | 19INR0128 |  | CROCKETT | WIND-O | WEST | 2021 | 152.3
891 | WHITE MESA 2 WIND | 21INR0521 |  | COKE | WIND-O | WEST | 2021 | 0
892 | WHITEHORSE WIND | 19INR0080 |  | FISHER | WIND-O | WEST | 2020 | 418.9
893 | WILDWIND | 20INR0033 |  | COOKE | WIND-O | NORTH | 2021 | 180.1
894 | Planned Capacity Total (Wind) | [6 empty] | 5362.4
895
896 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 732.4
897 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 35
898
899 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0
900 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 44
901
902 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 4630
903 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 37
904
905 | Planned Solar Resources with Executed SGIA
906 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2023 | 0
907 | ANDROMEDA SOLAR | 22INR0412 |  | SCURRY | SOLAR | WEST | 2023 | 0
908 | ANSON SOLAR | 19INR0081 |  | JONES | SOLAR | WEST | 2021 | 201.6
909 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2021 | 185
910 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2022 | 0
911 | AZURE SKY SOLAR | 21INR0477 |  | HASKELL | SOLAR | WEST | 2021 | 228.4
912 | BIG STAR SOLAR | 21INR0413 |  | BASTROP | SOLAR | SOUTH | 2022 | 0
913 | BLUE JAY SOLAR | 19INR0085 |  | GRIMES | SOLAR | NORTH | 2022 | 0
914 | BLUE JAY SOLAR II | 21INR0538 |  | GRIMES | SOLAR | NORTH | 2022 | 0
915 | BPL FILES SOLAR | 20INR0164 |  | HILL | SOLAR | NORTH | 2022 | 0
916 | BRASS FORK SOLAR | 22INR0270 |  | HASKELL | SOLAR | WEST | 2023 | 0
917 | BRAVEPOST SOLAR | 20INR0053 |  | TOM GREEN | SOLAR | WEST | 2023 | 0
918 | BRIGHT ARROW SOLAR | 22INR0242 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
919 | BRIGHTSIDE SOLAR | 18INR0060 |  | BEE | SOLAR | SOUTH | 2021 | 0
920 | BUFFALO CREEK (OLD 300 SOLAR CENTER) | 21INR0406 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
921 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2022 | 0
922 | CASTRO SOLAR | 20INR0050 |  | CASTRO | SOLAR | PANHANDLE | 2022 | 0
923 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2023 | 0
924 | CONCHO VALLEY SOLAR | 21INR0384 |  | TOM GREEN | SOLAR | WEST | 2022 | 0
925 | CORAZON SOLAR PHASE I | 15INR0044 |  | WEBB | SOLAR | SOUTH | 2021 | 202.6
926 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2025 | 0
927 | COTTONWOOD BAYOU | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0
928 | COTTONWOOD BAYOU SOLAR II | 21INR0228 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0
929 | CUTLASS SOLAR | 19INR0131 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
930 | DANCIGER SOLAR | 20INR0098 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
931 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
932 | DANISH FIELDS SOLAR II | 21INR0016 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
933 | DANISH FIELDS SOLAR III | 21INR0017 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
934 | DAWN SOLAR | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2022 | 0
935 | DELILAH SOLAR 1 | 22INR0202 |  | LAMAR | SOLAR | NORTH | 2022 | 0
936 | DELILAH SOLAR 2 | 22INR0203 |  | LAMAR | SOLAR | NORTH | 2023 | 0
937 | DELILAH SOLAR 3 | 23INR0042 |  | LAMAR | SOLAR | NORTH | 2023 | 0
938 | DELILAH SOLAR 4 | 23INR0060 |  | LAMAR | SOLAR | NORTH | 2023 | 0
939 | EIFFEL SOLAR | 22INR0223 |  | LAMAR | SOLAR | NORTH | 2023 | 0
940 | ELARA SOLAR | 21INR0276 |  | FRIO | SOLAR | SOUTH | 2021 | 0
941 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2022 | 0
942 | EQUINOX SOLAR 1 | 21INR0226 |  | STARR | SOLAR | SOUTH | 2025 | 0
943 | ESTONIAN SOLAR FARM | 22INR0335 |  | DELTA | SOLAR | NORTH | 2023 | 0
944 | EUNICE SOLAR | 20INR0219 |  | ANDREWS | SOLAR | WEST | 2021 | 426.7
945 | FAGUS SOLAR PARK (MISAE SOLAR II) | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2023 | 0
946 | FENCE POST SOLAR | 22INR0404 |  | NAVARRO | SOLAR | NORTH | 2022 | 0
947 | FIGHTING JAYS SOLAR | 21INR0278 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
948 | FORT BEND SOLAR | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
949 | FRYE SOLAR | 20INR0080 |  | SWISHER | SOLAR | PANHANDLE | 2022 | 0
950 | GALLOWAY 1 SOLAR | 19INR0121 |  | CONCHO | SOLAR | WEST | 2021 | 257
951 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2023 | 0
952 | GOLINDA SOLAR | 21INR0434 |  | FALLS | SOLAR | NORTH | 2023 | 0
953 | GRANDSLAM SOLAR | 21INR0391 |  | ATASCOSA | SOLAR | SOUTH | 2022 | 0
954 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2023 | 0
955 | GRIZZLY RIDGE SOLAR | 21INR0375 |  | HAMILTON | SOLAR | NORTH | 2022 | 0
956 | HOPKINS SOLAR | 20INR0210 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
957 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2023 | 0
958 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2021 | 0
959 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2022 | 0
960 | JADE SOLAR | 22INR0360 |  | SCURRY | SOLAR | WEST | 2022 | 0
961 | LILY SOLAR | 19INR0044 |  | KAUFMAN | SOLAR | NORTH | 2021 | 147.6
962 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2021 | 226.8
963 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2023 | 0
964 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
965 | MARKUM SOLAR | 20INR0230 |  | MCLENNAN | SOLAR | NORTH | 2022 | 0
966 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2021 | 240
967 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2022 | 0
968 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2022 | 0
969 | MYRTLE SOLAR | 19INR0041 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
970 | MYRTLE SOLAR II | 20INR0263 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
971 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2023 | 0
972 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2023 | 0
973 | NEBULA SOLAR (RAYOS DEL SOL) | 19INR0045 |  | CAMERON | SOLAR | COASTAL | 2021 | 0
974 | NOBLE SOLAR | 20INR0214 |  | DENTON | SOLAR | NORTH | 2022 | 0
975 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2023 | 0
976 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2023 | 0
977 | OYSTERCATCHER SOLAR | 21INR0362 |  | ELLIS | SOLAR | NORTH | 2024 | 0
978 | PEREGRINE SOLAR | 22INR0283 |  | GOLIAD | SOLAR | SOUTH | 2023 | 0
979 | PHOENIX SOLAR | 19INR0091 |  | FANNIN | SOLAR | NORTH | 2021 | 83.9
980 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
981 | PISGAH RIDGE SOLAR | 22INR0254 |  | NAVARRO | SOLAR | NORTH | 2022 | 0
982 | PLAINVIEW SOLAR (RAMSEY SOLAR) | 20INR0130 |  | WHARTON | SOLAR | SOUTH | 2022 | 514
983 | PROSPERO SOLAR II | 21INR0229 |  | ANDREWS | SOLAR | WEST | 2021 | 252.9
984 | RADIAN SOLAR | 21INR0205 |  | BROWN | SOLAR | NORTH | 2022 | 0
985 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2023 | 0
986 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) | 17INR0020a |  | PECOS | SOLAR | WEST | 2021 | 222
987 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) | 17INR0020b |  | PECOS | SOLAR | WEST | 2021 | 28
988 | RED-TAILED HAWK SOLAR | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2023 | 0
989 | ROSELAND SOLAR | 20INR0205 |  | FALLS | SOLAR | NORTH | 2022 | 0
990 | SAMSON SOLAR 1 | 21INR0221 |  | LAMAR | SOLAR | NORTH | 2022 | 0
991 | SAMSON SOLAR 2 | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2023 | 0
992 | SAMSON SOLAR 3 | 21INR0491 |  | LAMAR | SOLAR | NORTH | 2022 | 0
993 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
994 | SCHOOLHOUSE SOLAR | 22INR0211 |  | LEE | SOLAR | SOUTH | 2023 | 0
995 | SHAKES SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2022 | 0
996 | SIGNAL SOLAR | 20INR0208 |  | HUNT | SOLAR | NORTH | 2023 | 0
997 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2023 | 0
998 | SOLEMIO | 19INR0093 |  | HOPKINS | SOLAR | NORTH | 2023 | 0
999 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
1000 | SPANISH CROWN | 21INR0323 |  | FALLS | SOLAR | NORTH | 2023 | 0
1001 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2022 | 0
1002 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2022 | 0
1003 | STRATEGIC SOLAR 1 | 20INR0081 |  | ELLIS | SOLAR | NORTH | 2021 | 0
1004 | SUN VALLEY | 19INR0169 |  | HILL | SOLAR | NORTH | 2022 | 0
1005 | SUNRAY | 21INR0395 |  | UVALDE | SOLAR | SOUTH | 2023 | 0
1006 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2021 | 0
1007 | TEXANA SOLAR | 18INR0058 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
1008 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2023 | 0
1009 | TITAN SOLAR (IP TITAN) | 20INR0032 |  | CULBERSON | SOLAR | WEST | 2021 | 267.9
1010 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2022 | 0
1011 | VANCOURT SOLAR | 21INR0213 |  | CAMERON | SOLAR | COASTAL | 2021 | 0
1012 | VISION SOLAR 1 | 20INR0082 |  | NAVARRO | SOLAR | NORTH | 2021 | 0
1013 | WAGYU SOLAR | 18INR0062 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 120
1014 | WESTORIA SOLAR | 20INR0101 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
1015 | ZIER SOLAR | 21INR0019 |  | KINNEY | SOLAR | SOUTH | 2023 | 0
1016 | Planned Capacity Total (Solar) | [6 empty] | 3604.4
1017 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 68
1018
1019 | Planned Storage Resources with Executed SGIA
1020 | ANCHOR BESS | 21INR0474 |  | EASTLAND | STORAGE | NORTH | 2021 | 0
1021 | AZURE SKY BESS | 21INR0476 |  | HASKELL | STORAGE | WEST | 2021 | 0
1022 | BAT CAVE | 21INR0365 |  | MASON | STORAGE | SOUTH | 2021 | 100.5
1023 | BRP ANTLIA BESS | 22INR0349 |  | VAL VERDE | STORAGE | WEST | 2022 | 0
1024 | BRP CACHI BESS | 22INR0388 |  | GUADALUPE | STORAGE | SOUTH | 2022 | 0
1025 | BRP CARINA BESS | 22INR0353 |  | NUECES | STORAGE | COASTAL | 2022 | 0
1026 | BRP DICKENS BESS | 22INR0325 |  | DICKENS | STORAGE | PANHANDLE | 2022 | 0
1027 | BRP HYDRA BESS | 22INR0372 |  | PECOS | STORAGE | WEST | 2022 | 0
1028 | BRP PALEO BESS | 22INR0322 |  | HALE | STORAGE | PANHANDLE | 2022 | 0
1029 | BRP PAVO BESS | 22INR0384 |  | PECOS | STORAGE | WEST | 2022 | 0
1030 | BRP TORTOLAS BESS | 23INR0072 |  | BRAZORIA | STORAGE | COASTAL | 2022 | 0
1031 | CHISHOLM GRID | 20INR0089 |  | TARRANT | STORAGE | NORTH | 2021 | 101.7
1032 | CROSSETT POWER BATT | 21INR0510 |  | CRANE | STORAGE | WEST | 2021 | 200
1033 | DECORDOVA BESS ADDITION | 21INR0459 |  | HOOD | STORAGE | NORTH | 2022 | 0
1034 | ENDURANCE PARK STORAGE | 21INR0479 |  | SCURRY | STORAGE | WEST | 2022 | 0
1035 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2023 | 0
1036 | HIGH LONESOME BESS | 20INR0280 |  | CROCKETT | STORAGE | WEST | 2022 | 0
1037 | HOUSE MOUNTAIN 2 BATT | 22INR0485 |  | BREWSTER | STORAGE | WEST | 2023 | 0
1038 | IGNACIO GRID | 21INR0522 |  | HIDALGO | STORAGE | SOUTH | 2022 | 0
1039 | INERTIA BESS 2 | 22INR0375 |  | HASKELL | STORAGE | WEST | 2022 | 0
1040 | LILY STORAGE | 20INR0294 |  | KAUFMAN | STORAGE | NORTH | 2021 | 51.7
1041 | MADERO GRID | 21INR0244 |  | HIDALGO | STORAGE | SOUTH | 2022 | 0
1042 | NOBLE STORAGE | 22INR0436 |  | DENTON | STORAGE | NORTH | 2022 | 0
1043 | NORTH FORK | 20INR0276 |  | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5
1044 | QUEEN BESS | 20INR0281 |  | UPTON | STORAGE | WEST | 2022 | 0
1045 | RED HOLLY STORAGE | 21INR0033 |  | DAWSON | STORAGE | WEST | 2023 | 0
1046 | REPUBLIC ROAD STORAGE | 21INR0460 |  | ROBERTSON | STORAGE | NORTH | 2021 | 0
1047 | ROUGHNECK STORAGE | 19INR0176 |  | BRAZORIA | STORAGE | COASTAL | 2021 | 0
1048 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2023 | 0
1049 | SILICON HILL STORAGE | 20INR0291 |  | TRAVIS | STORAGE | SOUTH | 2022 | 0
1050 | SP TX-12B BESS | 21INR0357 |  | UPTON | STORAGE | WEST | 2021 | 0
1051 | VORTEX BESS | 21INR0473 |  | THROCKMORTON | STORAGE | WEST | 2022 | 0
1052 | BRP LOOP 463 (DGR) |  | BRP_4631_UNIT1 | VICTORIA | STORAGE | SOUTH | 2021 | 9.9
1053 | BRP LOPENO (DGR) |  | BRP_LOP1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 9.9
1054 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2021 | 9.9
1055 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2020 | 10
1056 | BRP RANCHTOWN (DGR) |  | BRP_RNC1_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.9
1057 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2020 | 10
1058 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 9.9
1059 | SWEETWATER BESS (DGR) |  | SWT_BESS_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.9
1060 | TOYAH POWER STATION (DGR) |  | TOYAH_BESS | REEVES | STORAGE | WEST | 2021 | 9.9
1061 | Planned Capacity Total (Storage) | [6 empty] | 643.7
1062 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 0
1063
1064 | Inactive Planned Resources
1065 | CHOCOLATE BAYOU W | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2022 | 0
1066 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5
1067 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150
1068 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND-P | PANHANDLE | 2022 | 0
1069 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND-P | PANHANDLE | 2021 | 0
1070 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2023 | 0
1071 | INERTIA WIND | 22INR0326 |  | HASKELL | WIND-O | WEST | 2022 | 0
1072 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60
1073 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2023 | 0
1074 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2023 | 0
1075 | LONGBOW SOLAR | 20INR0026 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
1076 | PITTS DUDIK SOLAR | 20INR0074 |  | HILL | SOLAR | NORTH | 2022 | 0
1077 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2022 | 0
1078 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2022 | 0
1079 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
1080 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2020 | 30
1081 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2023 | 0
1082 | INERTIA BESS | 22INR0328 |  | HASKELL | STORAGE | WEST | 2022 | 0
1083 | Inactive Planned Capacity Total | [6 empty] | 392.5
1084
1085 | Seasonal Mothballed Resources
1086 | GREGORY POWER PARTNERS GT1 (AS OF 5/1/2020, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 152
1087 | GREGORY POWER PARTNERS GT2 (AS OF 5/1/2020, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 151
1088 | GREGORY POWER PARTNERS STG (AS OF 5/1/2020,AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 75
1089 | SPENCER STG U4 (AS OF 5/5/2020, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 57
1090 | SPENCER STG U5 (AS OF 5/5/2020, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 61
1091 | NACOGDOCHES POWER (AS OF 10/16/2020, AVAILABLE 5/15 THROUGH 10/15) |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
1092 | Total Seasonal Mothballed Capacity | [6 empty] | 601
1093
1094 | Mothballed Resources
1095 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 430
1096 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
1097 | Total Mothballed Capacity | [6 empty] | 850
1098
1099 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1100 | SNYDER WIND (AS OF 6/1/2021) |  | ENAS_ENA1 | SCURRY | WIND-O | WEST | 2007 | 63
1101 | Total Retiring Capacity | [6 empty] | 63
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide Ancillary Services rather than sustained capacity available to meet system peak loads.
Unit Names with a (DGR) suffix are Distribution Generation Resources. Units rated 10 MW or less currently do not go through the GINR application process.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
* TOPAZ POWER PLANT, 20INR0231: Seven of the ten gas turbine units that make up this plant were approved for commerical operations on 8/26/21.
Note on I395: Extended outages: Schumansville DG hydro plant (3.6 MW) and 2.4 MW of the 4.8 MW Lakewood Tap DG hydro plant (DG_LKWT_2UNITS). R W MILLER STG 1 (MILLER_G1), 75 MW, started 8/14/2020 and expected to last for 18 months. Ray Olinger STG 1 (OLINGR_OLING_1), 78 MW, from 4/1/2021 to 1/1/2022. Limestone U1 (LEG_LEG_G1), 824 MW, from 7/4/2021 to 4/15/2022.

## Background
Release Date: September 3, 2021
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as a system-wide heat wave) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses an operating reserve thresholds of 2,300 and 1,000 MW to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) and Level 3 (EEA3) may be triggered during the time of the forecasted seasonal peak load. These threshold levels are intended to be roughly analogous to the 2,300 and 1,000 MW Physical Responsive Capability (PRC) thresholds for EEA1 and EEA3 with Load Shed, respectively. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 and 1,000 MW reserve capacity thresholds are reasonable indicators for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variation in these parameters is based on historic ranges of the parameter values or known changes expected in the near-term.
Thermal Outage Accounting
Directly comparing SARA thermal unplanned (previously "forced") outage scenario capacity with outage amounts listed in ERCOT outage reports — such as the Unplanned Resource Outages Report — will yield misleading results. The reason is that the SARA report consists of multiple resource availability line items, and thermal outages for certain resource types are reflected elsewhere in the SARA reports rather than the thermal outage scenario line items. As a result, the SARA thermal outage scenario amounts will always be less than what is typically shown in other outage reports. The main differences include the following:
• Outages for Private Use Network (PUN) generators are incorporated in the line item called “Capacity from Private Use Networks.” This is an aggregate estimate of the amount of energy injected into the ERCOT grid during the highest 20 seasonal hourly demands for the last three years, and incorporates average generator outage amounts over those hourly intervals as well as reflects PUN owner decisions to supply power to their industrial loads versus export to the grid. PUN outages are thus already reflected in the SARA available resource capacity estimate.
• Extended outages are reported in the SARA Capacities tab in a line item called “Operational Capacity Unavailable due to Extended Outage or Derate.” Extended Outages are those forced outages that are expected to last a minimum of 180 days as reported by the resource owner via submission of a Notice of Suspension of Operations (NSO) form. These outages are thus already reflected in the SARA available resource capacity estimate.
• The capacity of Switchable Generation Resources (SWGRs) that are assumed to serve a neighboring grid for the season is deducted from available resource capacity, so outages associated with these SWGRs are not reflected anywhere in the SARA report.
To more closely align the SARA with other outage reports based on ERCOT Outage Scheduler data, a modification was made to the treatment of outages classified as Unavoidable Extensions, or UEs. UEs are defined as "a Planned or Maintenance Outage that is not completed within the ERCOT-approved timeframe and extended." For past SARA reports, if the original outage was classified as Planned in the Outage Scheduler, then the UE would continue to be classified as Planned. If the original outage was classified as Forced, then the UE would continue to be classified as Forced. In contrast, for other ERCOT outage reports, UE outages are all classified as Forced (Unplanned). SARA reports now treat all UEs as Unplanned. While this category change does not impact the total base outage amount, it does increase the high and extreme unplanned thermal adjustments used in several risk scenarios.