## Slide 1
Proposed 2022 Ancillary Service Methodology And Preliminary Quantities
PDCWG
September 08, 2021
ERCOT Staff

## Slide 2: Stakeholder Discussion Timeline
August 11, 2021 – PDCWG (Current Methodology)
August 23, 2021 – WMWG (Current Methodology)
September 08, 2021 – PDCWG (Proposed Methodology)
September 22, 2021 – WMWG (Proposed Methodology)
October 13, 2021 – PDCWG (Proposed Methodology)
October 21, 2020 – OWG (Proposed Methodology)
October 25, 2021 – WMWG (Proposed Methodology)
November 03, 2021 - WMS
November 04, 2021 - ROS
November 17, 2021 - TAC
December 14, 2021 - BoD

## Slide 3: Summary of Feedback from August Meeting
Regulation
  Frequency profile particularly through mid-day and sunset hours has noticeable drags. Understand underlying drivers for exhaustion of Regulation.
  Review GTBD parameters and Regulation deployment parameters in LFC.
RRS
  Continue using the 2800 MW floor for peak hours.
  Assess if changes to Load dampening factor in RRS studies are needed to account for changing load composition (motor load vs electronic load).
Non-Spin
  Consider using an intra-day forced outage methodology that reasonably represents variations in intra-day changes in forced outage.
  Share Non-Spin deployment data. {included in last slide}

## Slide 4: Discussion Scope
ERCOT is not recommending any changes to the methodology used for computing Regulation Service requirements for 2022.
ERCOT is recommending one change in the methodology used for computing Responsive Reserve Service (RRS) requirements for 2022 for the peak hours.
ERCOT is recommending changes in the methodology used for computing Non-Spinning Reserve Service (Non-Spin) requirements for 2022 to include the highest net load forecast error within an operating hour and account for intra-day changes in thermal resource availabilities (due to forced outages).
The Ancillary Service (A/S) quantities for 2022 contained in this presentation are based on the methodology that was approved in December 2020.
  The quantities for 2022 reflect moving forward the historic data on which these are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities for January through July of 2022 have been posted on the meeting page for this meeting.
ERCOT is seeking stakeholder feedback on these proposes changes for the 2022 A/S Methodology.

## Slide 5: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements for 2022.
  ERCOT will continue to monitor the intra-hour net load ramps and will tune ERCOT’s Generation Applications in EMS when necessary to meet established frequency control related performance criteria.
The preliminary Regulation quantities for January 2022 through July 2022 in subsequent slides have been computed using current methodology (2020 and 2021 five-minute net load variability), updated Wind Adjustment tables and the proposed Solar Adjustment tables.

## Slide 6: Projected Increase in IRR Capacity

## Slide 7: Regulation Exhaustion
Reg-Up
Reg-Down

## Slide 8: Net Load Ramps vs Netload Ramp Forecast in GTBD
Average Net-Load 5 min Ramp
Average Net-Load 5-min Ramp Forecast Error
Positive: Actual NL > Forecast NL, Under-dispatch
Negative: Actual NL < Forecast NL Over-dispatch
Notes: Why does the avg net load ramp change signs in HE17-20 May - Jul?

## Slide 9: Solar Ramps Forecast
Error = PSRR Forecast - Actual

## Slide 10: Wind Adjustment Tables - 2022
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Notes: Avg Reg Up adjustment for wind is 1.57 MW
Avg Reg Down adjustment for wind is 1.44 MW

## Slide 11: Solar Adjustment Tables - 2022
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
Notes: Avg Reg Up adjustment for wind is 3.9 MW
Avg Reg Down adjustment for wind is 4.15 MW

## Slide 12: Regulation January
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 209 MW in HE17. Daily Average increase is ~39 MW.
Largest change in Reg Down is 194 MW in HE10. Daily Average increase is ~47 MW.

## Slide 13: Regulation Up March
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 309 MW in HE17. Daily Average increase is ~91 MW.
Largest change in Reg Down is 248 MW in HE10. Daily Average increase is ~83 MW.

## Slide 14: Regulation Up June
Notes: Trends between blue and red are fairly similar.
Largest change in Reg Up is 147 MW in HE20. Daily Average increase is ~52 MW.
Largest change in Reg Down is 125 MW in HE17. Daily Average increase is ~35 MW.

## Slide 15: Average Regulation Comparison
Notes: Reg Up
On an average blue and red are fairly similar. Largest increase is 91 MW in Mar
Reg Do
On an average blue and red are fairly similar. Largest increase is 94 MW in May

## Slide 16: Responsive Reserve Service (RRS) Methodology
ERCOT is proposing one change to the methodology used to compute the minimum RRS requirements for 2022.
  A floor of 2800 MW will be applied to RRS quantities during the peak. During the peak hour, this additional RRS will help maintain a larger operating margin.
The preliminary RRS quantities for January 2022 through July 2022 in subsequent slides have been computed using 2020 and 2021 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated for 2021 to use a minimum RRS-PFR limit of 1420 MW.

## Slide 17: RRS January
Chart: 
| a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
2021 (Dec Posting) | 3053 | 3053 | 2959 | 2880 | 2880 | 2959
2022 (Dec-2020 Methodology) | 3053 | 3053 | 2959 | 2959 | 2959 | 2959
2022 (2800 MW floor peak hours) | 3053 | 3053 | 2959 | 2959 | 2959 | 2959
2021 (July 12 Posting) | 3053 | 3053 | 2959 | 2880 | 2880 | 2959
Notes: Trends between blue and red are fairly similar.
Max Change between blue and red/gray in HE11-18 is 79 MW. No Change between red and gray
On an average decrease between blue and red/gray of 26 MW

## Slide 18: RRS May
Notes: Trends between blue and red are fairly similar.
Max Change between blue and red/gray in HE7-10 is 222 MW. Max Change between red and gray in HE15-22 is 17 MW.
On an average increase between blue and gray of 145 MW

## Slide 19: RRS July
Notes: Trends between blue and red are fairly similar.
Max Change between blue and gray in HE1-2 & HE23-24 is 54 MW.
On an average increase blue and gray of 9 MW

## Slide 20: Hourly Average RRS Comparison
Notes: On an average blue and red/gray are fairly similar.
On an average largest increase between blue and gray is 145 MW in May

## Slide 21: Non-Spinning Reserve Service Methodology
ERCOT is proposing the following changes to the methodology used to compute minimum Non-Spin requirements in 2022
  Update the hourly net load forecast uncertainty calculation to use
    the 6 Hours-Ahead net load forecast, and
    the highest 5-min net load within the hour
  Change percentile coverage to vary between 85th and 95th . The applicable coverage for any hour will continue to be based on risk of net load up ramp in the hour
  Build a table that tracks historical intra-day variations in thermal resource availabilities due to Forced Outages and use it to incrementally increase Non-Spin quantities.
ERCOT will continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for Operating Hours that are identified as having an increased potential of high forecast variability that may cause a higher net load during these hours.
The preliminary Non-Spin quantities for January 2022 through July 2022 in subsequent slides have been computed using current methodology (2019, 2020 and 2021 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the proposed Solar Over-Forecast Error Adjustment table.

## Slide 22: Drivers for the methodology changes
3 Hours Ahead vs. 6 Hours Ahead: On tighter days in Summer months generally units with 6 hours+ lead times tend to be available for RUC; these lead time tend to double during winter when units available for RUC are typically “cold”. Since forecast uncertainties tend to be a bit higher further away from the operating hours, using 6-hours ahead forecast errors allows to better reflect this risk in the computed Non-Spin quantities.
Hourly Average vs. Max 5-min Net load: Intra-hour net load patterns due to load/wind/solar can be vastly different even with same hourly average values. By using the highest 5-min net load within the hour, the largest net load forecast error for the hour will be used in determining Non-Spin quantities.
75th to 95th vs. 85th to 95th Percentile Coverage: Larger net load forecast errors have been observed during off peak hours. This change captures the increased risk for off peak hours in the Non-Spin methodology.
Intra-day Forced Outage table: This table will help account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 23: Trends in 6HA Net Load Forecast Error
As years progress, an increase in magnitude of the 6 Hours-Ahead net load forecast error can be observed during off peak hours

## Slide 24: Intra-Day Forced Outage Rate
For 2018, 2019 and 2020, the heat maps below show the 75th percentile of the maximum accumulated forced outage on thermal units (excluding IRR and PUN) since midnight for every hour in each month.

## Slide 25: Intra-Day Forced Outage Rate vs Net Load Forecast Error
For every hour in 2019 and 2020, the plot below tracks the maximum accumulated forced outage on thermal units (excluding IRR and PUN) since midnight as a function of 6 Hour-Ahead net load forecast error for the hour.
  The largest accumulated intra-day forced outage is ~3,500 MW and the largest 6 Hour-Ahead net load forecast error is ~15,000 MW.
As can be observed, extreme intra-day forced outages and highest net load forecast error do not tend to occur at the same time.
  *Forced Outages on thermal units, excluding IRR and PUN

## Slide 26: Proposed Intra-Day Forced Outage Table 2022
The proposed Intra-Day Forced Outage table has been built using 75th percentile of the maximum accumulated forced outage in a 6-hour block for each month in 2018, 2019, 2020.
  For the purposes of building this table, a conservative 75th percentile coverage is recommended due to the observation that the extreme forced outages tend to not occur at the same time as the highest net load forecast error.

## Slide 27: Wind Over-Forecast Error Adjustment Table 2022
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind capacity.
Max: 39 MW per 1000 MW additional Wind capacity
Mean: 31 MW per 1000 MW additional Wind capacity

## Slide 28: Solar Over-Forecast Error Adjustment Table 2022
Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Max: 56 MW per 1000 MW additional solar capacity
Mean: 13 MW per 1000 MW additional solar capacity

## Slide 29: Non-Spin January
Notes: Max change between red and purple in He15-18 is 2878 MW.
Largest value 4520 MW in HE15-18.
On an average increase of 2135 MW

## Slide 30: Non-Spin February
Notes: Max change between red and purple in He15-18 is 3032 MW.
Largest value 5117 MW in HE15-18.
On an average increase of 2361 MW

## Slide 31: Non-Spin March
Notes: Max change between red and purple in HE23-24 is 2218 MW.
Largest value 4311 MW in HE15-18.
On an average increase of 1804 MW

## Slide 32: Non-Spin April
Notes: Max change between red and purple in HE23-24 is 2369 MW.
Largest value 4394 MW in HE7-10.
On an average increase of 2023 MW

## Slide 33: Non-Spin May
Notes: Max change between red and purple in HE15-19 is 2513 MW.
Largest value 4994 MW in HE13-14.
On an average increase of 2339 MW

## Slide 34: Non-Spin June
Notes: Max change between red and purple in HE1-2,23-24 is 2896 MW.
Largest value 4839 MW in HE13-14.
On an average increase of 2367 MW

## Slide 35: Non-Spin July
Notes: Max change between red and purple in HE13-14 is 2635 MW.
Largest value 4293 MW in HE13,14.
On an average increase of 2153 MW

## Slide 36: Hourly Average Non-Spin Comparison
Notes: On an average largest increase between red and purple is 2367 MW in June

## Slide 37
Discussion

## Slide 38: Monthly Non-Spin Deployment 2019 through 2021*
Deployment of Non-Spin from online Resources with an Energy Offer Curve is considered as a standing Non-Spin deployment Dispatch Instruction for the duration of the Operating Hour.
Table below contains summary of monthly offline Non-Spin deployments
  *Partial Year (till August, 2021)
Year | Month | Day | Maximum MW Deployed | Total Duration (hr)
2019 | September | 22 | 74 | 0.03
2019 | October | 5 | 305 | 1.22
2019 | December | 22 | 115 | 3.54
2020 | February | 3 | 145 | 4.50
2021 | February | 13 | 324 | 3.81
2021 | February | 14 | 149 | 0.72
2021 | February | 15 | 389 | 24.00
2021 | February | 16 | 422 | 24.00
2021 | February | 17 | 379 | 24.00
2021 | February | 18 | 537 | 24.00
2021 | February | 19 | 372 | 10.15
2021 | April | 11 | 523 | 1.23
2021 | April | 13 | 375 | 3.55
2021 | June | 13 | 696 | 4.63
2021 | June | 14 | 512 | 2.06