## Slide 1
ERCOT Frequency Control Report
August 2021
ERCOT
Operations Planning
PDCWG | September 8th, 2021

## Slide 2: Summary of August 2021
CPS1: 174.29%
Current CPS1 12-Month Rolling Average: 169.47%
4 BAAL Exceedance(s)
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2021 RMS1 Statistics
  Mean: 16.55 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 41,365,985 MWh
  Wind Energy: 7,366,551 MWh
  Percent Energy from Wind: 17.81%
  Solar Energy: 1,678,373 MWh
  Percent Energy from Solar: 4.06%
Minimum System Inertia
  Mean: 271,310 MW*s
  Max: 310,732 MW*s on Aug 31st
  Min: 231,507 MW*s on Aug 10th
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Aug-21 CPS1 (%): 174.29
Notes: 1. 82% @ 08/16/2021 HE 14:00
Expected Generation Deviation
Expected gen dev remained negative during the later part of the hour. The largest expected gen dev was -2143MW @ 13:43 with contribution from thermal and solar. Loss of approx. 1100 MW of generation between 13:32 and 13:40 due to a thermal trip and runback.
IRR Ramps
Solar generation ramped down by approximately 780 MW, which coincided with the generation loss event.
Regulation: Regulation up was exhausted during the generation loss event.
Other
624 MW of RRS was deployed at 13:34, SCED was run manually multiple times and Manual offset of 400 MW @ 13:38
2. 24% @ 08/24/2021 HE 20:00
Expected Generation Deviation
Expected gen dev remained negative for the most part of the hour. The largest expected gen dev was -1655MW @ 19:55 with significant contribution from solar
IRR Ramps
Solar generation ramped down by 3500 MW during this hour.
Regulation: Regulation up was exhausted for most part of the hour
Other
SCED was run manually multiple times

## Slide 5: BAAL Exceedances & Violations
There were 4 BAAL exceedance(s) in August
Notes: Occurred on 8/16/21 due to generation loss event

## Slide 6: 15-Minute Average CPS1%
Aug-21 CPS1 (%): 174.29

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 169.47%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.55 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 41,365,985 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,366,551 MWh

## Slide 23: % Energy from Wind Generation
Notes: 17.81%

## Slide 24: Total Energy From Solar Generation
Notes: 1,678,373 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.06%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 231,507 MW*s on 8/10/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 271,310 MW*s
Max: 310,732 MW*s on Aug 31st
Min: 231,507 MW*s on Aug 10th

## Slide 28: Questions?
Thank you!