## Slide 1
2021 RTP Off-Peak Sensitivity Analysis
Craig Wolf
September 2021
RPG Meeting

## Slide 2: Introduction
NERC Reliability Standard TPL-001-4 requires sensitivity analysis to be performed
The focus of the 2021 RTP off-peak sensitivity analysis will be a stressed resource availability scenario
All 2021 RTP stability limits will be respected in this sensitivity analysis
This case will be built from the 2024MIN RTP case

## Slide 3: Assumptions
The base case will include a significant amount of planned unit outages
  Historical and future outage scheduler data will be utilized to determine outage levels for conventional resources
A base case operating reserve of 3,000 MW will be established
PUN units that don’t participate in the energy market will be left as modeled in the 2024MIN RTP case

## Slide 4: Assumptions Cont’d
Nuclear:
  2,565 MW online
  This represents the outage of one unit at each site
Renewables:
  Wind: 0 MW online
  Solar: 0 MW online
  Hydro: 0 MW online
Batteries:
  0 MW online
DC Ties:
  0 MW import/export

## Slide 5: Assumptions Cont’d
Gas:
  ~12,700 MW offline
  ~40,500 MW online
Coal:
  ~ 4,000 MW offline
  ~ 9,800 MW online
These outage levels are determined from historical and future outage scheduler data
The individual units turned offline in the base case will be determined through a G-1 screening
  This will identify the most severe outages to incorporate

## Slide 6: Assumptions Cont’d
Total Generation:
  ~61,265 MW online
Other load determination factors:
  ~ 4,516 MW of self serve load
  ~ 1,200 MW of estimated losses
  ~ 3,000 MW of operational reserves
Total Load:
  ~ 57,065 MW of load excluding estimated losses
  ~ 52,550 MW of load excluding estimated losses and self-serve load
  Existing load will be scaled to reach the desired load level

## Slide 7
Questions?
Craig.Wolf@ercot.com