## Slide 1: PLWG Extreme Case Group
PLWG Meeting 9/15/2021

## Slide 2: Proposed New Cases / Extreme Events
New Case | Case Description
Extreme cold | Statewide less than 20 degrees Fahrenheit
Extreme heat | Statewide greater than 105 degrees Fahrenheit
Extreme drought | Statewide extended lack of rainfall
Extreme heat and drought | Combination of extreme heat and drought scenarios
Tornadoes | More likely standalone in the North portion of the system
Hurricanes/Tropical Storms | More likely on the coastal side of the system (e.g. Ike, Harvey)

## Slide 3: Extreme Winter Case
6 am time period
February 15, 2021 Weather Assumptions (99/1 Winter)
  Uses a forecast developed by ERCOT
  TSPs would develop the appropriate distribution of the load forecast
Load would be not scaled down to match generation
Solar generation at 0%
Wind generation at 10%
Storage at 0%
Disable reactive capability for IRR units below 10% output
  Currently, no market exists for reactive services
One study would be a G1N1 or GXN1 analysis, where the GX is a group of generation facilities in the same physical area or with a common failure mode (e.g., gas pipeline)
Another study would be systemwide natural gas fired deration of XX% to be reflective of natural gas system not pressurized appropriately
Demand response (voluntary and involuntary) may be needed
  Reduce large Industrial loads as necessary
  If still insufficient to solve the case, reduce other loads on their system
  Involuntary demand response can also be described as energy shortages
  Involuntary demand response would be allocated based on the ERCOT method

## Slide 4: Extreme Heat and Drought Summer Case
6 pm time period
August 2, 2011 Weather Assumptions (99/1 Summer)
  Uses a forecast developed by ERCOT
  TSPs would develop the appropriate distribution of the load forecast
Load would be not scaled down to match generation
Solar generation at 80%
Wind generation at 10%
Storage at 0%
Disable reactive capability for IRR units below 10% output
  Currently, no market exists for reactive services
G1N1 or GXN1 analysis, where the GX is a group of generation facilities with low water risks (both natural gas and coal)
Demand response (voluntary and involuntary) may be needed
  Reduce large Industrial loads as necessary
  If still insufficient to solve the case, reduce other loads on their system
  Involuntary demand response can also be described as energy shortages
  Involuntary demand response would be allocated based on the ERCOT method

## Slide 5: Hurricanes/Tropical Storms/Tornadoes
Summer loads
  Both 90/10 and 99/1 weather assumptions
  Uses forecasts developed by ERCOT
  TSPs would develop the appropriate distribution of the load forecast
Load would be not scaled down to match generation
Solar generation at 80%
Wind generation at 50%
Storage at 0%
Disable reactive capability for IRR units below 10% output
  Currently, no market exists for reactive services
First study would be a G1N1 or GXN1 analysis, where the GX is a group of generation facilities within same physical area i.e. by county or study area like Houston, DFW, Valley or Corpus Christi area generators and N-X analysis removing multiple major transmission lines from service within a specific area (e.g., two 345-kV circuits into the Valley out).
Second study would be a G1N1 or GXN1 analysis, where the GX is a group of generation facilities in the same physical area (same as above) with the addition of a percentage (all or X%) of load being removed in those areas as well and N-X analysis removing multiple major transmission lines from service within a specific area (e.g., two 345-kV circuits into the Valley out).
Demand response (voluntary and involuntary) may be needed
  Reduce large Industrial loads as necessary
  If still insufficient to solve the case, reduce other loads on their system
  Involuntary demand response can also be described as energy shortages
  Involuntary demand response would be allocated based on the ERCOT method

## Slide 6: Appendix

## Slide 7: Members
John Bernecker (ERCOT)
Doug Evans (STEC)
Andrew Hamann (LCRA)
Kevin Hanson (National Grid)
Brian Hithersay (BEPC)
Harsh Naik (Oncor)
Lori Simpson (Exelon)
Mina Turner (AEP)
Monica Walker (GM)