## AVR Template
STATION CODE (EXACT): |  |  | Instructions: Put the exact Station Code and the exact names of your Unit(s) and any reactive devices (If applicable) in the respective column(s) that is in the ERCOT Network Operations Model. Make sure they are the exact spelling and in all CAPS and no spaces.
For Conventional and CC Generators: Fill out the PSS Status ON/OFF columns and the Generator terminal Frequency under Conventional Generation. Hover over the cells that have comments for more information. The PSS Status [ON] column should have the word "ON" in it when the AVR test has the PSS enabled, and likewise the PSS Status [OFF] column should have the word "OFF" in it when the AVR test has the PSS disabled.
ERCOT AVR/PSS Performance Test Guide and Template
IRR and IBR AVR Test Process: | [13 empty] | Conventional and C.C. AVR/PSS Test Process:
[5 empty] | • Coordinate AVR test – QSE coordinates with ERCOT and TSP/TO! • Start with a few minutes of data with the AVR set point at its neutral or nominal setting. • Increase the AVR set-point by 2-4% (not to exceed 1.05 per unit voltage, or lower value if specified by the Transmission Operator or system conditions) and allow sufficient time for the AVR system response to settle (Minimum 5 minutes). • Change the AVR set point back to the nominal set point and allow sufficient time for the AVR system response to settle (Minimum 5 minutes). • Decrease the voltage set-point by 2-4% step-change (limited to 0.95pu), depending on the initial set-point voltage and ERCOT’s and TSP’s feedback on the size of step-change allowable at the time of the test based on system conditions. • Allow sufficient time for the AVR system response to settle (Minimum 5 minutes) • Change the voltage set-point back to the original set-point • Allow sufficient time for the AVR system response to settle (Minimum 5 minutes) • Record all the data and submit the AVR test results to ERCOT via NDCRC Record in 1- 4 sec intervals! | [8 empty] | • Coordinate AVR/PSS test – QSE coordinates with ERCOT and TSP/TO! • The tests should be performed when the generators under test are on-line and at high or full output • If the generator is equipped with a PSS, the PSS should be turned off to verify the functioning and performance of the AVR. Another test should be conducted with the PSS on to verify the functioning and performance of the PSS • A voltage set-point step of ±2-4% is recommended for the tests (limited to the range of .95pu-1.05pu at the POI) • Test data should be collected for at least 1-5 seconds prior to the step change and for at least 10–20 seconds after • The test should begin with the AVR voltage set-point at its neutral or nominal setting. The AVR voltage set-point should be changed by introducing the step and allowed to settle, then the AVR voltage set-point should be returned to the setting prior to the step change and allowed to settle • Record all the data and submit the AVR and/or PSS test results to ERCOT via NDCRC Record in 1- 4 sec intervals! Record in 1- 4 sec intervals!
|  | Voltage Levels (kV) |  |  | Reactive Power Output (MVAr) |  |  |  |  | Real Power Output (MW) |  |  |  |  | Capacitor (MVAr) |  |  |  |  | Reactor (MVAr) |  | SVC/STATCOM/S.C. |  | Conventional Generation (ONLY)
Time Stamp - Local Time (Central Standard Time) MM/DD/YYYY HH:MM:SS | AVR Set Point (kV) | POI or POIB Voltage | MV Bus Voltage | Actual Voltage at Monitored Terminals | Gross MVAr-UNIT_NAME | Gross MVAr-UNIT_NAME | Gross MVAr-UNIT_NAME | Gross MVAr-UNIT_NAME | Gross MVAr-UNIT_NAME | Gross MW-UNIT_NAME | Gross MW-UNIT_NAME | Gross MW-UNIT_NAME | Gross MW-UNIT_NAME | Gross MW-UNIT_NAME | Gross MVAr-CAP_NAME | Gross MVAr-CAP_NAME | Gross MVAr-CAP_NAME | Gross MVAr-CAP_NAME | Gross MVAr-CAP_NAME | Gross MVAr-REACTOR_NAME | Gross MVAr-REACTOR_NAME | Reactive Power-DYN_DEV_NAME | Reactive Power-DYN_DEV_NAME | PSS Status [ON] | PSS Status [OFF] | Generator Terminal Frequency (Hz)
Note on B1: Include ONLY upper case letters and must be between 2 and 8 characters long. The only special characters allowed are underscores and dashes.
Note on B8: Use a 2%-4% step change.
Note on C8: Use POIB voltage if you have that. If not, then this can be the POI voltage.
Note on E8: This is where the AVR control system is controlling voltage.
Note on F8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MVAr-UNIT_NAME -> Gross MVAr-UNIT1.
Note on G8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MVAr-UNIT_NAME -> Gross MVAr-UNIT1.
Note on H8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MVAr-UNIT_NAME -> Gross MVAr-UNIT1.
Note on I8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MVAr-UNIT_NAME -> Gross MVAr-UNIT1.
Note on J8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MVAr-UNIT_NAME -> Gross MVAr-UNIT1.
Note on K8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MW-UNIT_NAME -> Gross MW-UNIT1.
Note on L8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MW-UNIT_NAME -> Gross MW-UNIT1.
Note on M8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MW-UNIT_NAME -> Gross MW-UNIT1.
Note on N8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MW-UNIT_NAME -> Gross MW-UNIT1.
Note on O8: Put the EXACT Unit Name in ALL CAPS after the dash. Example: Gross MW-UNIT_NAME -> Gross MW-UNIT1.
Note on P8: Put the EXACT Capacitor Name in ALL CAPS after the dash. Example: Gross MVAr-CAP_NAME -> Gross MVAr-CAP1.
Note on Q8: Put the EXACT Capacitor Name in ALL CAPS after the dash. Example: Gross MVAr-CAP_NAME -> Gross MVAr-CAP1.
Note on R8: Put the EXACT Capacitor Name in ALL CAPS after the dash. Example: Gross MVAr-CAP_NAME -> Gross MVAr-CAP1.
Note on S8: Put the EXACT Capacitor Name in ALL CAPS after the dash. Example: Gross MVAr-CAP_NAME -> Gross MVAr-CAP1.
Note on T8: Put the EXACT Capacitor Name in ALL CAPS after the dash. Example: Gross MVAr-CAP_NAME -> Gross MVAr-CAP1.
Note on U8: Put the EXACT Reactor Name in ALL CAPS after the dash. Example: Gross MVAr-REACTOR_NAME -> Gross MVAr-R1.
Note on V8: Put the EXACT Reactor Name in ALL CAPS after the dash. Example: Gross MVAr-REACTOR_NAME -> Gross MVAr-R1.
Note on W8: Put the EXACT Dynamic Device Name in ALL CAPS after the dash. Example: Gross MVAr-DYN_DEV_NAME -> Gross MVAr-STATCOM1.
Note on X8: Put the EXACT Dynamic Device Name in ALL CAPS after the dash. Example: Gross MVAr-DYN_DEV_NAME -> Gross MVAr-STATCOM1.
Note on Y6: This section is for Conventional Generation Tests only.
Note on Y8: Type ON for all timestamps that the PSS is in the "ON" status. Make sure it's in all caps.
Note on Z8: Type OFF for all timestamps that the PSS is in the "OFF" status. Make sure it's in all caps.