## Slide 1
Port Lavaca Area Improvement Regional Planning Group Project
Shun Hsien (Fred) Huang
Manager, Regional Planning
Technical Advisory Committee Meeting
ERCOT Public
September 29, 2021

## Slide 2: Overview
American Electric Power (AEPSC) submitted the Port Lavaca Area Improvement project for Regional Planning Group review
  The project was initially submitted as a Tier 2 project that was estimated to cost $97.8 Million
Addresses reliability needs and aging infrastructure in the area

## Slide 3: Overview
Pursuant to Protocol Section 3.11.4.6 (Tier 2)
  ERCOT shall conduct an independent review of a submitted Tier 2 project
Based on ERCOT’s recommended option in the ERCOT independent review, this project is reclassified as Tier 1 project that was estimated to cost $101.5 Million

## Slide 4: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 5: Project Need
In addition to the aging infrastructure identified by AEP, ERCOT’s independent review indicated reliability planning criteria violations
System improvement is needed to meet reliability planning criteria and address aging infrastructure
 | Thermal Overloads | Aging Infrastructure
Total | 4 miles 69-kV | 41 miles 69-kV (built in 1949~1953)

## Slide 6: Comparison of Project Options
ERCOT analyzed six options and short-listed three options
Among the short-listed three options, Option 2EA provides better operational flexibility, supports future system improvement needs, and has less impact to customers under outage conditions.
 | Option 1 | Option 2EA | Option 4EA
Met ERCOT and NERC Reliability Criteria | Yes | Yes | Yes
Improved Operational Flexibility (Planned Maintenance Outages) | Yes | Better | Yes
Require CCN (miles) | 2 | 2 | 2
Voltage conversion from 69-kV to 138-kV | No | Yes | Yes
Capital Cost Estimates | $97.5 M | $101.5 M | $76.4 M

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the Load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 2EA did not cause new or additional congestion
  no potential future generation units were found within the Port Lavaca area load pocket which may impact reliability issue
  the load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation:
Based on the review, ERCOT will recommend the Board endorse Option 2EA to address the reliability and aging infrastructure needs in the Port Lavaca area
AEPSC expects to implement the upgrades related to reliability and aging infrastructure issues by May 2023 and December 2024, respectively
Estimated Capital Cost: $101.5 Million

## Slide 9: ERCOT Recommendation: Option 2EA
Rebuild the existing Brookhollow - Cangrejo (Port Lavaca) 69-kV line using 2000 A conductor, 138-kV capable but continue to operate at 69-kV (2.0 miles)
Rebuild portion of the existing Point Comfort - Carancahua 69-kV line using 2000 A conductor, 138-kV capable but continue to operate at 69-kV (2.0 miles)
Construct a new Cangrejo 138/69-kV substation to replace the existing Port Lavaca 69-kV substation and install a new 138/69-kV transformer
Rebuild a portion (STEC Tap - Cangrejo) of the existing North Carbide - Cangrejo (Port Lavaca) 69-kV line using 2000 A conductor, 138-kV capable but continue to operate at 69-kV (2.2 miles)
Retire the existing North Carbide - STEC Tap 69-kV line (9.6 miles)
Rebuild a portion of the existing North Carbide - Sand Crab 138-kV line to form a double-circuit 138k-kV line (10.3 miles)
Construct a new Beecher 138-kV substation to replace the existing Placedo 69-kV substation
Construct a new Dacosta 138-kV, three breaker ring bus, substation at the intersection of the existing Chocolate Bayou - Gohlke 138-kV line and the existing Cangrejo (Port Lavaca) - Victoria 69-kV line
Loop the existing Chocolate - Gohlke 138-kV line into the new Dacosta 138-kV substation
Rebuild and convert a portion of the existing Cangrejo (Port Lavaca) - Victoria 69-kV line to 138-kV line using 2000 A conductor and terminate at the new Dacosta 138-kV substation (18 miles)
Retire the remaining 69-kV line from Victoria going toward Dacosta (10.7 miles)

## Slide 10: Option 2EA