## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
October 07, 2021

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of July
    2 FMEs in the month of August
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 09/8/2021
  Review of emergency conditions list from ROS
  ERCOT Ancillary Service Methodology (Part2,discussion)
  Loss of Generation Event Analysis – May 9,2021
  ERCOT reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in July
  7/20/2021 8:46:05
    Loss of 801 MW generation
    Interconnection Frequency Response: 1313 MW/0.1 Hz
    56 Resources were evaluated. These includes,
      54 Generation Resources
      2 Controllable Load Resources
      0 Energy Storage Resources
    4 of 54 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 54 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
There were 2 FMEs in August
  8/28/2021 7:07:20
    Loss of 781 MW generation
    Interconnection Frequency Response: 1662 MW/0.1 Hz
    53 Resources were evaluated. These includes,
      51 Generation Resources
      2 Controllable Load Resources
      0 Energy Storage Resources
    8 of 51 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    7 of 51 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Frequency Measurable Events
  8/31/2021 17:40:36
    Loss of 502 MW generation
    Interconnection Frequency Response: 913 MW/0.1 Hz
    82 Resources were evaluated. These includes
      82 Generation Resources
      0 Controllable Load Resources
      0 Energy Storage Resources
    20 of 82 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    18 of 82 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 8: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 471 MW/0.1 Hz
IMFR Performance currently
1212.07 MW/0.1HZ

## Slide 9
Questions?

## Slide 10: Frequency Control Report
August 2021

## Slide 11: CPS1 Performance
Current 12-Month Rolling Average: 169.47%

## Slide 12: RMS1 Performance of ERCOT Frequency

## Slide 13: Frequency Profile Analysis

## Slide 14: Time Error Corrections

## Slide 15: ERCOT Total Energy
Notes: 37,331,144 MWh

## Slide 16: ERCOT Total Energy from Wind Generation
Notes: 6,965,821 MWh

## Slide 17: ERCOT % Energy from Wind Generation
Notes: 18.66%

## Slide 18: ERCOT Total Energy from Solar Generation
Notes: 1,643,972 MWh

## Slide 19: ERCOT % Energy from Solar Generation
Notes: 4.40%