| NOGRR Number | 227 | NOGRR Title | Add Phasor Measurement Recording Equipment Location for Main Power Transformer for Intermittent Renewable Resource (IRR) |
| --- | --- | --- | --- |
| Date of Decision |  | October 7, 2021 |  |
| Action |  | Approved |  |
| Timeline |  | Normal |  |
| Effective Date |  | November 1, 2021 |  |
| Priority and Rank Assigned |  | Not Applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 6.1.3.3, Data Recording and Redundancy Requirements |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) allows for single phase current magnitude/angle data for an interconnected Intermittent Renewable Resource (IRR) over 20 MVA to be taken from either side of the main power transformer where turbines exist on a feeder(s) that were aggregated to two or more IRRs. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Many IRRs aggregate turbines/inverters that exist on the same feeder or feeders to two or more Resources. In this case, it is physically impossible to measure the single phase current magnitude/angle per individual Resource. This NOGRR allows the current magnitude/angle to be measured at a point where the flow from the IRR flows through the same element, such as the main power transformer. |  |
| ROS Decision |  | On 6/3/21, ROS voted unanimously via roll call to table NOGRR227 and refer the issue to the Operations Working Group (OWG). All Market Segments participated in the vote. On 7/8/21, ROS voted unanimously via roll call to recommend approval of NOGRR227 as submitted. All Market Segments participated in the vote. On 8/5/21, ROS voted unanimously via roll call to endorse and forward to TAC the 7/8/21 ROS Report and the Revised Impact Analysis for NOGRR227. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 6/3/21, there was no discussion. On 7/8/21, there was no discussion. On 8/5/21, participants noted the Revised Impact Analysis. |  |
| TAC Decision |  | On 8/27/21, TAC voted unanimously via roll call to recommend approval of NOGRR227 as recommended by ROS in the 8/5/21 ROS Report. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 8/27/21, TAC reviewed the ERCOT Opinion and ERCOT Market Impact Statement for NOGRR227. |  |
| ERCOT Opinion |  | ERCOT supports approval of NOGRR227. |  |
| ERCOT Market Impact Statement |  | ERCOT Staff has reviewed NOGRR227 and believes that NOGRR227 will improve efficiencies for Entities by allowing current magnitude/angle to be taken from either side of the main power transformer where turbines exist on feeders that were aggregated. |  |
| PUCT Decision |  | On 10/7/21, the PUCT approved NOGRR227 and accompanying ERCOT Market Impact Statement as presented in Project No. 52307, Review of Rules Adopted by the Independent Organization in Calendar Year 2021. |  |

| Sponsor |  |
| --- | --- |
| Name | James Teixeira |
| E-mail Address | Jay.Teixeira@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6582 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Guide Language Revision

- 6.1.3.3	Data Recording and Redundancy Requirements

(1)	Recorded electrical quantities shall be sufficient to determine the following:

(a)	For Transmission Facility owner locations meeting paragraphs (1) or (2) of Section 6.1.3.2, Location Requirements:

(i)	Phase-to-neutral voltage magnitude/angle data for each phase from at least two distinct transmission level element measurements;

(ii)	Single phase current magnitude/angle data for each phase from at least two distinct transmission level lines; and

(iii)	Frequency and df/dt data for at least two transmission level element measurements.

(b)	For Generator Resource owner locations meeting Section 6.1.3.2:

(i)	Phase-to-neutral voltage, or phase-to-phase voltage magnitude/angle data for each phase from at least one generator-interconnected bus measurement;

(ii)	Single phase current magnitude/angle data for each phase from each interconnected generator over 20 MVA or on the high or low side of a main power transformer that represents the flow from multiple Intermittent Renewable Resources (IRRs) behind the main power transformer with total aggregated capacity greater than 20 MVA; and

[NOGRR227: Replace item (ii) above with the following upon system implementation of NPRR973:] (ii) Single phase current magnitude/angle data for each phase from each interconnected generator over 20 MVA or on the high or low side of a Main Power Transformer (MPT) that represents the flow from multiple Intermittent Renewable Resources (IRRs) behind the MPT with total aggregated capacity greater than 20 MVA; and

(iii)	Frequency and df/dt data for at least one generator-interconnected bus measurement.