## Slide 1
ERCOT Frequency Control Report
September 2021
ERCOT
Operations Planning
PDCWG | October 13th, 2021

## Slide 2: Summary of September 2021
CPS1: 171.88%
Current CPS1 12-Month Rolling Average: 169.33%
1 BAAL Exceedance(s)
1 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2021 RMS1 Statistics
  Mean: 16.47 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz
Energy Statistics
  Total Energy: 36,556,459 MWh
  Wind Energy: 6,767,688 MWh
  Percent Energy from Wind: 18.51%
  Solar Energy: 1,723,725 MWh
  Percent Energy from Solar: 4.72%
Minimum System Inertia
  Mean: 230,941 MW*s
  Max: 293,036 MW*s on Sep 6th
  Min: 177,795 MW*s on Sep 24th
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Sep-21 CPS1 (%): 171.88
Notes: 1. 85% @ 09/13/2021 HE 17:00
Expected Generation Deviation
Expected gen dev remained negative for the most part of the hour.. The largest expected gen dev was -1645 MW @ 16:30 with contribution from solar and wind.
IRR Ramps
Between 16:21 to 16:26 solar ramped down by 400 MW and wind ramped down by 400 MW. Again between 16:45 and 16:50 solar ramped down by 400 MW.
Regulation: Regulation up was exhausted during these IRR ramp intervals

## Slide 5: BAAL Exceedances & Violations
There is 1 BAAL exceedance(s) in September
Notes: Occurred on 9/12/2021 due to generation loss event

## Slide 6: 15-Minute Average CPS1%
Sep-21 CPS1 (%): 171.88

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 169.33%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 16.47 mHz
  Min: 12.01 mHz
  Max: 60.6 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 36,556,459 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,767,688 MWh

## Slide 23: % Energy from Wind Generation
Notes: 18.51%

## Slide 24: Total Energy From Solar Generation
Notes: 1,723,725 MWh

## Slide 25: % Energy from Solar Generation
Notes: 4.72%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 177,795 MW*s on 9/24/2021
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 230,941 MW*s
Max: 293,036 MW*s on Sep 6th
Min: 177,795 MW*s on Sep 24th

## Slide 28: Questions?
Thank you!