## Slide 1: PLWG Extreme Case Group
PLWG Meeting 10/15/2021

## Slide 2: Extreme Winter Case
Early morning
February 15, 2021 Weather Assumptions (99/1 Winter)
  Uses a forecast developed by ERCOT or developed by the TDSPs
  TSPs would develop the appropriate distribution of the load forecast
Load would be not scaled down to match generation
Solar generation at 0%
Wind generation at 10%
Storage at 0%
Disable reactive capability for IRR units below 10% output
  Currently, no market exists for reactive services
All Ancillary Service generation and load are assumed dispatched
DC Ties are assumed to have no imports and no exports
GTCs are not violated
One study would be a G1N1 or GXN1 analysis, where the GX is a group of generation facilities in the same physical area or with a common failure mode (e.g., gas pipeline)
Another study would be systemwide natural gas fired deration of XX% to be reflective of natural gas system not pressurized appropriately
Demand response (voluntary and involuntary) may be needed
  Reduce large Industrial loads as necessary
  If still insufficient to solve the case, reduce other loads on their system
  Involuntary demand response can also be described as energy shortages
  Involuntary demand response would be allocated based on the ERCOT method

## Slide 3: Extreme Heat and Drought Summer Case
Early evening
August 2, 2011 Weather Assumptions (99/1 Summer)
  Uses a forecast developed by ERCOT or developed by the TDSPs
  TSPs would develop the appropriate distribution of the load forecast
Load would be not scaled down to match generation
Solar generation at 80%
Wind generation at 10%
Storage at 0%
Disable reactive capability for IRR units below 10% output
  Currently, no market exists for reactive services
All Ancillary Service generation and load are assumed dispatched
DC Ties are assumed to have full imports and no exports
GTCs are not violated
G1N1 or GXN1 analysis, where the GX is a group of generation facilities with low water risks (both natural gas and coal)
Demand response (voluntary and involuntary) may be needed
  Reduce large Industrial loads as necessary
  If still insufficient to solve the case, reduce other loads on their system
  Involuntary demand response can also be described as energy shortages
  Involuntary demand response would be allocated based on the ERCOT method

## Slide 4: Hurricanes/Tropical Storms/Tornadoes
Summer loads
  Both 90/10 and 99/1 weather assumptions
  Uses forecasts developed by ERCOT or developed by the TDSPs
  TSPs would develop the appropriate distribution of the load forecast
Load would be not scaled down to match generation
Solar generation at 80%
Wind generation at 50%
Storage at 0%
Disable reactive capability for IRR units below 10% output
  Currently, no market exists for reactive services
All Ancillary Service generation and load are assumed dispatched
DC Ties are assumed to have only imports and exports that helps the situation
GTCs are not violated
First study would be a G1N1 or GXN1 analysis, where the GX is a group of generation facilities within same physical area i.e. by county or study area like Houston, DFW, Valley or Corpus Christi area generators and N-X analysis removing multiple major transmission lines from service within a specific area (e.g., two 345-kV circuits into the Valley out).
Second study would be a G1N1 or GXN1 analysis, where the GX is a group of generation facilities in the same physical area (same as above) with the addition of a percentage (all or X%) of load being removed in those areas as well and N-X analysis removing multiple major transmission lines from service within a specific area (e.g., two 345-kV circuits into the Valley out).
Demand response (voluntary and involuntary) may be needed
  Reduce large Industrial loads as necessary
  If still insufficient to solve the case, reduce other loads on their system
  Involuntary demand response can also be described as energy shortages
  Involuntary demand response would be allocated based on the ERCOT method

## Slide 5: Next Steps
Definitions of Extreme Event Contingencies TPL 001 –would need more input from other entities (e.g. TERC)
Either ERCOT or a working group will establish development and maintenance of these contingencies such as:
  Derate of thermal units resulting from gas curtailments. Would be across many units.
  Loss of multiple generators resulting from single point of failure in the gas supply system.
Establish a frequency for review of extreme event scenarios case development
  An initial frequency to consider is once per year as the resource mix and load forecasts are changing rapidly.

## Slide 6: What will be done with the information
At ROS, a stakeholder made a comment about what will be done with the findings
One idea is to review the criteria that ERCOT uses to recommend developing system improvements following contingency events that would allow for load shed.
Does ERCOT have a criteria on cascading that has relevance?
Is this criteria adequate to “fix” the problem?

## Slide 7: Appendix

## Slide 8: Members
John Bernecker (ERCOT)
Doug Evans (STEC)
Andrew Hamann (LCRA)
Kevin Hanson (National Grid)
Brian Hithersay (BEPC)
Harsh Naik (Oncor)
Lori Simpson (Exelon)
Mina Turner (AEP)
Monica Walker (GM)