| NPRR Number | 1098 | NPRR Title | Direct Current Tie (DC Tie) Reactive Power Capability Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | October 14, 2021 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 3.15.1, ERCOT Responsibilities Related to Voltage Support 3.15.4, Direct Current Tie Responsibilities Related to Voltage Support (new) 6.5.6, TSP and DSP Responsibilities |  |
| Related Documents Requiring Revision/Related Revision Requests |  | Nodal Operating Guide Revision Request (NOGRR) 234, Related to NPRR1098, DC Tie Reactive Power Capability Requirements Planning Guide Revision Request (PGRR) 097, Related to NPRR1098, DC Tie Reactive Power Capability Requirements |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) establishes Reactive Power capability requirements for new Direct Current Ties (DC Ties) interconnecting to the ERCOT System and existing DC Ties replaced after January 1, 2021. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NPRR is proposed in accordance with the May 23, 2017 order of the Public Utility Commission of Texas (PUCT) in Project No. 46304, Oversight Proceeding Regarding ERCOT Matters Arising Out of PUC Docket No. 45624 Relating to DC Tie Project Proposed by Southern Cross Transmission, LLC, which requires ERCOT to address a number of issues as a condition for the energization of the DC Tie project proposed by Southern Cross Transmission, LLC. Directive 8 in the order requires, in part, that ERCOT “determine whether Southern Cross Transmission or any other entity scheduling flows across the Southern Cross DC Tie should be required to provide or procure voltage support service…” This directive essentially requires a determination as to whether Southern Cross Transmission, LLC should be required to provide some quantity of Reactive Power capability to facilitate imports and exports over that DC Tie. ERCOT also considered this question in context of policy for other potential new DC Ties. ERCOT and stakeholders on the Technical Advisory Committee (TAC) determined that new DC Ties should be required to provide a defined measure of Reactive Power capability similar to that required of Generation Resources and Energy Storage Resources (ESRs). These Resources are required to provide leading/lagging Reactive Power capability at a 0.95 power factor in accordance with Protocol Section 3.15, Voltage Support, to help meet the Reactive Power needs resulting from their MW Injections and MW Withdrawals. Similarly, imports and exports over DC Ties require reactive support. Accordingly, ERCOT developed the following proposal, which was endorsed by TAC on January 27, 2021 and serves as basis for this NPRR: Any DC Tie facility that has an initial energization date after January 1, 2021, and any DC Tie facility that is replaced after that date, shall have at least 0.95 power factor leading/lagging reactive power capability. This NPRR implements ERCOT’s TAC-approved proposal. Consistent with that position, this NRPR does not require existing DC Tie Facilities to provide Reactive Power capability in the absence of any other significant changes at those Facilities. This is because the existing DC Ties interconnected to the ERCOT System are all owned by Transmission Service Providers (TSPs), which have already installed separate reactive capability to meet their obligations related to voltage support under the Protocols, Operating Guides, and North American Electric Reliability Corporation (NERC) Reliability Standards. Requiring these TSPs to install additional capability to meet the standard proposed in this NPRR would be superfluous and unnecessarily costly. |  |
| Credit Work Group Review |  | To be determined |  |
| PRS Decision |  | On 10/14/21, PRS voted via roll call to recommend approval of NPRR1098 as submitted. There were three abstentions from the Consumer (Occidental), and Independent Retail Electric Provider (IREP) (2) (Reliant, Just Energy) Market Segments. All Market Segments participated in the vote. |  |
| Summary of PRS Discussion |  | On 10/14/21, participants discussed potential impacts to the review and approval timeline should NPRR1098 be tabled, and that the related NOGRR and PGRR are being discussed at ROS working groups ahead of the comment period for ROS. Participants noted that Urgent status might be requested for the related NOGRR and PGRR so that the three items may be considered together by the ERCOT Board. |  |

| Sponsor |  |
| --- | --- |
| Name | John Bernecker |
| E-mail Address | John.Bernecker@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4274 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Protocol Language Revision

# 2.1	DEFINITIONS

Point of Interconnection (POI)

The voltage level and substation where a Generation Entity’s interconnection Facilities connect to the Transmission Facilities as reflected in the Standard Generation Interconnection Agreement (SGIA) between a Generation Entity and a Transmission Service Provider (TSP) or the voltage level and substation where Load interconnects to the TSP Facilities.

[NPRR1005: Replace the above definition “Point of Interconnection (POI)” with the following upon system implementation:] - Point of Interconnection (POI) Any physical location where a Generation Entity’s Facilities or any Direct Current Tie (DC Tie) Facilities electrically connect to a Transmission Service Provider’s (TSP’s) Facilities.

[NPRR1005: Insert the following definition “Point of Interconnection Bus (POIB)” upon system implementation:] Point of Interconnection Bus (POIB) For a Generation Resource or Direct Current Tie (DC Tie) connecting to the ERCOT Transmission System through a Transmission Service Provider (TSP) substation, the Electrical Bus at that TSP substation that is electrically closest to the Generation Resource’s or DC Tie’s Point of Interconnection (POI), or any electrically equivalent Electrical Bus in that substation. For a Generation Resource connecting to the ERCOT Transmission System through a non-TSP substation, the Electrical Bus at that non-TSP substation that is electrically closest to the Generation Resource’s POI, or any electrically equivalent Electrical Bus in that substation.

## 3.15.1	ERCOT Responsibilities Related to Voltage Support

(1)	ERCOT, in coordination with the TSPs, shall establish, and update as necessary, Voltage Profiles at POI of Generation Resources required to provide VSS to maintain system voltages within established limits.

[NPRR989: Replace paragraph (1) above with the following upon system implementation:] (1) ERCOT, in coordination with the TSPs, shall establish, and update as necessary, Voltage Profiles at POI of Generation Resources and ESRs required to provide VSS to maintain system voltages within established limits.

(2)	ERCOT shall communicate to the Qualified Scheduling Entity (QSE) and TSPs the desired voltage at the point of generation interconnection by providing Voltage Profiles.

[NPRR989: Replace paragraph (2) above with the following upon system implementation:] (2) ERCOT shall communicate to the Qualified Scheduling Entity (QSE) and TSPs the desired voltage at the POI by providing Voltage Profiles.

(3)	ERCOT, in coordination with TSPs, shall deploy static Reactive Power Resources as required to continuously maintain dynamic reactive reserves from QSEs and DCTOs, both leading and lagging, adequate to meet ERCOT System requirements.

(4)	For any Market Participant’s failure to meet the Reactive Power voltage control requirements of these Protocols, ERCOT shall notify the Market Participant in writing of such failure and, upon a request from the Market Participant, explain whether and why the failure must be corrected.

(5)	ERCOT shall notify all affected TSPs of any alternative requirements it approves.

(6)	Annually, ERCOT shall review Distribution Service Provider (DSP) power factors using the actual summer Load and power factor information included in the annual Load data request to assess whether DSPs comply with the requirements of this subsection.  At times selected by ERCOT, ERCOT shall require manual power factor measurement at substations and POIs that do not have power factor metering.  ERCOT shall try to provide DSPs sufficient notice to perform the manual measurements.  ERCOT may not request more than four measurements per calendar year for each DSP substation or POI where power factor measurements are not available.

(7)	If actual conditions indicate probable non-compliance of TSPs and DSPs with the requirements to provide voltage support, ERCOT shall require power factor measurements at the time of its choice while providing sufficient notice to perform the measurements.

(8)	ERCOT shall investigate claims of TSP and DSP alleged non-compliance with Voltage Support requirements. The ERCOT investigator shall advise ERCOT and TSP planning and operating staffs of the results of such investigations.

## 3.15.4	Direct Current Tie Operator (DCTO) Responsibilities Related to Voltage Support

(1)	The following Direct Current Ties (DC Ties) are subject to the Reactive Power capability requirements specified in these Protocols and the ERCOT Operating Guides:

(a) 	Any DC Tie with an initial energization date after January 1, 2021.

(b)	Any DC Tie that is modified by increasing the physical capacity of the DC Tie by 20 MW or more or by changing the power converter associated with the DC Tie, unless the replacement is in-kind.

(2)	A Direct Current Tie Operator (DCTO) operating a DC Tie meeting the applicability requirements of paragraph (1) above shall ensure that the DC Tie Facility has the following Reactive Power capabilities:

(a)	An over-excited (lagging or producing) power factor capability of 0.95 or less determined at the DC Tie’s physical capacity at any voltage from 0.95 per unit to 1.04 per unit, as measured at the Point of Interconnection Bus (POIB);

(b)	An under-excited (leading or absorbing) power factor capability of 0.95 or less determined at the DC Tie’s physical capacity at any voltage from 1.0 per unit to 1.05 per unit, as measured at the POIB;

(c)	Reactive Power capability shall be available at all MW levels, whether injecting or withdrawing power, and may be met through a combination of the DC Tie’s dynamic leading and lagging operating capability and/or dynamic VAr-capable devices.

(3)	Any DCTO operating a DC Tie meeting the applicability requirements of paragraph (1) above must conduct an engineering study demonstrating the ability of the DC Tie Facility to meet the Reactive Power requirements in paragraph (2) above.  Any study results must be accepted by ERCOT prior to the initial energization date of the DC Tie.

(4)	ERCOT may, with notice, require performance testing to demonstrate a DC Tie Facility’s ability to meet the Reactive Power requirements in paragraph (2) above.

(5)	A DCTO operating a DC Tie meeting the applicability requirements of paragraph (1) above or the owner of that DC Tie may enter into an agreement with a TSP in which the DCTO or DC Tie owner compensates the TSP to provide Reactive Power capability to meet the Reactive Power requirements of paragraph (2) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (2).

(6)	Each DCTO operating a DC Tie meeting the applicability requirements of paragraph (1) above shall comply with any instruction from its designated Transmission Operator (TO) with respect to the DC Tie’s reactive power capability, including any instruction to maintain a specific voltage at the POIB, subject to the DC Tie’s operating characteristic limits and voltage limits, and within the tolerances identified in paragraph (2) of Nodal Operating Guide Section 2.7.3.6, DCTO Responsibilities and DC Tie Requirements, and subject to any superseding Dispatch Instruction from ERCOT.

(7)	Each DCTO shall use a single control system to control all devices at a DC Tie Facility needed to meet the Reactive Power requirements in paragraph (2) above.  The control system shall be operated in automatic voltage control mode unless ERCOT directs the DCTO to operate the system in manual mode.

6.5.6	TSP, DCTO, and DSP Responsibilities

(1)	Each TSP shall notify ERCOT of any changes in status of Transmission Elements as provided in these Protocols and clarified in the ERCOT procedures.

(2)	Each TSP shall as soon as practicable report to ERCOT any short-term inability to meet minimum TSP reactive requirements.

(3)	Each DSP shall as soon as practicable report to ERCOT any short-term inability to meet minimum DSP reactive requirements.

(4)	Each DCTO shall immediately report to ERCOT and its designated TO any inability of any DC Tie Facility it operates to meet the Reactive Power capability requirements in these Protocols.