## ImprovementCostSummary02252015
| Project Cost |  |  |  |  | XFMR MVA
| 345 | 138 | 69 | Total |  | 345 | 138 | 69 | Total
2014 | 220788971 | 498044759 | 150528335 | 869362065 | 2014 | 2972 | 1172 | 0 | 4144 | For ROS and BOD Reports
2015 | 321196422 | 794175942 | 205714889 | 1321087253 | 2015 | 5622 | 1505 | 280 | 7407 | ·All Projects (in engineering, routing, licensing and construction): |  |  |  | 6150842887
2016 | 841927000 | 825897634 | 257336500 | 1925161134 | 2016 | 7272 | 1090 | 0 | 8362 | ·Transmission Projects Energized in 2015: |  |  |  | 32834000
2017 | 124446200 | 645486901 | 133558000 | 903491101 | 2017 | 6782 | 510 | 330 | 7622
2018 | 543660000 | 371609971 | 132476000 | 1047745971 | 2018 | 1200 | 390 | 0 | 1590
2019 | 78190000 | 215375031 | 44100000 | 337665031 | 2019 | 0 | 195 | 0 | 195
2020 | 12187250 | 53201000 | 13800000 | 79188250 | 2020 | 700 | 0 | 0 | 700
2021+ | 218736044 | 256522160 | 94079943 | 569338147 | 2021+ | 3600 | 970 | 0 | 4570
2015COM | 10000 | 32074000 | 750000 | 32834000 | 2015COM | 0 | 0 | 0 | 0
2015PLAN | 321186422 | 762101942 | 204964889 | 1288253253 | 2015PLAN | 5622 | 1505 | 280 | 7407
2014-2021+ | 2361131887 | 3660313398 | 1031593667 | 7053038952 | 2014-2021+ | 28148 | 5832 | 610 | 34590
2014-2015 | 541985393 | 1292220701 | 356243224 | 2190449318 | 2014-2015 | 8594 | 2677 | 280 | 11551
2016-2021+ | 1819146494 | 2368092697 | 675350443 | 4862589634 | 2016-2021+ | 19554 | 3155 | 330 | 23039
| Circuit Miles New |  |  |  | Circuit Miles Rebuilt, Reconductored or Upgraded |  |  |  |  | Total
| 345 | 138 | 69 | Total |  | 345 | 138 | 69 | Total | 345 | 138 | 69 | Total
2014 | 7.3 | 132.32 | 0.52 | 140.14 | 2014 | 46 | 408.67 | 159.9 | 614.57 | 53.3 | 540.99 | 160.42 | 754.71
2015 | 44.3 | 255.2 | 2.8 | 302.3 | 2015 | 197.89 | 708.14 | 165.14 | 1071.17 | 242.19 | 963.34 | 167.94 | 1373.47
2016 | 333.038 | 245.6 | 37.75 | 616.388 | 2016 | 63.7 | 495.16 | 291.23 | 850.09 | 396.738 | 740.76 | 328.98 | 1466.478
2017 | 0 | 125.91 | 0 | 125.91 | 2017 | 64.4 | 625.61 | 148.1 | 838.11 | 64.4 | 751.52 | 148.1 | 964.02
2018 | 133 | 43.55 | 0 | 176.55 | 2018 | 92 | 242.76 | 191.16 | 525.92 | 225 | 286.31 | 191.16 | 702.47
2019 | 18 | 80.7 | 33.11 | 131.81 | 2019 | 93.4 | 79.79 | 11.11 | 184.3 | 111.4 | 160.49 | 44.22 | 316.11
2020 | 4 | 8.01 | 0 | 12.01 | 2020 | 67.96 | 26.6 | 5.13 | 99.69 | 71.96 | 34.61 | 5.13 | 111.7
2021+ | 125.8 | 60.2 | 9 | 195 | 2021+ | 136.2 | 163.1 | 115.48 | 414.78 | 262 | 223.3 | 124.48 | 609.78
2015COM | 0 | 6.8 | 0 | 6.8 | 2015COM | 25.4 | 78.8 | 9.4 | 113.6 | 25.4 | 85.6 | 9.4 | 120.4
2015PLAN | 44.3 | 248.4 | 2.8 | 295.5 | 2015PLAN | 172.49 | 629.34 | 155.74 | 957.57 | 216.79 | 877.74 | 158.54 | 1253.07
2014-2021+ | 665.438 | 951.49 | 83.18 | 1700.108 | 2014-2021+ | 761.55 | 2749.83 | 1087.25 | 4598.63 | 1426.988 | 3701.32 | 1170.43 | 6298.738
2014-2015 | 51.6 | 387.52 | 3.32 | 442.44 | 2014-2015 | 243.89 | 1116.81 | 325.04 | 1685.74
2016-2021+ | 613.838 | 563.97 | 79.86 | 1257.668 | 2016-2021+ | 517.66 | 1633.02 | 762.21 | 2912.89

## FutureTPIT020115NoCost
FEBRUARY BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 2/1/2015
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
4005 | Salem Substation Upgrade | Install a 345/138/13.2-kV, 672 MVA autotransformer at Salem Substation. |  | Salem |  | Under Construction |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013110 | 2015-02-02 |  | 345 | 0 | 0 | 672 |  | Washington |  | Tier 4 |  |  |  | 7058, 7289 | Y | N |  | The new 672 MVA autotransformer will be energized from the Salem 345-kV bus and circuit breakers will remain open on the 138-kV side. | 4350 | 4005
4088 | McNeil-Dessau: Upgrade Ckt 904 | Reconductor last Mcneil span off MC-DE Ckt 904 to 3000 amps |  | McNeil | Dessau | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2015-02-09 |  | 138 | 0 | 3.8 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9079, 9193 | Y |  |  |  | 4438 | 4088
09TPIT0117 | Stryker Creek - Dialville 138 kV line | Upgrade existing 138 kV line |  | Stryker Creek | Dialville | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R664-E | 2015-02-15 |  | 138 | 0 | 15.2 | 0 |  | Cherokee | Cherokee | Tier 4 |  |  |  | 3110, 3111, 3160 | Y | N |  |  | 1244 | 1241
3905 | McNeil-Decker Plant: Upgrade Ckt 1013 | Reconductor to 3000 amps as part of DP-MC Corridor Upgrade |  | McNeil | Decker Plant | Under Construction |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2015-02-15 |  | 138 | 0 | 9.56 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9076, 9188 | Y |  |  |  | 4201 | 3905
3985 | Dessau-Sprinkle: Upgrade Ckt 906 | Reconductor to 3000 amps as part of DP-MC Corridor Upgrade |  | Dessau | Sprinkle | Under Construction |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2015-02-15 |  | 138 | 0 | 1.58 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9193, 9271 | Y |  |  |  | 4310 | 3985
15TPIT0025A | Monticello SES - Monticello Tap 138 kV line | Reconductor existing Monticello Tap - Monticello Mining line section |  | Monticello Mining | Monticello Tap | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R906-E | 2015-02-15 |  | 138 | 0 | 14.7 | 0 |  | Titus | Franklin | Tier 4 |  |  |  | 1791, 1794 | Y | N |  |  | 4520 | 2643
14TPIT0059B | Bevo Station and Autotransformer | 138 kV and autotransformer by December 2014. |  | BEVO |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-02-20 |  | 138 | 0 | 0 | 150 |  | Dimmit |  | Tier 1 | 2012-04-01 | 2012-08-01 | 2012-09-01 | 5871, 78280 | Y | N |  |  | 3440 | 3264
15TPIT0059 | Avery Ranch - Jollyville Transmission Line Upgrade | Upgrade the 1.1 mile Avery Ranch (7534) - Jollyville (9223) 138-kV transmission line to bundled 959.6 ACSS/TW Suwanee, 660MVA. |  | Avery Ranch | Jollyville | Under Construction |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013396 | 2015-02-23 |  | 138 | 0 | 1.1 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 7534, 9223 | Y | N |  |  | 3404 | 3231
14TPIT0031B | Project to add new Auto #2 and moving existing #3 to new pos | Install new autotransformer on bus 5055 |  |  |  | Planned | T-0176 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0588 | 2015-02-26 |  | 345 | 0 | 0 | 600 |  | Bexar | Bexar | Tier 4 |  |  |  | 5058, 5056, 5055 | Y | N |  |  | 2862 | 2736
14TPIT0003 | Ranchtown - New 138 kV Substation | Loop new 138kV substation into the existing 138kV Helotes to Menger Creek line |  | Ranchtown | Helotes-Menger Creek | Planned | T-0175 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0567 | 2015-02-27 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5358, 5200, 7665 | Y | N |  | There are no transformers associated with this project. There is no transmission line additions associated with this project | 958 | 957
12TPIT0081 | 36th St - New 138kV Substation | Loop new 138kV substation into existing 138kV Merida to Medina Base line and replace exiting Kelly Field #3 138kV substation | Delayed due to Budget Constraints | Merida | Medina Base | Planned | T-0161 | CPS | Hector Torres HVTorres@cpsenergy.com 210-353-2404 | S-0578 | 2015-02-28 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5245, 5305, 5310, 5427 | Y | N |  | There are no transformers associated with this project | 952 | 951
15TPIT0035F | Velasco to West Columbia Upgrades and Conversion to 138kV | Retire Velasco 138/69 kV Auto |  | Velasco |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-02-28 |  | 69 | 0 | 0 | -100 |  | Brazoria |  | Tier 3 | 2012-06-14 | 2012-07-24 |  | 49032, 43360, 43370 | Y | N |  | Cost included in project 15TPIT0035A. | 4291 | 2388
15TPIT0013 |  | Rebuild Lake Kemp Switch to Seymour with 1033 acsr conductor |  | Seymour | Lake Kemp | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 10047 | 2015-03-01 |  | 69 | 0 | 6.9 | 0 |  |  |  | Tier 4 |  |  |  | 779, 782 | Y |  |  |  | 4136 | 3852
4399 | Crestonio to Lobo SS: Raise four 138 kV structures | Increase the MOT rating of the Lobo SS to Falfurrias 138kV line by raising 49 structures |  | Crestonio | Lobo SS | Planned | 702 - 0872 | AEP TCC | Mike Tallon 918-599-2664 | 3549 | 2015-03-01 |  | 138 | 0 | 32.1 | 0 |  | Duval | Webb | Tier 4 |  |  |  | 8297, 80221, 8695, 80439 | Y | N |  |  | 4778 | 4399
15TPIT3405 | New SECO station with load and line | Adds a new 138 kV line to a new load serving substation SECO |  | SECO | Razorback | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-03-02 |  | 138 | 9.2 | 0 | 0 |  | Medina | Medina | Tier 4 |  |  |  | 5806, 80241 | Y | N |  |  | 3605 | 3405
12TPIT0062B | Butler Road - New Substation | Low side (12.47 kV) energization and load addition. |  |  |  | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE04512 | 2015-03-06 |  | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38930 | Y |  |  |  | 4512 | 1191
14TPIT0032 | Downing to Mountary | Existing 69 kV line. |  | Downing | Mountary | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 10044 | 2015-03-15 |  | 69 | 0 | 15 | 0 |  | Comanche | Comanche | Tier 4 |  |  |  | 281, 294 | Y | N | 2009-R29 |  | 1065 | 1064
15TPIT0007 | Green Mountain to Stonegate - 138kV 2nd Circuit | Build second 138kV transmission line from Green Mountain to Stonegate on existing transmission structures |  | Green Mountain | Stonegate | Planned | S-0608 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0179 | 2015-03-16 |  | 138 | 11.5 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5093, 5180, 5415 | Y | N |  | There are no transformers associated with this project | 970 | 969
15TPIT0062 | McNeil - Marshall Ford Transmission Line Upgrade | Upgrade and convert the 14.5 mile McNeil (7334) - Marshall Ford (7356) 69-kV transmission line to 138-kV bundled 795 ACSR, 440 MVA. |  | McNeil | Marshall Ford | Under Construction |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013494 | 2015-03-31 |  | 138 | 0 | 14.5 | 0 |  | Travis | Travis | Tier 3 | 2013-03-01 | 2013-03-30 |  | 7334, 7356 | Y | N |  |  | 3407 | 3234
3355 | Razorback: Build 138 kV Temp Tap | Construct new Razorback station along the Uvalde to Castroville (STEC) 138 kV line |  | Uvalde |  | Under Construction | 611 - 0779 | ETT | Brent Harris 918-599-2664 | 3550 | 2015-03-31 |  | 138 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 80241, 5083, 8234 | Y |  |  |  | 3544 | 3355
3040A | WA Parish to Fort Bend Ckt.09 | Upgrade 138kV Ckt.09 Fort Bend to Reading to increase thermal ratings. | Delay in Project Schedule | Fort Bend | Reading | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-03-31 |  | 138 | 0 | 2.6 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44280, 44570 | Y | N |  |  | 4577 | 3040
4609 | Flewellen Ckt.09 & 25 Swaps | Swap circuit positions at Flewellen substation for circuits 09 & 25. |  | Flewellen | Brazos Valley/Mason Road | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 937 | 2015-03-31 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44231, 44100, 44230, 44280, 44450 | Y | N |  |  | 5016 | 4609
4178 | Holt Switching Station Additions | Install 138 kV circuit breaker to create a POI |  | Holt |  | Planned |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8227 | 2015-04-15 |  | 138 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  | 1141 | Y | N |  |  | 4531 | 4178
4279 | Mercers Gap 138 kV Switching Station | Construct new switching station |  | Mercers Gap |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R799 | 2015-04-15 |  | 138 | 0 | 0 | 0 |  | Comanche |  | Tier 4 |  |  |  | 1653, 1441, 1654 | Y | N |  |  | 4654 | 4279
15TPIT0061 | Marshall Ford to Lago Vista Transmission Line Upgrade | Upgrade the 6.5 mile Marshall Ford (7356) - Lago Vista (7352) 138-kV transmission line to bundled 795 ACSR, 440 MVA. |  | Marshall Ford | Lago Vista | Under Construction |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013487 | 2015-04-20 |  | 138 | 0 | 6.5 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 7352, 7356 | Y | N |  |  | 3406 | 3233
14TPIT0063 | Munday to BEC Munday: Rebuild 69 kV line | Rebuild Munday to BEC Munday 69 kV line with 959.6 ACSR | Transmission Status Update | Munday | BEC Munday | Under Construction | 568 - 0742 | AEP TNC | Aaron Schwerman 918-599-2664 | 2572 | 2015-04-30 |  | 69 | 0 | 2.4 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 764, 6107 | Y | N |  |  | 1847 | 1804
14TPIT0119 | Mason Road to Obrien Ckt25 | Upgrade substation equipment at Mason Road and Obrien to increase Ckt.25 thermal ratings. | Delay in Project Schedule | Mason Road | Obrien | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-04-30 |  | 138 | 0 | 0 | 0 |  | Harris | Fort Bend | Tier 4 |  |  |  | 44450, 44510 | Y | N |  |  | 3049 | 2875
14TPIT0127 | Purgatory Road Substation Addition | Construct the new Purgatory Road Substation (7489) on the PEC Sattler (7488) - Hunter (7491) 138-kV transmission line |  | Sattler | Hunter | Under Construction |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2015-04-30 |  | 138 | 0 | 0 | 0 |  | Comal |  | Tier 4 |  |  |  | 7489, 7488, 7491 | Y | N |  |  | 3205 | 3036
15TPIT0042 | FM 237 Yorktown Substation | Replace T1, 138kV-26.18 kV, 30 MVA PWT w/associated bus, structures, panels, etc. |  | FM 237 |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2015-04-30 |  | 138 | 0 | 0 | 0 |  | DeWitt |  | Tier 4 |  |  |  | 78191 | Y | N |  |  | 3501 | 3320
4500 | Humble to King Ckt94 | Upgrade Equipment at Humble substation |  | Humble | King | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-04-30 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 40830, 40911 | Y |  |  |  | 4897 | 4500
13TPIT0128 | Danevang Switch to Danevang Substaton Rebuild | Rebuild 4-0 ACSR 69 kV to 138 capable 795 ACSR. |  | Danevang Switch | Danevang Substation | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-05-01 |  | 69 | 0 | 2.2 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  | 5544, 5548 | Y | N |  |  | 1578 | 1548
13TPIT0171 | Farmersville West - New Substation | Build a new 138-12.47 kV substation to accommodate load growth in Farmersville. Cut Oncor's Princeton - Royce City 138 kV line into the new substation. |  |  |  | Planned | 16TPIT0005 | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07214 | 2015-05-01 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 37291, 12527 | Y | N |  |  | 2062 | 2010
14TPIT0078 | Advance Capacitor Bank | Install 15 MVAR at Advance substation |  | Advance | Advance | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12011 | 2015-05-01 |  | 69 | 0 | 0 | 0 | 0,15 | Parker |  | Tier 4 |  |  |  | 518 | Y | N |  |  | 2309 | 2236
3968 | Ferguson - Sandy Creek - Pitsburg Transmission Line Upgrade | Increase ground clearance of Ferguson (7126) to Sandy Creek (7127) (approx 9 miles) and Sandy Creek to Pitsburg (7120) (approx 18.9 miles) transmission lines to obtain 221 MVA rating. |  | Ferguson | Sandy Creek - Pitsburg | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014206 | 2015-05-11 |  | 138 | 0 | 27.9 | 0 |  | Llano | Llano | Tier 4 |  |  |  | 7120, 7126, 7127 | Y | N |  |  | 4289 | 3968
4436 | Wynn Joyce Phase2 Upgrade Project | Upgrade Wynn Joyce to a 138kV ring substation with 3 lines out to Miller, Rosehill, and Ben Davis substations |  | Wynn Joyce | Miller, Rosehill, Ben Davis | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2015-05-13 |  | 138 | 0 | 11.5 | 0 |  | Dallas | Dallas |  |  |  |  | 813, 817, 824, 968 | Y | N |  |  | 4822 | 4436
14TPIT0016 | East Mesquite - Prairie Creek 138 kV line | Upgrade existing line |  | East Mesquite | Prairie Creek | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4069-E | 2015-05-15 |  | 138 | 0 | 2.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2441, 2754, 2756, 2759 | Y | N | 2009-R19 |  | 1825 | 1783
13TPIT0060 | Cedar Hill Switch - Mountain Creek 138 kV line | Upgrade existing line |  | Cedar Hill Switch | Mountain Creek | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4068-E | 2015-05-15 |  | 138 | 0 | 11.4 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2411, 2412, 2421, 2422 | Y | N |  |  | 2593 | 2488
15TPIT0079 | Roanoke Switch - Coppell Switch 138 kV Line Phase 2 | Rebuild existing double-circuit Southlake - Grapevine Junction line section |  | Southlake | Grapevine Junction | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5001C-E | 2015-05-15 |  | 138 | 0 | 7.7 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2014, 2019, 2020, 2023 | Y | N |  |  | 2690 | 2574
16TPIT0033 | Mason - Screwbean 138 kV Line | Rebuild existing 138 kV line |  | Screwbean | Mason | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8173-E | 2015-05-15 |  | 138 | 0 | 15 | 0 |  | Reeves | Culberson | Tier 4 |  |  |  | 1083, 1084, 1094, 1095 | Y | N |  |  | 3010 | 2837
11TPIT0097 | Norwood Switch 345/138 kV autotransformer | Replace #1 345/138 kV autotransformer |  | Norwood Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4070-E | 2015-05-15 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 4 |  |  |  | 2410, 2404, 12404 | Y | N |  |  | 3233 | 3064
15TPIT0072 | Eddy 69 kV capacitors | Install shunt capacitors |  | Eddy |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R769-E | 2015-05-15 |  | 69 | 0 | 0 | 0 | 0,27.6 | McLennan |  | Tier 4 |  |  |  | 3580 | Y | N |  |  | 3252 | 3083
15TPIT0095 | Tyler Northwest 138/69 kV autotransformer | Replace existing autotransformer |  | Tyler Northwest |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6020 | 2015-05-15 |  | 138 | 0 | 0 | 100 |  | Smith | Smith | Tier 4 |  |  |  | 3141, 3142, 3157 | Y | N |  |  | 3254 | 3085
15TPIT0076 | North Andrews - Means 69 kV line section | Rebuild existing North Andrews - Means 69 kV line section as a double-circuit line with a 69 kV circuit and a 138 kV circuit |  | North Andrews | Means | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8142-E | 2015-05-15 |  | 69 | 2.8 | 2.8 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1160, 1285 | Y | N |  |  | 3328 | 3157
15TPIT0080 | Big Springs Switch - Big Springs West 138 kV Line | Upgrade existing line |  | Big Springs Switch | Big Springs W | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8139-E | 2015-05-15 |  | 138 | 0 | 7.9 | 0 |  | Howard | Howard | Tier 4 |  |  |  | 1322, 1324 | Y | N |  |  | 3332 | 3161
15TPIT0088 | North Andrews #1 and #2 138/69 kV autotransformers | Replace existing autotransformers. This project now includes TPIT project 17TPIT0016. |  | North Andrews |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8149-E | 2015-05-15 |  | 138 | 0 | 0 | 300 |  | Andrews |  | Tier 4 |  |  |  | 1159, 1160 | Y | N |  |  | 3336 | 3165
15TPIT0091 | Midland Airport - Glenhaven 138 kV Line | Upgrade existing line |  | Odessa EHV | Midessa | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8137-E | 2015-05-15 |  | 138 | 0 | 5.5 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1118, 1120, 1121 | Y | N |  |  | 3338 | 3167
15TPIT0092 | Odessa North - Westover 138 kV Line | Upgrade existing line |  | Odessa North | Westover | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8182-E | 2015-05-15 |  | 138 | 0 | 4.9 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1122, 1129, 1130 | Y | N |  |  | 3341 | 3170
15TPIT0085 | Eagle Mountain - Saginaw 138 kV Line (Eagle Mtn - Wag Rob) | Upgrade existing Eagle Mountain - Wagley Robertson line section |  | Eagle Mountain | Wagley Robertson | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5200-E | 2015-05-15 |  | 138 | 0 | 13.8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1860, 2076, 11860, 2075, 12065 | Y | N |  |  | 3382 | 3209
15TPIT0084 | Commerce 138/69 kV autotransformer | Replace existing autotransformer |  | Commerce |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R941-E | 2015-05-15 |  | 138 | 0 | 0 | 100 |  | Hunt |  | Tier 4 |  |  |  | 1820, 1821, 11820 | Y | N |  |  | 3385 | 3212
15TPIT0083A | Collin - Arco (TMPA) 138 kV Line (Oncor's section) | Add second circuit to existing line from Collin to Frisco (Brazos) |  | Collin | Frisco (Brazos) | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R929 | 2015-05-15 |  | 138 | 1.9 | 0 | 0 |  | Collin | Denton | Tier 4 |  |  |  | 681, 2370 | Y | N |  |  | 3389 | 3216
3433 | Midland County Northwest 345/138 kV Switching Station | Construct new switching station with a 345/138 kV autotransformer |  | Midland County Northwest |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8199-E | 2015-05-15 |  | 345 | 0 | 0 | 600 |  | Midland |  | Tier 3 | 2013-11-01 | 2014-08-01 |  | 1183, 1185, 1186, 1018, 1022, 1176, 1182 | Y | N |  |  | 3633 | 3433
3456 | Morgan Creek 138/69 kV autotransformer | Replace existing autotransformer |  | Morgan Creek Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8151-E | 2015-05-15 |  | 138 | 0 | 0 | 150 |  | Mitchell |  | Tier 4 |  |  |  | 1032, 1033, 11035 | Y | N |  |  | 3659 | 3456
3429 | Andrews County South 345/138 kV Switching Station | Construct new switching station with a 345/138 kV autotransformer |  | Andrews County South |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8200-E | 2015-05-15 |  | 345 | 0 | 0 | 600 | -75,0 | Andrews |  | Tier 3 | 2013-11-01 | 2014-08-01 |  | 1157, 1158, 1162, 1150, 1153 | Y | N |  |  | 3768 | 3429
14TPIT0015 | Stryker - Troup - Tyler Grande 138 kV line | Upgrade existing line. This project also includes 16TPIT0066 (Stryker creek - Troup 138 kV Line section) | Construction schedule change | Stryker Creek | Tyler Grande | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6002 | 2015-05-15 |  | 138 | 0 | 28.9 | 0 |  | Cherokee | Smith | Tier 4 |  |  |  | 3110, 3143, 3147, 3156, 3227 | Y | N |  |  | 4139 | 1434
11TPIT0015 | Sherry - Grand Prairie - Cedar Hill 138 kV Line | Upgrade existing Sherry - Fish Creek 138 kV line section (south circuit) |  | Sherry | Fish Creek | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5121-E | 2015-05-15 |  | 138 | 0 | 6.2 | 0 |  | Tarrant | Dallas | Tier 4 |  |  |  | 1920, 2258, 2259, 2262, 2421, 12491 | Y | N |  |  | 4141 | 2570
3875 | Dermott Sw. Station - Ennis Creek Tap 138 kV Line | Convert existing 69 kV line to 138 kV line |  | Dermott Sw. Station | Ennis Creek Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9004 | 2015-05-15 |  | 138 | 0 | 7.5 | 0 |  | Scurry | Scurry | Tier 4 |  |  |  | 11410, 1312, 1313, 1314, 1410, 11306 | Y | N |  |  | 4165 | 3875
06TPIT0043C | Sherry - Liggett 138 kV line and Liggett - International Air | Rebuild existing Watson - International Airport line section |  | Watson | International Airport | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5042-WA | 2015-05-15 |  | 138 | 0 | 2.8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2124, 2128 | Y | N |  | Sherry - GM section was completed in 2009. | 4211 | 2653
3923 | Morgan Creek 138 kV Bus | Re-arrange connections for combustion turbines |  | Morgan Creek |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9006 | 2015-05-15 |  | 138 | 0 | 0 | 0 |  | Mitchell |  | Tier 4 |  |  |  | 1032 | Y | N |  |  | 4223 | 3923
3924 | McDonald Road 138 kV Switching Station | Install 138 kV breakers |  | McDonald Road |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8237 | 2015-05-15 |  | 138 | 0 | 0 | 0 |  | Howard |  | Tier 4 |  |  |  | 1333 | Y |  |  |  | 4224 | 3924
3926 | Lamesa 69 kV Switching Station | Rebuild station as a ring bus |  | Lamesa |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8245 | 2015-05-15 |  | 69 | 0 | 0 | 0 |  | Dawson |  | Tier 4 |  |  |  | 1164 | Y |  |  |  | 4226 | 3926
3932 | McDonald Road - Garden City East 138 kV Line | Rebuild existing 69 kV line as a double-circuit 138 kV and 69 kV line and convert Garden City East Substation to 138 kV |  | McDonald Road | Garden City East | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8238 | 2015-05-15 |  | 138 | 19 | 19 | 0 |  | Howard | Glasscock | Tier 4 |  |  |  | 1225, 1218, 1333, 1352 | Y | N |  |  | 4234 | 3932
11TPIT0032A | NW Carrollton - Collin second 138 kV circuit | Rebuild existing Collin - Austin Ranch Junction line section as a double-circuit line |  | Collin | Austin Ranch Junction | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M368 | 2015-05-15 |  | 138 | 11.6 | 11.6 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 12516, 12517, 12688, 629, 2370, 2517, 2518 | Y | N | 2009-R13 |  | 4240 | 1055
3970 | Paris 69 kV Capacitors | Install shunt capacitors |  | Paris Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R975 | 2015-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Lamar |  | Tier 4 |  |  |  | 1778 | Y | N |  |  | 4294 | 3970
3977 | Cobb 345 kV Switching Station | Construct 345 kV switching station |  | Cobb Switch |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R949 | 2015-05-15 |  | 345 | 0 | 0 | 0 |  | Clay |  | Tier 4 |  |  |  | 1458, 1422, 1429 | Y | N |  |  | 4302 | 3977
4101 | China Grove terminal 138 kV equipment replacement | Replace terminal equipment on line to Bluff Creek |  | China Grove |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9010 | 2015-05-15 |  | 138 | 0 | 0 | 0 |  | Mitchell |  | Tier 4 |  |  |  | 1309, 1318 | Y | N |  |  | 4450 | 4101
4174 | Cosden 138 kV terminal equipment replacement | Replace terminal equipment on line to Morgan Creek |  | Cosden |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9011 | 2015-05-15 |  | 138 | 0 | 0 | 0 |  | Howard |  | Tier 4 |  |  |  | 1032, 1332 | Y | N |  |  | 4527 | 4174
4177 | Holt 138 kV Switching Station | Rebuild station as a double bus |  | Holt |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8246 | 2015-05-15 |  | 138 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  | 1141 | Y | N |  |  | 4530 | 4177
14TPIT0092 | Temple Switch - Bell County East 345 kV line | Upgrade existing 345 kV line |  | Temple Switch | Bell County East | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R765 | 2015-05-15 |  | 345 | 0 | 10 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 13434, 13435, 3414, 3687, 13429, 39950 | Y | N |  |  | 4605 | 2375
15TPIT0071 | Eastland 69 kV capacitors | Install shunt capacitors |  | Eastland |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R768 | 2015-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Eastland |  | Tier 4 |  |  |  | 1621 | Y | N |  |  | 4666 | 3481
4289 | City View 138 kV terminal equipment replacement | Replace terminal equipment in the Fisher Road - City View - Pleasant Vally 138 kV Line |  | City View |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R967 | 2015-05-15 |  | 138 | 0 | 0 | 0 |  | Wichita |  | Tier 4 |  |  |  | 1426, 1483, 17006, 17005, 17007 | Y | N |  |  | 4668 | 4289
4296 | Midkiff 138 kV Switching Station POI | Establish a 138 kV point of interconnection (POI) | Construction schedule change | Midkiff |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8273 | 2015-05-15 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  |  | Y | N |  |  | 4677 | 4296
4324 | Ringgold 69 kV Substation | Construct new substation with shunt capacitors |  | Ringgold |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R969 | 2015-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Montague |  | Tier 4 |  |  |  | 11546 | Y | N |  |  | 4701 | 4324
3888A | Ranger 138kV Substation | Construct service to new 138kV RANGER customer-owned substation. Loop through Ckt.84 Channelview - DEPOT. |  | Ranger | Channelview/Depot | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 55 | 2015-05-29 |  | 138 | 0.2 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40380, 40280, 40282, 40410 | Y | N |  |  | 4178 | 3888
3910 | Lobo: Replace 138/69 kV autotransformer | Add 138/69 kV autotranformer capacity at Lobo |  | Lobo |  | Planned | 681 - 0850 | ETT | Rich Haley 918-599-2664 | 2599 | 2015-05-29 |  | 138 | 0 | 0 | 91 |  | Webb |  | Tier 4 |  |  |  | 80222, 80221 | Y | N |  |  | 4208 | 3910
15TPIT0043C | Fort Bend Area Upgrades | Remove Richmond substation from CNP transmission service | Delay in project schedule | Richmond |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 937 | 2015-05-29 |  | 69 | 0 | 0 | 0 |  | Fort Bend |  | Tier 3 | 2012-09-14 | 2012-10-29 |  | 44580, 44290 | Y | N |  | Cost included in project 15TPIT0043D. | 4569 | 4208
3888B | Ranger 138kV Substation | Loop existing Ckt.84 Crystal Bay to DOWLAP into SR Bertron. |  | SR Bertron | Crystal Bay/DOWLAP | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 55 | 2015-05-30 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40290, 40490, 41400, 41405 | Y | N |  | Project is associated with the addition of Ranger 138kV substation. | 4179 | 3888
11TPIT0001 | Lobo to Molina, build 345 kV circuit energized at 138kV | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Molina 138kV stations. |  | Lobo | Rio Bravo | Under Construction | 206 - 0288 | AEP TCC | Kenneth 'Rich' Haley GAREED@AEP.COM 918-599-2664 | 880 | 2015-05-31 |  | 138 | 26 | 0 | 0 |  | Webb | Webb | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 | 80230, 8295, 8646, 80221 | Y | N |  | NA | 1248 | 1245
15TPIT0032 | Fort Sam to Tenth Street - 138 kV Transmission Line Rebuild | Rebuild approximately three of the five circuit miles of 138 kV transmission of the Ft. Sam to Tenth Street transmission circuit from Tenth Street to Coliseum. |  | Fort Sam | Tenth St | Planned | S-0744 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0188 | 2015-05-31 |  | 138 | 0 | 3 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5160, 5420 | Y | N |  | There are no transformers associated with this project | 2381 | 2305
14TPIT0099 | Treaschwig - Westfield Ckt.66 | Upgrade 138kV Ckt. 66 Treaschwig to Westfield to increase thermal ratings. |  | Treaschwig | Westfield | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0 | 8.4 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 46550, 46570 | Y | N |  | Project is part of the 2012 ERCOT 5-Year Plan. | 2751 | 2630
14TPIT3390 | Alvin Auto Removal | Disconnect Alvin Autotransformer A1. | Delay in project schedule | Alvin Auto |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0 | 0 | -83 |  | Brazoria |  | Tier 4 |  |  |  | 42130, 42140, 48001, 49086, 42651, 43260, 42820 | Y | N |  |  | 3588 | 3390
15TPIT3391 | Bellaire Autotransformer Upgrade | Replace existing 600MVA Bellaire autotransformer A4 with 800MVA autotransformer. |  | Bellaire |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 345 | 0 | 0 | 200 |  | Harris |  | Tier 4 |  |  |  | 47000, 47010, 49002 | Y | N |  |  | 3589 | 3391
3396 | Cedar Hill: Replace 138/69 kV autotransformer | Add 138/69 kV autotransformer capacity at Cedar Hill | Transmission Status Update | Cedar Hill |  | Under Construction | 626 - 0794 | AEP TNC | Eric Scott 918-599-2664 | 2584 | 2015-05-31 |  | 69 | 0 | 0 | 90 |  | Coke |  | Tier 4 |  |  |  | 6423, 6425 | Y | N |  |  | 3594 | 3396
3397 | Sterling City: Add 69 kV capacitor banks | Add two 7.2 Mvar capacitor banks at Sterling City | Transmission Status Update | Sterling City |  | Under Construction | 629 - 0797 | AEP TNC | Rick McCracken 918-599-2664 | 2586 | 2015-05-31 |  | 69 | 0 | 0 | 0 | 0,14.4 | Sterling |  | Tier 4 |  |  |  | 6435 | Y | N |  |  | 3595 | 3397
3398 | Cedar Hill: Add 69 kV capacitor bank | Add one 7.2 Mvar capacitor bank at Cedar Hill | Transmission Status Update | Cedar Hill |  | Under Construction | 629 - 0797 | AEP TNC | Eric Scott 918-599-2664 | 2587 | 2015-05-31 |  | 69 | 0 | 0 | 0 | 0,7.2 | Coke |  | Tier 4 |  |  |  | 6423 | Y | N |  |  | 3596 | 3398
3399 | Bronte: Add 69 kV capacitor banks | Add two 7.2 Mvar capacitor banks at Bronte | Transmission Status Update | Bronte |  | Under Construction | 629 - 0797 | AEP TNC | Rick McCracken 918-599-2664 | 2588 | 2015-05-31 |  | 69 | 0 | 0 | 0 | 0,14.4 | Coke |  | Tier 4 |  |  |  | 6414 | Y | N |  |  | 3597 | 3399
16TPIT0020 | Constrcut: Molina 138 kV Station | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and build Molina 138kV stations. |  | MOLINA |  | Under Construction | 206-0288 | AEP TCC | Kenneth 'Rich' Haley GAREED@AEP.COM 918-599-2664 | 900 | 2015-05-31 |  | 138 | 0 | 0 | 0 |  | Webb |  | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 | 80230 | Y | N |  | NA | 3673 | 3468
15TPIT0053 | Molina to Zapata: Cut-In | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Molina 138kV stations. |  | MOLINA | ZAPATA | Under Construction | 206 - 0288 | AEP TCC | KENNETH 'RICH' HALEY GAREED@AEP.COM 918-599-2664 | 38191 | 2015-05-31 |  | 138 | 2 |  | 0 |  | Webb | Webb | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 | 8299 | Y | N |  | NA | 3703 | 3496
15TPIT0052 | Molina to Wormser: Cut-In | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Molina 138kV stations. |  | MOLINA | WORMSER | Under Construction | 206 - 0288 | AEP TCC | KENNETH 'RICH' HALEY GAREED@AEP.COM 918-599-2664 | 38190 | 2015-05-31 |  | 138 | 0.5 | 0 | 0 |  | Webb | Webb | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 | 8295 | Y | N |  | NA | 3704 | 3497
16TPIT0027 | Beeville to Sinton: Rebuild 69 kV Line | Rebuild Beeville - Sinton 69kV Line for future 138 kV operation |  | BEEVILLE | SINTON | Under Construction | 579-0737 | AEP TCC | FRANK PRITZLAFF GAREED@AEP.COM 918-599-2664 | 3465 | 2015-05-31 |  | 69 | 0 | 29.4 | 0 |  | Bee | San Patricio | Tier 1 | 2012-08-31 | 2012-12-27 | 2013-04-05 | 8198, 8405, 8904, 8413 | Y | N |  |  | 3717 | 3510
16TPIT0019 | Lobo 138 kV station: install 3 additional CB | Construct 345 kV circuit from Lobo to Molina energized at 138 kV on the open position of the Lobo to North Edinburg 345kV line. Upgrade Lobo and Molina 138kV stations. |  | LOBO |  | Under Construction | 206 - 0288 | AEP TCC | KENEATH 'RICH' HALEY GAREED@GMAIL.COM 918-599-2664 | 634 | 2015-05-31 |  | 138 |  |  |  |  | Webb |  | Tier 3 | 2012-03-12 | 2012-04-02 | 2012-04-27 | 80221 | Y | N |  |  | 3727 | 3520
3040C | WA Parish to Fort Bend Ckt.09 | Upgrade 138kV Ckt.09 Crabb River Road to WA Parish to increase thermal ratings. | Delay in Project Schedule | Crabb River Road | WA Parish | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-05-31 |  | 138 | 0 | 9.5 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44010, 44172 | Y | N |  |  | 3896 | 3040
14TPIT0065 | Rusthill: Build 138 kV station | Build new 138 kV four breaker ring bus station, Rusthill, reterminate the 138 kV lines from Concho into Rusthill and add 138/69 kV autotransformer capacity | Transmission Status and Schedule Update | Rusthill |  | Under Construction | 567 - 0741 | AEP TNC | Eric Scott 918-599-2664 | 2571 | 2015-05-31 |  | 138 | 0 | 0 | 130 |  | Tom Green |  | Tier 4 |  |  |  | 61010, 61011, 6448, 6449, 6450, 6452, 6453 | Y | N |  |  | 3948 | 1795
3823 | Stewart Capacitor Bank | Install 7.2MVAR capacitor bank at Stewart substation. |  | Stewart |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 859 | 2015-05-31 |  | 138 | 0 | 0 | 0 | 0,7.2 | Brazoria |  | Tier 4 |  |  |  | 43290 | Y | N |  |  | 4105 | 3823
3886 | Ckt.75 Rothwood Loop | Loop Ckt.75 King - Kuykendahl tap into Rothwood 345kV substation. |  | Rothwood | King/Kuykendal | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 989 | 2015-05-31 |  | 345 | 0.1 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40900, 45972, 46290 | Y | N |  |  | 4176 | 3886
14TPIT0064 | West Yates to Dinny: Rebuild 69 kV line | Rebuild West Yates to Dinny (formerly Discovery Canyon) 69 kV line with 959.6 ACSS/TW |  | West Yates | Dinny | Planned | 570 - 0744 | AEP TNC | Eric Scott 918-599-2664 | 2574 | 2015-05-31 |  | 69 | 0 | 2.28 | 0 |  | Pecos | Crockett | Tier 4 |  |  |  | 6574, 6576, 6581, 60370, 60371, 60372, 6556, 6572, 6575, 6580, 6585 | Y | N |  |  | 4180 | 1803
4007 | Pasadena to Spencer tap Ckt.06 Upgrades | Upgrade 138 kV Ckt.06 Pasadena to Spencer tap to increase thermal ratings. |  | Pasadena | Spencer/College | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1024 | 2015-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 43040, 43271 | Y | N |  |  | 4352 | 4007
4147 | WA Parish to Sienna Ckt.02 Substation Upgrade | Upgrade substation equipment at WA Parish to increase thermal ratings for 138kV Ckt.02. |  | WA Parish | Sienna | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1129 | 2015-05-31 |  | 138 | 0 | 0 | 0 |  | Fort Bend |  | Tier 4 |  |  |  | 44010, 44651 | Y | N |  |  | 4492 | 4147
4162 | BARBUR Replacement 138kV Substation ALKANE | Replace existing customer-owned BARBUR substation with another nearby substation. |  | ALKANE | LaPorte/Morgans Point | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0.1 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40140, 40160, 40941, 41100 | Y | N |  |  | 4513 | 4162
3936A | Fairmont to Webster Ckt.06 Upgrades | Upgrade 138kV Ckt.06 Fairmont to NASA to increase thermal ratings |  | Fairmont | NASA | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0 | 7.2 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42610, 42970 | Y | N |  |  | 4532 | 3936
4182A | Alexander Island 138kV Conversion | Convert Alexander Island from double-tap 69kv to double-tap 138kV service. Tap existing Ckt.87 SR Bertron to ARITEK. |  | Alexander Island | SR Bertron/AIRTEK | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0.2 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40081, 41391, 40120, 41410, 41400, 41415 | Y | N |  |  | 4537 | 4182
4182B | Alexander Island 138kV Conversion | Convert Alexander Island from double-tap 69kv to double-tap 138kV service. Tap from Ckt.84 DOWLAP - SR Bertron (reconfigured in 2015). |  | Alexander Island | DOWLAP/SR Bertron | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0.1 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40082, 41392, 40490, 41383, 41400, 41410 | Y | N |  |  | 4596 | 4182
4266 | Wolfberry: Build 138 kV station & add 138 kV caps | Construct 138 kV substation box bay for customer interconnection, and install two 14.4 Mvar capacitor banks | Project Title, Project Description, and Project Status Update | Wolfberry |  | Under Construction | 687 - 0857 | AEP TNC | Eric Scott 918-599-2664 | 2604 | 2015-05-31 |  | 138 | 0 | 0 | 0 | 0,28.8 | Reagan |  | Tier 4 |  |  |  | 60375, 6535, 6562 | Y | N |  |  | 4639 | 4266
4426 | Aritek to Chorin Ckt 87 Thermal Uprate | Upgrade 138kV Ckt.87 ARITEK to CHORIN to increase thermal ratings. |  | ARITEK | CHORIN | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40120, 40320 | Y | N |  |  | 4810 | 4426
4427 | Blodgett to Teco Ckt 37 Thermal Uprate | Upgrade 138kV Ckt.37 Blodgett to Teco to increase thermal ratings. |  | Blodgett | Teco | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-05-31 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47430, 47521 | Y | N |  |  | 4811 | 4427
10TPIT0001 | Trumbo - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Leon Creek to Pleasanton Rd-Loxley (AEP) line | Accelarated by Disribution Planning | Trumbo | Leon Creek-Pleasanton Rd | Planned | T-0082 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0181 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5429, 5260, 8203 | Y | N |  | There are no transformers associated with this project | 976 | 975
11TPIT0009 | Dunlap 138kV substation | Install one 30MVA Transformer at Dunlap Substation |  | Dunlap Substation | Dunlap Substation | Under Construction |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | 3230_117_2930 3230_117_2933 3240_117_4930 3240_117_4933 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9045 | Y | N |  |  | 1021 | 1020
15TPIT0023 | Seaton Auto | Upgrade 138-69 kV auto to 100 MVA |  | Seaton | Seaton | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 11036 | 2015-06-01 |  | 138 | 0 | 0 | 100 |  | Bell |  | Tier 4 |  |  |  | 131, 130 | Y | N |  |  | 1188 | 1185
14TPIT0068 | Future 69kV upgrades & North Denton Auto Upgrade |  |  |  |  | Planned |  | DME | Chuck Sears 940-349-7111 |  | 2015-06-01 |  | 69 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 905, 915, 912, 985 | Y |  |  |  | 1425 | 1424
16TPIT0037 | Rebuild Orange Grove to Casa Blanca | Rebuild 4/0 ACSR 69 kV to 795 ACSR circuit on 138 kV capable structures. |  | Orange Grove | Casa Blanca | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-06-01 |  | 69 | 0 | 6.7 | 0 |  | Jim Wells | Jim Wells | Tier 1 | 2012-09-05 | 2013-01-31 | 2013-03-12 | 5662, 8166 | Y | N |  |  | 3116 | 2947
3265 | Paredes switch new switching station for wind farm | A new swtiching station in the E Rio Hondo to Central 138 kV line |  | Paredes |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-06-01 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 5761, 5764, 5766 | Y | N |  |  | 3441 | 3265
3417 | North Calliham Capacitor | Adds 9.6 MVAR capacitor to North Calliham |  | North Calliham |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-06-01 |  | 69 | 0 | 0 | 0 | 0,9.6 | McMullen |  | Tier 4 |  |  |  | 5698 | Y | N |  |  | 3617 | 3417
3454 | Braunig_to_Toyota_Rebuild | Rebuild an existing 138 kV transmissions line between the Toyota and Valley Road Substations. |  | Braunig-Alamo1_8-Mauerman-Valley | Alamo1_8-Mauerman-Toyota-Cagnon | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0181 | 2015-06-01 |  | 138 | 0 | 13.7 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5007, 5053, 5297, 5025, 5428, 5465 | Y | N |  | There are no transformers associated with this project | 3655 | 3454
4077 |  |  |  | Katz |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 14006 | 2015-06-01 |  | 69 | 0 | 0 | 0 | 0,16 | King |  | Tier 4 |  |  |  | 774 | Y |  |  |  | 4427 | 4077
4089 | Summit: Upgrade Ckt Breaker SU-950 | Upgrade SU-950 bus tie circuit breaker (connecting buses MB1 and MB2) and related switches to 3000 amps |  | Summit | Summit | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2015-06-01 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9279, 9280 | Y |  |  |  | 4439 | 4089
4136 | DME_Pockrus_Spencer |  |  | Pockrus | Spencer | Planned | N/A | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2015-06-01 |  | 138 | 3.8 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 917, 982 | Y | N | N/A |  | 4481 | 4136
4137 | DME_BBrae_NLakes |  |  | Bonnie Brae | North Lakes | Planned | N/A | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2015-06-01 |  | 69 | 0 | 1.2 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 905, 915 | Y | N | N/A |  | 4482 | 4137
4322 | Add McKinney Station - Tap Woodrow - Kingsrow line |  |  | Woodrow | Kingsrow | Planned |  | DME | Chuck Sears 940-349-7111 |  | 2015-06-01 |  | 69 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 907, 901, 909 | Y | N |  |  | 4699 | 4322
3267A | Rebuild ERioHondoTo Paredes to Central Avenue 138 kV line | Rebuild Paredes Switch to East Rio Hondo |  | E Rio Hondo | Paredes Switch | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-06-02 |  | 138 | 0 | 6 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5761, 5764 | Y | N |  |  | 3443 | 3267
3881 | GSEC_3881_Add_Church_Sub |  | NA |  |  | Under Construction | NA | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2015-06-02 |  | 138 | 0 | 0 | 0 |  | Callahan | Callahan | Tier 4 |  |  |  | 60367, 60365 | Y | N |  | Approximate energization date of 06/2015 | 4171 | 3881
3868 | Butman Substation | Construct the new Butman substation on the existing LCRA TSC Abilene South to Eskota 138-kV transmission line (T470). |  | Butman | Abilene S / Eskota | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2015-06-05 |  | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 76318, 76317, 76319 | Y | N |  |  | 4156 | 3868
3880 | GSEC_3880_Add_Butman_Sub |  | NA |  |  | Under Construction | NA | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2015-06-06 |  | 138 | 0 | 0 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 76318 | Y | N |  | Approximate energization date of 06/2015 | 4170 | 3880
13TPIT0047 | Parkway to EC Mornhinweg | Construct a new 138 kV 795 ACSR transmission line between the new EC Mornhinweg substation (7463) and the Parkway substation (7611). |  | Parkway | EC Mornhinweg | Planned | 13TPIT0066 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1010634 | 2015-06-10 |  | 138 | 8 | 0 | 0 |  | Comal | Guadalupe | Tier 2 | 2009-02-01 | 2009-06-15 |  | 7463, 7611 | Y | N |  |  | 1004 | 1003
12TPIT0143C | Danevang Switch to El Campo Rebuild | Rebuild 4-0 ACSR 69 kV to 138 capable 795 ACSR. |  | Danevang Switch | Plainview | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-06-12 |  | 69 | 0 | 4.89 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  | 5540, 5544 | Y | N |  |  | 1549 | 1535
4001 | Cuero Hydro to Hochheim Transmission Line Overhaul | Upgrade the Cuero Hydro (78189) to Hochheim (78577) 69kV transmission line to 795 ACSR Drake (111 MVA), 138kV capable. |  | Cuero Hydro | Hochheim | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013683 | 2015-06-23 |  | 69 | 0 | 10.67 | 0 |  | DeWitt | DeWitt | Tier 4 |  |  |  | 8578, 78189, 78577 | Y | N |  |  | 4327 | 4001
15TPIT0060 | Convert KenedySw - Guadalupe (Cuero) to 138kV | Convert the 42.3 miles Kenedy Switch (8186) - Guadalupe (7253) 69-kV line to 138-kV line, 220 MVA. Guadalupe is a new substation to be built near Cuero Hydro (78189). |  | Kenedy Switch | Guadalupe | Under Construction |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013403 | 2015-06-24 |  | 138 | 0 | 42.3 | 0 |  | Karnes | DeWitt | Tier 1 | 2013-02-15 | 2013-02-15 |  | 78188 | Y | N |  | Coordinate with AEP Coordinate with GVEC | 3968 | 3724
3872 | MARINE 138kV Substation | Construct service to new 138kV MARINE customer-owned substation. Loop through Ckt.59 Surfside to Quintana. | Delay in project schedule | MARINE | Surfside/Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 55 | 2015-06-29 |  | 138 | 1.5 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 43155, 43360, 43435 | Y | N |  |  | 4160 | 3872
14TPIT0050 | Lon Hill to North Edinburg: Reconductor 345kV Line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Replace Series Capacitors at North Edinburg and Rio Hondo | Updated In-Service Date | Lon Hill | North Edinburg | Under Construction | 071 - 0281 | AEP TCC | Michael Glueck 918-599-2664 | 3183 | 2015-06-30 |  | 345 | 0 | 122.88 | 0 |  | Nueces | Hidalgo | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 5660, 8455, 8452, 8905 | Y | N |  |  | 1420 | 1419
16TPIT0035 | BEC Munday to Gillespie: Rebuild 69 kV line | Rebuild BEC Munday to Gillespie 69 kV line with 959.6 ACSR | Transmission Status Update | BEC Munday | Gillespie | Under Construction | 568 - 0742 | AEP TNC | Aaron Schwerman 918-599-2664 | 2578 | 2015-06-30 |  | 69 | 0 | 7.2 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 764, 6112 | Y | N |  |  | 2911 | 2756
14TPIT0140 | Bunsen: Build new four breaker 138 kV station | Construct new Bunsen station along the Lon Hill to Kingsville 138 kV line and build 0.8 miles of double circuit 138 kV line with 959.6 ACSS/TW from Bunsen to new customer station |  | Lon Hill | Kingsville | Under Construction | 610 - 0778 | AEP TCC | Dave Goetz 918-599-2664 | 3493 | 2015-06-30 |  | 138 | 1.6 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8459, 8452, 8518 | Y |  |  |  | 3221 | 3052
15TPIT0068 | Add Hecker 138kV substation | Add Hecker 138kV substation | Changed Dollars | Dupont SS | Whitepoint SS | Planned | 608 - 0776 | AEP TCC | Teresa Trotman gareed@aep.com 918-599-2664 | 3488 | 2015-06-30 |  | 138 | 0 | 0 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8565, 8422, 8961 | Y | N |  |  | 3268 | 3099
17TPIT0009 | East Munday: Replace 138/69 kV autotransformer | Add 138/69 kV autotransformer capacity at East Munday | Transmission Status Update | East Munday |  | Under Construction | 588 - 0746 | AEP TNC | Aaron Schwerman 918-599-2664 | 2580 | 2015-06-30 |  | 69 | 0 | 0 | 90 |  | Knox |  | Tier 4 |  |  |  | 6108, 6110 | Y | N |  |  | 3400 | 3227
15TPIT3253 | Treaschwig to Humble Ckt. 66 | Upgrade 138kV Ckt. 66 Treaschwig to Humble to increase thermal ratings. | Delay in Project Schedule | Treaschwig | Humble | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 732 | 2015-06-30 |  | 138 | 0 | 9.4 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40830, 46550 | Y | N |  |  | 3427 | 3253
3832 | Reconductor Heights - Whiteoak Ckt34 to Increase Thermal Rat | Reconductor Ckt.34 Heights to White Oak and upgrade substation equipment to increase thermal ratings. |  | Heights | White Oak | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 823 | 2015-06-30 |  | 69 | 0 | 4.35 | 0 |  | Harris |  | Tier 4 |  |  |  | 46620, 47580, 47680 | Y | N |  |  | 4115 | 3832
3850 | Russek Street: Build 138 kV station | Construct the new Russek Street station along the Big Lake to Twin Buttes 138 kV line | Transmission Status, Company Contact, and Schedule Update | Russek Street |  | Under Construction | 673 - 0842 | AEP TNC | Rick McCracken 918-599-2664 | 2808 | 2015-06-30 |  | 138 | 0 | 0 | 0 |  | Reagan |  | Tier 4 |  |  |  | 6517, 6535, 6559 | Y | N |  |  | 4134 | 3850
3851 | Russek Street: Add 138 kV capacitor banks | Add one 14.4 Mvar and two 7.2 Mvar capacitor banks at Russek Street | Transmission Status, Company Contact, and Schedule Update | Russek Street |  | Under Construction | 672 - 0841 | AEP TNC | Rick McCracken 918-599-2664 | 2807 | 2015-06-30 |  | 138 | 0 | 0 | 0 | 0,28.8 | Reagan |  | Tier 4 |  |  |  | 6517 | Y | N |  |  | 4135 | 3851
3964 | Johnson City Cap Bank Addition | Add two (2) 69-kV 7.8 MVAR capacitor banks at PEC Johnson City (7516) substation. |  | Johnson City |  | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2015-06-30 |  | 69 | 0 | 0 | 0 | 0,15.6 | Blanco |  | Tier 4 |  |  |  | 7516 | Y | N |  |  | 4285 | 3964
4013 | Hindes Temporary Tap: STEC Interconnect | Hindes Temporary Tap: STEC Interconnect |  | DILLEY SS | SAN MIGUEL | Planned | 682 - 0837 | AEP TCC | Mike Tallon 918-599-2664 | 3539 | 2015-06-30 |  | 138 | 0 | 0 | 0 |  | La Salle |  | Tier 4 |  |  |  | 88215, 5704, 8212 | Y | N |  |  | 4358 | 4013
14TPIT0100 | Tilden Capacitor | Add 19.2 MVAR capacitor |  | Tilden |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-07-01 |  | 138 | 0 | 0 | 0 | 0,19.2 | McMullen |  | Tier 4 |  |  |  | 5701 | Y | N |  |  | 2661 | 2555
14TPIT0121 | Channelview to CONIAL Ckt.84 Thermal Uprate | Upgrade 138kV Ckt.84 Channelview to CONIAL to increase thermal ratings. |  | Channelview | CONIAL | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-07-01 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41675, 40280, 40330, 40580, 40590, 40610, 40611, 41171, 41260, 41670, 40370, 40720, 40780, 41010, 41172, 41530, 41712 | Y | N |  |  | 3048 | 2874
3680 | Decker-Exxon Ckt83 Thermal Uprate | Upgrade 138kV Ckt.83 Decker to Exxon to increase thermal ratings. |  | Decker | Exxon | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-07-01 |  | 138 | 0 | 1 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40430, 40570 | Y | N |  |  | 3918 | 3680
3950A | TH Wharton to White Oak Ckt.71 | Upgrade 345kV Ckt.71 TH Wharton to Addicks to increase thermal ratings. (Transmission upgrades only.) |  | TH Wharton | Addicks | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-07-01 |  | 345 | 0 | 9.7 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45500, 45600 | Y | N |  |  | 4269 | 3950
3950B | TH Wharton to White Oak Ckt.71 | Upgrade 345kV Ckt.71 Addicks to White Oak to increase thermal ratings. (Transmission upgrades only.) |  | Addicks | White Oak | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-07-01 |  | 345 | 0 | 9.1 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45600, 46600 | Y | N |  |  | 4270 | 3950
4129 | SLU_GlassRanch_addition |  |  | Sales Ranch | Glass Ranch | Planned | N/A | SLU | Brad Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2015-07-01 |  | 138 | 10 | 0 | 0 | 0,48 | Martin | Martin | Tier 4 |  |  |  | 79507, 79508, 79558, 79510, 79616, 79550, 79618 | Y | N | N/A |  | 4474 | 4129
4131 | SLU_Pemkiff_addition |  |  | Pemkiff | Upton | Planned | N/A | SLU | Brad Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2015-07-01 |  | 138 | 0.3 | 0 | 0 |  | Upton | Upton | Tier 4 |  |  |  | 79555, 1210, 79612, 79614 | Y | N | N/A |  | 4476 | 4131
4132 | SLU_TelephoneRd_addition |  |  | Telephone Road | Amoco Tap | Planned | N/A | SLU | Brad Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2015-07-01 |  | 345 | 32.8 | 0 | 500 |  | Midland | Andrews | Tier 2 | 2013-12-20 | 2014-07-23 |  | 79630, 79650, 1158, 1185, 79618, 904532 | Y | N | N/A |  | 4477 | 4132
4535 | Add new 138kV Natural Dam Station |  |  | Natural Dam | Natural Dam | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2015-07-01 |  | 138 | 0 | 0 | 0 |  | Martin | Martin | Tier 4 |  |  |  | 79509 | Y | N |  |  | 4937 | 4535
3361 | Magill Station: New 138kV Station for STEC Interconnect | Build New 138kV Station to Accommodate STEC Interconnection to serve customer load |  | Bay City | Lane City | Planned | 609 - 0777 | AEP TCC | Dave Goetz gareed@aep.com 918-599-2664 | 3496 | 2015-07-15 |  | 138 | 0 | 0 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 8111, 8113, 8127 | Y | N |  |  | 3556 | 3361
3406 | Tenaris 138 kV station | Connects new load to new Magill station with 138 kV line |  | Magill | Tenaris | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-07-16 |  | 138 | 4.5 | 4.5 | 0 |  | Matagorda | Matagorda | Tier 4 |  |  |  | 5562, 5554, 5556, 5560, 8111 | Y | N |  |  | 3606 | 3406
12TPIT0143B | Danevang Switch to El Campo Rebuild | Rebuild 4-0 ACSR 69 kV to 138 capable 795 ACSR. |  | Industrial Park | Plainview | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-07-24 |  | 69 | 0 | 5.3 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  | 5540, 5543 | Y | N |  | cost in last phase of project | 1548 | 1535
14TPIT0108 | Kenedy 138/69 kV Switching Station: Upgrade | Construct 138 double circuit line from Kenedy Switch Station to Tuleta and Pettus respectively. Kenedy Switching station to Pettus will be energized at 69 kV. Upgrade 138 kV site at Kenedy Switching Station and construct new Tuleta 138 kV Station. |  | KENEDY SWITCHING STATION |  | Under Construction | 603 - 0765 | AEP TCC | FRANK PRITZLAFF(AEP) GAREED@AEP.COM 918-599-2664 | 3482 | 2015-07-30 |  | 138 | 0 | 0 | 0 |  | Karnes |  | Tier 4 |  |  |  | 8186 | Y | N |  |  | 3683 | 3477
4256 | Santa Rita: Build 69 kV station | Construct new 69 kV in and out substation off the Big Lake to McCamey line, and demolish Texon | Transmisison Status Update | Santa Rita |  | Under Construction | 691 - 0861 | AEP TNC | Bill Clarke 918-599-2664 | 2608 | 2015-07-31 |  | 69 | 0 | 0 | 0 |  | Reagan |  | Tier 4 |  |  |  | 6504, 6538, 6541, 6555 | Y | N |  |  | 4627 | 4256
3271 | Comal Street - New 138kV Substation | Loop new 138kV substation into the existing 138kV Laredo to Five Points. |  | Comal St | Laredo-Five Points | Planned | T-0216 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0721 | 2015-08-15 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5096, 5150, 5255 | Y | N |  | There are no transformers associated with this project | 3447 | 3271
12TPIT0143A | Danevang Switch to El Campo Rebuild | Rebuild 4-0 ACSR 69 kV to 138 capable 795 ACSR. |  | Industrial Park | El Campo | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-08-21 |  | 69 | 0 | 2.2 | 0 |  | Wharton | Wharton | Tier 4 |  |  |  | 5538, 5543 | Y | N |  | cost in last phase of project | 1547 | 1535
3687 | Estes: Build 138 kV station | Construct new Estes station along the South Abilene to Putnam 138 kV line | Schedule Update | Estes |  | Planned | 655 - 0824 | AEP TNC | Eric Scott 918-599-2664 | 1819 | 2015-08-31 |  | 138 | 0 | 0 | 0 |  | Callahan |  | Tier 4 |  |  |  | 60365, 6309, 6773 | Y | N |  |  | 3928 | 3687
4180 | Cinnamon: Build 69 kV station | Construct new Cinnamon tap on the North San Angelo to San Angelo Grape Creek Tap 69 kV line | Company Contact and Schedule Update | Cinnamon |  | Planned | 695 - 0865 | AEP TNC | Eric Scott 918-599-2664 | 2809 | 2015-08-31 |  | 69 | 0 | 0 | 0 |  | Tom Green |  | Tier 4 |  |  |  | 60380, 6459, 6462 | Y | N |  |  | 4535 | 4180
13TPIT0148B | Cotulla 138 kV bus load and auto | Second phase installs 138 kV breakers and autotransformer in Sept 15. |  | Cotulla |  | Under Construction |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-09-01 |  | 69 | 0 | 0 | 150 |  | La Salle |  | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5876, 8520 | Y | N |  |  | 3650 | 3449
4494 | AEP_4494_Koch Upriver | Add 138kV breakers at Koch Upriver 138kV Substation |  | Koch Upriver | Koch Upriver | Planned | 693 - 0863 | AEP TCC | Glen Reed 918-599-2664 | 3540 | 2015-09-01 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8467 | Y | N |  |  | 4888 | 4494
4029 | Upgrade Sealy 10.8 MVAR cap bank to 12.6 MVAR | Upgrade Sealy 10.8 MVAR cap bank to 12.6 MVAR | Delay in project schedule | Sealy |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-09-25 |  | 138 | 0 | 0 | 0 | 0,1.8 | Austin |  | Tier 4 |  |  |  | 44640 | Y | N |  |  | 4374 | 4029
14TPIT0120 | Moore Road 138kV Substation | Build new 138kV Moore Road substation. Loop-Tap through Ckt.08 GBY to Uvalde. | Delay in project schedule | Moore Road | Greens Bayou/Uvalde | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-09-30 |  | 138 | 0.6 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40555, 40710, 41651 | Y | N |  |  | 3047 | 2873
15TPIT0029 | CMC Tap to CMC (SMI) 138kV Transmission Line | Build 2 miles of new double ckt 138kV t-line loop, 1192 ACSR between CMC Tap and CMC (SMI) substation. Add terminals at CMC plant substation |  | CMC Tap | CMC (SMI) | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2015-09-30 |  | 138 | 2.2 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7602, 7604, 7606 | Y | N |  |  | 3403 | 3230
3418 | Nelson Sharpe: Add 345 kV Terminal for WF Interconnect | Add a new 345 kV line terminal at Nelson Sharpe for the Patriot WF Interconnect | Updated In-Service Date | Nelson Sharpe |  | Under Construction | 515 - 0756 | AEP TCC | Dave Goetz 918-599-2664 | 3474 | 2015-09-30 |  | 345 | 0 | 0 | 0 |  | Kleberg |  | Tier 4 |  |  |  | 85000 | Y | N |  | Delayed Upon Request From Developer | 3618 | 3418
3674 | Puncher: Add 69 kV capacitor bank | Puncher: Add one 7.2 Mvar capacitor bank | Company Contact and Schedule Update | Puncher |  | Planned | 647 - 0816 | AEP TNC | Michael Tallon 918-599-2664 | 1811 | 2015-09-30 |  | 69 | 0 | 0 | 0 | 0,7.2 | Mason |  | Tier 4 |  |  |  | 6407 | Y | N |  |  | 3911 | 3674
3715 | Cottulla STEC 138kV Station | Cotulla STEC 138kV Substation | NEW | JARDIN | COTULLA (AEP) | Planned | 631 - 0800, 3719 | AEP TCC | Glen Reed 918-599-2664 | 3528 | 2015-09-30 |  | 138 | 0 | 0 | 0 |  | La Salle | La Salle | Tier 4 |  |  |  | 8520, 8526, 8610, 8611 | Y | N |  |  | 3959 | 3715
14TPIT0044 | Helotes to Hill Country - 138 kV Substation Equipment Upgrad | Upgrade terminals at Helotes and Hill Country to ensure a 2420 A rating and remove existing MLSE on Helotes to Hill Country 138 kV transmission line |  | Helotes | Hill Country | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0651 | 2015-10-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5200, 5210, 5461 | Y | N |  | There are no transformers associated with this project | 964 | 963
15TPIT0011 | Shannon to Montague | Rebuild Shannon to Montague 69 kV line with 959 ACSS. |  | Shannon | Montague | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 10045 | 2015-10-01 |  | 69 | 0 | 23.36 | 0 |  | Clay | Montague | Tier 4 |  |  |  | 768, 769, 772, 1548 | Y | N |  |  | 2536 | 2431
14TPIT0062 | Kurten Substation Upgrade | Install (3) Breaker ring to support (2) existing 138 lines and (1) existing 138/12.5 transformer (No MOD changes necessary) |  |  |  | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2015-10-01 |  | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  |  | 3041 | 2867
4076 |  |  |  | Stephenville |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 13002 | 2015-10-01 |  | 138 | 0 | 0 | 60 |  | Erath |  | Tier 4 |  |  |  | 299, 295 | Y |  |  |  | 4426 | 4076
4133 | SLU_Vealmoor_addition |  |  | Vealmoor | Longdraw | Planned | N/A | SLU | Brad Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2015-10-01 |  | 345 | 11.4 | 0 | 450 |  | Borden | Borden | Tier 2 | 2013-12-20 | 2014-07-23 |  | 79640, 59900, 79600 | Y | N | N/A |  | 4478 | 4133
4154 | ARCHER 138kV Substation | Construct service to new 138kV ARCHER customer-owned substation. Loop through Ckt.92 Scarsdale to El Dorado. |  | ARCHER | Scarsdale/El Dorado | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-10-01 |  | 138 | 0.1 | 0.5 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42570, 42562, 43610 | Y | N |  |  | 4501 | 4154
4536 | Tap 138kV East Stiles - Stiles line to create Rocky Rd Stati |  |  | East Stiles | Stiles | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2015-10-01 |  | 138 | 0 | 0 | 0 |  | Reagan | Reagan | Tier 4 |  |  |  | 79562, 79614, 79623 | Y | N |  |  | 4938 | 4536
4537 | Add new line to connect Rocky Rd to Coates station (new) |  |  | Rocky Rd | Coates | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2015-10-01 |  | 138 | 7 | 0 | 0 |  | Reagan | Reagan | Tier 4 |  |  |  | 79563, 79562 | Y | N |  |  | 4939 | 4537
4538 | Add new 138kV line from Tall City to Glass Ranch |  |  | Tall City | Glass Ranch | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2015-10-01 |  | 138 | 10 | 0 | 0 |  | Midland | Martin | Tier 2 |  |  |  | 79507, 79558 | Y | N |  |  | 4940 | 4538
4539 | Tap 138kV Sales Ranch - Grady line to create Coronado statio |  |  | Sales Ranch | Grady | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2015-10-01 |  | 138 | 0 | 0 | 0 |  | Martin | Martin | Tier 4 |  |  |  | 79564, 79508, 79550 | Y | N |  |  | 4941 | 4539
08TPIT0172 | Gunsight 138 kV Switching Station | Construct new switching station to connect a new wind farm |  | Gunsight Switching Station |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R829-WA | 2015-10-15 |  | 138 | 0 | 0 | 0 |  | Howard |  | Tier 4 |  |  |  | 1360, 1355, 1395 | Y | N |  |  | 2680 | 2564
12TPIT0205 | AEP_McCampbell: New Substation Cut In | Customer to construct 138kV substation. Two 138kV circuits Cut-In to McCampbell substation. | Planned | Dupont SS | Whitepoint SS | Planned | 561 - 0729 | AEP TCC | Glen Reed 918-599-2664 | 3435 | 2015-10-30 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 | 2000-01-01 | 2000-01-01 | 2000-01-01 | 80469, 8414, 8422, 8961, 80470 | Y | N |  |  | 3444 | 3268
4401 | Javalina: Build 138 kV Temp Tap | Interconnect Javalina Windfarm at Javalina to connect Bordas to the Molina to Rio Bravo 138 kV line |  | Javalina |  | Planned | 699 - 0869 | ETT | Rich Haley 918-599-2664 | 3543 | 2015-10-31 |  | 138 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  | 80646, 8295, 80230 | Y |  |  |  | 4780 | 4401
11TPIT0012 | Euless - Grapevine Ball St - Grapevine Jnct 138 kV Line | Reconductor existing double-circuit 138 kV line (Euless - Grapevine Ball Street east circuit and Euless - Grapevine Junction west circuit) |  | Euless | Grapevine Ball Street/Grapevine Junction | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5131-E | 2015-11-15 |  | 138 | 0 | 11.8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2014, 2016, 2021, 12012, 12022, 12021, 12040 | Y | N |  | Euless - Highway 360 Substation section by 5/2014 | 3112 | 2943
09TPIT0044 | E. Richardson - Apollo 138kV line (Oncor' section) | Upgrade existing 138 kV line |  | E. Richardson | Apollo | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3033-WA | 2015-11-15 |  | 138 | 0 | 2.3 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 802, 2690 | Y | N |  |  | 3239 | 3070
3971 | Eskota second 138/69 kV autotransformer | Install second 138/69 kV autotransformer |  | Eskota |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9008 | 2015-11-15 |  | 138 | 0 | 0 | 100 |  | Nolan |  | Tier 4 |  |  |  | 1340, 1339 | Y | N |  |  | 4295 | 3971
4169 | Sweetwater Creek 69 kV capacitor | Install shunt capacitor |  | Sweetwater Creek |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9007 | 2015-11-15 |  | 69 | 0 | 0 | 0 | 0,27.6 | Nolan |  | Tier 4 |  |  |  | 1407 | Y | N |  |  | 4522 | 4169
3969 | Bergheim Capacitor Bank | Add one (1) 138kV 31.2 MVAR capacitor bank at the Bergheim (7170) substation. |  | Bergheim |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014336 | 2015-11-23 |  | 138 | 0 | 0 | 0 | 0,31.2 | Comal |  | Tier 4 |  |  |  | 7170 | Y | N |  |  | 4290 | 3969
10TPIT0010 | Coppell to Roanoke Reconductor | Reconductor existing Coppell to Roanoke 138kv line with 959ACSS conductor |  | Coppell | Roanoke | Planned | 12TPIT0079 | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 2005 | 2015-12-01 |  | 138 | 0 | 17 | 0 |  | Tarrant | Dallas | Tier 4 |  |  |  | 555, 556, 661, 648, 1852 | Y | N |  | construction by Oncor | 230 | 233
12TPIT0123 | Braunig West Bus - 138 kV Substation Equipment Upgrade | Upgrade Terminals at Braunig West for Valley Rd., Mauermann Rd., Streich Rd. circuits and upgrade terminals at remote ends to ensure a 2420 A rating and remove the existing MLSE on the 138kV transmission lines. |  | Braunig_W | Valley Rd Mauermann Streich Rd | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0658 | 2015-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5007, 5025, 5417, 5465 | Y | N |  | There are no transformers associated with this project | 639 | 639
12TPIT0090 | Whitney 2nd Auto | Replace 60 MVA, 138-69 kV auto with 75 MVA auto |  | Whitney |  | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 10048 | 2015-12-01 |  | 138 | 0 | 0 | 75 |  | Bosque |  | Tier 4 |  |  |  | 243, 3546 | Y | N |  |  | 883 | 882
16TPIT0012 | Encino to Skyline - 138 kV Substation Equipment Upgrade | Upgrade terminals at Encino and Skyline to ensure a 2420 A rating and remove existing MLSE on Encino to Skyline 138 kV transmission line |  | Encino | Skyline | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0671 | 2015-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5140, 5369 | Y | N |  | There are no transformers associated with this project | 973 | 972
14TPIT0061 | Briarcrest to Atkins Upgrade | Upgrade to 795 ACSR to alleviate overload during double contingency situations. Add OPGW. Add new poles/structures. |  | Atkins | Briarcrest | Planned |  | BRYN |  |  | 2015-12-01 |  | 138 | 0 | 3.4 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32864, 32877 | Y |  |  |  | 2052 | 2001
15TPIT0033 | Randolph - 138 kV Substation Equipment Upgrade | Upgrade the Weiderstein and Tuttle terminals and ensure a 2000 A rating (minimum). Reconfigure and-or upgrade the main bus to ensure a 2000 A rating (minimum). |  | Randolph | Tuttle-Weiderstein | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0645b | 2015-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5360, 5435 | Y | N |  | There are no transformers associated with this project | 2382 | 2306
13TPIT0100 | Correction of Effective date for 13TPIT0100 to 12/1/2015 | Build Westminster 138 kV Substation and transmission line tap from Oncor's Anna Switch - Van Alstyne 138 kV line. | Budget |  |  | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07612 | 2015-12-01 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 37270 | Y | N |  |  | 3812 | 3598
3764 | Brackettville 138 kV Station: Upgrade 138 kV Station | Construct a five breakers ring at the expanded Brackettville 138 kV Statio for the Generator Interconnect |  | BRACKETTVILLE |  | Under Construction | 665-0834 | AEP TCC | MICHAEL TALLON GAREED@AEP.COM 918-599-2664 | 3529 | 2015-12-01 |  | 138 |  |  |  |  | Kinney |  | Tier 4 |  |  |  | 8252 | Y | N |  |  | 4009 | 3764
4078 |  |  |  | Perch Hill |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 | 12012 | 2015-12-01 |  | 138 | 0 | 0 | 0 | 0,25 | Wise |  | Tier 4 |  |  |  | 590 | Y |  |  |  | 4428 | 4078
4134 | DME_Wrow-KRow_update |  |  | Kingsrow | woodrow | Planned | N/A | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2015-12-01 |  | 69 | 0 | 4.2 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 901, 907, 909 | Y | N | N/A |  | 4479 | 4134
4135 | DME_Krow-NDenton_Update |  |  | Kingsrow | N Denton | Planned | N/A | DME | Chuck Sears cxsears@cityofdenton.com 940-249-7111 |  | 2015-12-01 |  | 69 | 0 | 1.91 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 909, 912 | Y | N | N/A |  | 4480 | 4135
4501 | Trading Post 138-kV Breakers | Install Line Breakers at Trading Post on the Trading Post to Marshall Ford and the Trading Post to Cedar Valley 138kV lines (T315). |  | Trading Post |  | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2015-12-01 |  | 138 | 0 | 0 | 0 |  | Travis |  | Tier 4 |  |  |  | 7505, 9282 | Y | N |  |  | 4898 | 4501
4170 | Midessa South 138 kV Switching Station | Construct new 138 kV switching station |  | Midessa South |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8252 | 2015-12-14 |  | 138 | 0 | 0 | 0 |  | Midland |  | Tier 4 |  |  |  | 1124, 1137, 1138 | Y | N |  |  | 4523 | 4170
08TPIT0153 | Elkton - Athens 138 kV line | Upgrade existing 138 kV line |  | Elkton | Athens | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R651-E | 2015-12-15 |  | 138 | 0 | 27.9 | 0 |  | Henderson | Henderson | Tier 4 | 2007-11-26 |  |  | 3106, 3238 | Y | N |  |  | 1246 | 1243
15TPIT0039 | Plano Tennyson Road - McDermott | Upgrade 138 kV line |  | Plano Tennyson Road | McDermott | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4103-E | 2015-12-15 |  | 138 | 0 | 5.3 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 2523, 10011, 2516 | Y | N |  |  | 2346 | 2273
15TPIT0040 | Temple Switch 345/138 kV autotransformer | Replace existing autotransformer |  | Temple |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R758-E | 2015-12-15 |  | 345 | 0 | 0 | 600 |  | Bell |  | Tier 4 |  |  |  | 3414, 13415, 13414 | Y | N |  |  | 2465 | 2376
13TPIT0064 | Rocky Mound Switching Station series capacitors | Install series capacitors for Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery part) |  | Rocky Mound Switching Station |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | C079-E | 2015-12-15 |  | 345 | 0 | 0 | 0 |  | Haskell |  | CREZ |  |  |  | 17012, 17013, 17014, 17015, 1421, 60515 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. | 2768 | 2644
15TPIT0058 | Permian Basin - Ward Gulf Tap - Wink 138 kV line | Upgrade existing 138 kV line |  | Permian Basin | Wink | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8189-E | 2015-12-15 |  | 138 | 0 | 16.5 | 0 |  | Ward | Winkler | Tier 4 |  |  |  | 1010, 1074, 1087 | Y | N |  |  | 3007 | 2834
15TPIT0078 | Tyler Northwest - Tyler 69 kV Line | Upgrade existing line |  | Tyler Northwest | Tyler | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6021-E | 2015-12-15 |  | 69 | 0 | 3 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3142, 3207 | Y | N |  |  | 3231 | 3062
15TPIT0082 | Collin - Custer (Brazos) 138 kV Line (Oncor's section) | Upgrade existing line |  | Collin | Custer (Brazos) | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R937-E | 2015-12-15 |  | 138 | 0 | 3.5 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 2364, 2365, 2566, 2567 | Y | N |  |  | 3378 | 3207
3874 | Morgan Creek - Cosden 138 kV Line | Rebuild existing aged 138 kV line |  | Morgan Creek | Cosden | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9001 | 2015-12-15 |  | 138 | 32.5 | 0 | 0 |  | Mitchell | Howard | Tier 4 |  |  |  | 1032, 1332 | Y | N |  |  | 4164 | 3874
3925 | Spraberry 138 kV Switching Station | Upgrade switching station and replace 138/69 kV autotransformer. |  | Spraberry |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8236 | 2015-12-15 |  | 138 | 0 | 0 | 100 |  | Midland |  | Tier 4 |  |  |  | 1329, 1330 | Y |  |  |  | 4225 | 3925
3934 | Spraberry - Garden City East 138 kV Line | Rebuild existing 69 kV line as a double-circuit 138 kV and 69 kV line |  | Spraberry | Garden City East | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8241 | 2015-12-15 |  | 138 | 33 | 33 | 0 |  | Midland | Glasscock | Tier 3 |  |  |  | 1220, 1328, 1225, 1329, 1337 | Y | N |  |  | 4236 | 3934
11TPIT0032B | NW Carrollton - Collin second 138 kV circuit | Rebuild existing NW Carrollton - Austin Ranch Junction line section as a double-circuit line |  | NW Carrollton | Austin Ranch Junction | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M368 | 2015-12-15 |  | 138 | 9.4 | 9.4 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 12376, 12519, 663, 2362, 2363, 2519 | Y | N | 2009-R13 |  | 4241 | 1055
15TPIT0025B | Monticello SES - Monticello Tap 138 kV line | Rebuild existing Monticello SES - Monticello Mining 138 kV line section |  | Monticello SES | Monticello Mining | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R906-E | 2015-12-15 |  | 138 | 0 | 5.5 | 0 |  | Titus | Franklin | Tier 4 |  |  |  | 1791, 1795 | Y | N |  |  | 4521 | 2643
4171 | Midessa - Midessa South 138 kV Line | Rebuild Midessa South - Midessa Sw. Sta. 138 kV Line on double-circuit 138 kV structures. Install a second circuit. |  | Midessa | Midessa South | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8254 | 2015-12-15 |  | 138 | 9.4 | 9.4 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 11159, 1059, 1120, 1124, 1138 | Y | N |  |  | 4524 | 4171
4172 | Odessa - Midessa South 138 kV Line | Rebuild the Odessa EHV - Odessa TI Tap and the Odessa TI Tap - Midessa South Sw. Sta. 138 kV line sections using double-circuit 138 kV structures. |  | Odessa | Midessa South | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8253 | 2015-12-15 |  | 138 | 10 | 0 | 0 |  | Ector | Midland | Tier 4 |  |  |  | 1027, 1124, 1127, 1126, 1128, 1137 | Y | N |  |  | 4525 | 4172
4173 | Odessa 138 kV Switching Station | Rebuild station as a ring bus | Construction schedule change | Odessa |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8251 | 2015-12-15 |  | 138 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  | 11126, 1122, 1126, 1127 | Y | N |  |  | 4526 | 4173
4204 | Wink 138 kV Switching Station | Upgrade 138 kV bus arrangement to breaker and a half |  | Wink |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8263 | 2015-12-15 |  | 138 | 0 | 0 | 0 |  | Winkler |  | Tier 4 |  |  |  | 1074, 1075 | Y | N |  |  | 4561 | 4204
4206 | Wink 69 kV Switching Station | Upgrade 69 kV bus arrangement to a ring bus and install a second 138/69 kV autotransformer. |  | Wink |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8264 | 2015-12-15 |  | 69 | 0 | 0 | 50 |  | Winkler |  | Tier 4 |  |  |  | 1075, 1074 | Y |  |  |  | 4563 | 4206
4347 | Renner 345 kV bus rearrangement | Convert 345 kV bus to a ring bus arrangement |  | Renner |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3099A | 2015-12-15 |  | 345 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 2354, 2355, 2359, 2358, 2361, 2513 | Y | N |  |  | 4720 | 4347
3267B | Rebuild ERioHondoTo Paredes to Central Avenue 138 kV line | Rebuild Paredes Switch to Central Avenue |  | Central Avenue | Paredes Switch | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2015-12-15 |  | 138 | 0 | 21 | 0 |  | Cameron | Cameron | Tier 4 |  |  |  | 5761, 5766 | Y | N |  |  | 4818 | 3267
15TPIT0083B | Collin - Arco (TMPA) 138 kV Line (Oncor's section) | Add second circuit to existing line from Krugerville to Arco (TMPA) | Construction schedule change | Krugerville | Arco (TMPA) | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R929 | 2015-12-15 |  | 138 | 5.7 |  | 0 |  | Denton | Denton | Tier 4 |  |  |  | 681, 2370 | Y | N |  |  | 4926 | 3216
15TPIT0034A | Freeport Area Upgrades and Conversion to 138kV | Upgrade Ckt.47 Velasco to Freeport | Delay in Project Schedule | Velasco | Freeport | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-23 |  | 69 | 0 | 4.5 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 42640, 43370 | Y | N |  | Substation Cost included in project 15TPIT0034B. | 2491 | 2389
15TPIT0034F | Freeport Area Upgrades and Conversion to 138kV | Upgrade Ckt.47 Surfside to Quintana | Delay in Project Schedule | Surfside | Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-24 |  | 69 | 0 | 2.1 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 43310, 43135 | Y |  |  | Substation Cost included in project 15TPIT0034B. | 3528 | 2389
15TPIT0034I | Freeport Area Upgrades and Conversion to 138kV | Upgrade Ckt.10 Velasco to Surfside to 138kV and rename to Ckt.59 | Delay in Project Schedule | Velasco | Surfside | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-25 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 43310, 43315, 43360, 43370 | Y |  |  | Substation Cost included in project 15TPIT0034B. | 3531 | 2389
15TPIT0034B | Freeport Area Upgrades and Conversion to 138kV | Convert Ckt.47 Velasco to Freeport to 138kV and rename to Ckt.59 | Delay in Project Schedule | Velasco | Freeport | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-26 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 42640, 42645, 43360 | Y | N |  |  | 2492 | 2389
15TPIT0034C | Freeport Area Upgrades and Conversion to 138kV | Upgrade Ckt.47 Freeport to Quintana to 138kV and rename to Ckt.59 | Delay in Project Schedule | Freeport | Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-27 |  | 69 | 0 | 3.9 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 42640, 43135 | Y | N |  | Substation Cost included in project 15TPIT0034B. | 2493 | 2389
15TPIT0034D | Freeport Area Upgrades and Conversion to 138kV | Convert Ckt.47 Freeport to Quintana to 138kV and rename to Ckt.59 | Delay in Project Schedule | Freeport | Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-28 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 43135, 43435, 42640, 42645, 43310 | Y | N |  | Substation Cost included in project 15TPIT0034B. | 2494 | 2389
15TPIT0034E | Freeport Area Upgrades and Conversion to 138kV | Convert Ckt.47 Freeport to Bryan to 138kV and rename to Ckt.59 | Delay in Project Schedule | Freeport | Bryan | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-29 |  | 138 | 0 | 2.4 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 42200, 44205, 42640, 42645 | Y |  |  | Substation Cost included in project 15TPIT0034B. | 3527 | 2389
17TPIT0004 | Frisco to Krugerville Second Circuit | Add second circuit from Frisco to Krugerville |  | Frisco | Krugerville | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12042 | 2015-12-30 |  | 138 | 12 | 0 | 0 |  | Collin | Denton | Tier 4 |  |  |  | 623, 638, 649, 1993, 2370 | Y | N |  |  | 2537 | 2432
15TPIT0034G | Freeport Area Upgrades and Conversion to 138kV | Convert Ckt.47 Surfside to Quintana to 138kV and rename to Ckt.59 | Delay in Project Schedule | Surfside | Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2015-12-30 |  | 138 | 0 | 0 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 43310, 43315, 43135, 43435 | Y |  |  | Substation Cost included in project 15TPIT0034B. | 3529 | 2389
13TPIT0151A | Gibbons Creek Upgrades Project | Gibbons Creek Upgrades Project Phase 1, adding of the 2x100 MVAr new reactors into the 345 kV North and South buses of Gibbons Creek substation |  | Gibbons Creek | Gibbons Creek |  |  | GARLAND | Paul Ricciardi PRicciardi@gpltexas.org 972-205-3476 |  | 2015-12-30 |  | 345 | 0 | 0 | 0 | -200,0 | Grimes | Grimes | Tier 3 |  |  |  | 967 | Y | N |  |  | 3930 | 3689
15TPIT3363A | Obrien Autotransformer Upgrade | Replace existing Obrien 600MVA autotransformer A1 with 800MVA auto. |  | Obrien |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 681 | 2015-12-30 |  | 345 | 0 | 0 | 800 |  | Fort Bend |  | Tier 4 |  |  |  | 49031, 49065, 44500, 44510 | Y | N |  | TPIT Cost Reflected in project 15TPIT3363B | 4253 | 3363
4578 | McCampbell: New substation Cut In | Customer to construct 138kV substation. Two 138kV circuits Cut-in to McCampbell substation. |  | Dupont SS | Whitepoint SS | Planned | 561 - 0729 | AEP TCC | Glen Reed 599-599-2664 | 3435 | 2015-12-30 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 80470, 80469 | Y | N |  |  | 4985 | 4578
05TPIT0065 | Highway 32-Wimberley | Construct a new 795 ACSR (220-MVA) 138-kV double circuit transmission line (approximately four miles) between the Highway 32(7546) and Wimberley(7496) substations. |  | Highway 32 | Wimberley | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2015-12-31 |  | 138 | 4 | 0 | 0 |  | Hays | Hays | Tier 4 |  |  |  | 7496, 7545, 7546 | Y | N |  |  | 998 | 997
15TPIT0024 | Lon Hill to Nelson Sharpe: Reconductor 345kV Line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Replace Series Capacitors at North Edinburg and Rio Hondo | Updated Trans Status and In-Service Date | Lon Hill | Nelson Sharpe | Under Construction | 071 - 0281 | AEP TCC | Michael Glueck 918-599-2664 | 3180 | 2015-12-31 |  | 345 | 0 | 20.81 | 0 |  | Nueces | Kleberg | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 8455, 85000 | Y | N |  |  | 1422 | 1421
13TPIT0157 | Cactus to Ft. Lancaster: Rebuild 69 kV line | Rebuild Cactus to Ft. Lancaster 69 kV line with 959.6 ACSS |  | Cactus | Ft. Lancaster | Planned | 569 - 0743 | AEP TNC | Eric Scott 918-599-2664 | 2573 | 2015-12-31 |  | 69 | 0 | 9.28 | 0 |  | Crockett | Pecos | Tier 4 |  |  |  | 6577, 6578, 6579 | Y | N |  |  | 1844 | 1801
16TPIT0023 | South McAllen - Stewart Road: Rebuild 138kV Line | Rebuild South McAllen - Stewart Road 138kV Line |  | South McAllen | Stewart Road | Under Construction | 601 - 0763 | AEP TCC | Aaron Schwerman gareed@aep.com 918-599-2664 | 3470 | 2015-12-31 |  | 138 | 0 | 9.8 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8371, 8758, 8951 | Y | N |  | 0 | 1945 | 1896
15TPIT0081 | Centerville Switch 138 kV Series Reactors | Increase size of series reactors |  | Centerville Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4105-E | 2015-12-31 |  | 138 | 0 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2439, 2450, 12439, 12450 | Y | N |  |  | 3230 | 3061
3441 | Falfurrias: Replace 138/69 kV autotransformer | Add 138/69 kV autotranformer capacity at Falfurrias |  | Falfurias |  | Planned | 632 - 0801 | AEP TCC | Brent Harris 918-599-2664 | 3511 | 2015-12-31 |  | 138 | 0 | 0 | 92 |  | Brooks |  | Tier 4 |  |  |  | 8508, 8510 | Y |  |  |  | 3641 | 3441
3636 | Welsh HVDC: Upgrade Station Svc and Install New Filter | Welsh HVDC Tie: Phase 2 Station Upgrades | PM, PVID, Prj Desc, In-Service Changes | WELSH HVDC Tie |  | Planned | 625 - 0793 | AEP TCC | Bill Clarke 918-599-2664 |  | 2015-12-31 |  | 345 | 0 | 0 | 0 | 0,100 | Titus |  | Tier 4 |  |  |  | 5925 | Y | Y |  |  | 3866 | 3636
3887 | Relocate Seguin Auto to Nixon | Relocate 138/69 kV Auto at Seguin to LCRA Nixon, associated GCBs, Bus |  | LCRA Nixon |  | Planned |  | LCRATSC/GVEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2015-12-31 |  | 138 | 0 | 0 | 40 |  | Gonzales |  | Tier 1 | 2012-09-01 | 2012-10-31 | 2013-03-10 | 7617 | Y | N |  |  | 4177 | 3887
15TPIT3363B | Obrien Autotransformer Upgrade | Move existing 600MVA Obrien auto A1 and parallel with existing auto A2. Rename autos 2A & 2B. | Delay in Project Schedule | Obrien |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 681 | 2015-12-31 |  | 345 | 0 | 0 | 0 |  | Fort Bend |  | Tier 4 |  |  |  | 49064, 49065, 44500, 44510 | Y | N |  |  | 4254 | 3363
3951 | TH Wharton to Fairbanks Ckt.81 |  |  | TH Wharton | Fairbanks | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-12-31 |  | 138 | 0 | 3.8 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45511, 45760 | Y | N |  |  | 4271 | 3951
3936B | Fairmont to Webster Ckt.06 Upgrades | Upgrade 138kV Ckt.06 NASA to Webster to increase thermal ratings |  | NASA | Webster | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-12-31 |  | 138 | 0 | 5.7 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 42970, 43500 | Y | N |  |  | 4533 | 3936
4183 | Jordan Cap Bank | Move existing Mont Belvieu cap bank #2 to Jordan 138kV substation |  | Jordan |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 95 | 2015-12-31 |  | 138 | 0 | 0 | 0 | 0,6.7 | Chambers |  | Tier 4 |  |  |  | 41114, 41111, 40855 | Y | N |  |  | 4538 | 4183
4184 | Fairmont to QUANAB Ckt.06 | Upgrade 138kV Ckt.06 Fairmont to QUANAB to increase thermal ratings. |  | Underwood | Fairmont/QUANAB | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 991 | 2015-12-31 |  | 138 | 0 | 6.2 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41310, 41631, 42610 | Y | N |  |  | 4539 | 4184
4185 | HO Clarke Partial Load Conversion (TR1) | Convert HO Clarke TR1 load to 138kV. Tap off of Ckt.09 HO Clarke to Brays |  | HO Clarke |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1112 | 2015-12-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47151, 47050, 47150 | Y | N |  |  | 4540 | 4185
4310 | Long Draw Reactor Addition | Add three breakers and two 100 MVAR reactors at WETT's Long Draw substation |  | Long Draw |  | Planned |  | WETT | Julius Horvath julius.horvath@windenergyoftexas.com 512-436-9585 |  | 2015-12-31 |  | 345 | 0 | 0 | 0 | 200,0 | Borden |  | Tier 4 |  |  |  | 59900 | Y | N |  |  | 4687 | 4310
4400 | Crestonio to Falfurrias: Raise forty-five 138 kV structures | Increase the MOT rating of the Lobo SS to Falfurrias 138kV line by raising 49 structures |  | Crestonio | Falfurrias | Planned | 702 - 0872 | AEP TCC | Mike Tallon 918-599-2664 | 3546 | 2015-12-31 |  | 138 | 0 | 43.9 | 0 |  | Duval | Brooks | Tier 4 |  |  |  | 8510, 8695 | Y |  |  |  | 4779 | 4400
4409 | Liston: Build new three breaker 138 kV station | Interconnect Los Vientos V Windfarm at Liston to connect LKHoward to the Bates to Garza 138 kV line |  | Liston |  | Planned | 698 - 0868 | AEP TCC | Bill Clarke waclarke@aep.com 918-599-2664 | 2900 | 2015-12-31 |  | 138 | 0 | 0 | 0 |  | Starr |  | Tier 4 |  |  |  | 8394, 8392, 8835 | Y |  |  |  | 4788 | 4409
4418 | HARBOR 138kV Substation | Loop Ckt. 59 Freeport to Quintana into new 138kV HARBOR substation |  | HARBOR | Freeport/Quintana | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-12-31 |  | 138 | 0.1 | 0 | 0 |  | Brazoria | Brazoria | Tier 4 |  |  |  | 43165, 42645, 43435 | Y | N |  |  | 4798 | 4418
4455 | Fayatte to Frelsburg Transmission Line Overhaul | Replace 10 full structures with OPGW capability. |  | Fayetteville | Frelsburg | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014183 | 2015-12-31 |  | 138 | 0 | 0 | 0 |  | Fayette | Colorado | Tier 4 |  |  |  | 7263, 7286 | Y | N |  |  | 4840 | 4455
4464 | Comal to Loop 337 Transmission Line Upgrade | Upgrade/Replace un-rated switches and CTs to remove MLSE elements. |  | Comal | Loop 337 | Planned |  | NBU | Greg Baumbach gbaumbach@nbutexas.com 830-629-8441 |  | 2015-12-31 |  | 138 | 0 | 0 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7176, 7456, 7459 | Y | N |  |  | 4850 | 4464
4540 | Tap 138kV St. Lawrence - Eiland line to create Carterville s |  |  | St. Lawrence | Eiland | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2016-01-01 |  | 138 | 0 | 0 | 0 |  | Glasscock | Glasscock | Tier 4 |  |  |  | 79560, 79620, 79625 | Y | N |  |  | 4942 | 4540
4544 | Upgrade sections of 138kV Buffalo - Grady line |  |  | Buffalo | Grady | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2016-01-01 |  | 138 | 0 | 14.3 | 0 |  | Martin | Martin | Tier 4 |  |  |  | 79510, 79508, 79550, 79549, 79564 | Y | N |  |  | 4946 | 4544
4363 | Miracle Lake 138 kV substation | Add new 138 kV substation between Cross and Pearsall |  | Miracle Lake |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-01-15 |  | 138 | 0 | 0 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 5700, 5707, 5895 | Y | N |  |  | 4737 | 4363
3845 | Hindes 138kV Substation: STEC Interconnect | Hindes 138kV Substation: STEC Interconnect |  | Dilley SS | San Miguel | Planned | 682 - 0837 | AEP TCC | Mike Tallon gareed@aep.com 918-599-2664 | 3531 | 2016-01-30 |  | 138 | 0 | 0 | 0 |  | La Salle |  | Tier 4 |  |  |  | 8215, 88215, 5704, 8212 | Y | N |  |  | 4129 | 3845
3665 | Texon Tap to Santa Rita: Rebuild 69kV line | Rebuild Texon Tap to Santa Rita 69 kV line with 959.6 ACSS/TW |  | Texon Tap | Santa Rita | Planned | 643 - 0812 | AEP TNC | Bill Clarke 918-599-2664 | 1460 | 2016-01-31 |  | 69 | 0.8 | 3.7 | 0 |  | Reagan | Reagan | Tier 4 |  |  |  | 6504, 6542, 6541, 6555 | Y | N |  |  | 4736 | 3665
16TPIT0026 | Lon Hill to Smith: Rebuild 69kV line | Rebuild Lon Hill - Smith 69kV Line with 1533.3 ACSR/TW conductor | Reformated project number to match other numbers | Lon Hill | Smith | Planned | 583 - 0739 | AEP TCC | William Clarke 918-599-2664 | 3462 | 2016-02-01 |  | 69 | 0 | 3.1 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8448, 8866, 80479, 80480 | Y | N |  | 0 | 1821 | 1779
14TPIT0080 | Oran to Advance Rebuild | Rebuild Oran to Advance with 959 ACSS, 138 kV construction (operate at 69 kV) |  | Oran | Advance | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12010 | 2016-02-01 |  | 69 | 0 | 13.7 | 0 |  | Palo Pinto | Parker | Tier 4 |  |  |  | 518, 519, 785 | Y | N |  |  | 2311 | 2238
3796 | Pachal 69 kV station | Add new station for AEP load on 69 kV |  | Pachal |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-02-01 |  | 69 | 0 | 0 | 0 |  | Frio |  | Tier 4 |  |  |  | 5845, 5842, 5893 | Y | N |  |  | 4047 | 3796
3681 | TH Wharton to Addicks Ckt.71 Sub Upgrade | Upgrade substation equipment at TH Wharton and Addicks to increase thermal ratings for 345kV Ckt.71. |  | TH Wharton | Addicks | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-02-28 |  | 345 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 45500, 45600 | Y | N |  |  | 4268 | 3681
16TPIT0042 | Uvalde Station: Add 2nd 138/69 kV Auto | Upgrade138/69 kV Auto at Uvalde Station | Transmission status, Contact and Cost Update | UVALDE | UVALDE | Under Construction | 663-0832 | AEP TCC | Rick McCraken GAREED@AEP.COM 918-599-2664 | 3480 | 2016-03-01 |  | 138 |  |  | 130 |  | Uvalde |  | Tier 4 |  |  |  | 8231, 8234 | Y | N |  |  | 3741 | 3534
17TPIT0007 | Gillespie to Pointer: Rebuild 69 kV line | Rebuild Gillespie to Pointer 69 kV line with 959.6 ACSR |  | Gillespie | Pointer | Planned | 568 - 0742 | AEP TNC | Aaron Schwerman 918-599-2664 | 2579 | 2016-03-31 |  | 69 | 0 | 6.7 | 0 |  | Knox | Knox | Tier 4 |  |  |  | 6112, 6113, 60346 | Y | N |  |  | 2912 | 2757
3676 | Foxtail: Build 345 kV station | Interconnect Green Pastures Wind Farm at Foxtail to connect Green Pastures and Vertigo to the Oklaunion to Mulberry Creek 345 kV line |  | Foxtail |  | Planned | 648 - 0817 | AEP TNC | Gregory Gibbs 918-599-2664 | 1813 | 2016-03-31 |  | 345 | 0 | 0 | 0 |  | Baylor |  | Tier 4 |  |  |  | 6076, 6100, 6235 | Y | N |  |  | 3913 | 3676
3982 | EF 90 Corpus Tank Farm | EF 90 Corpus Tank Farm - Kepler 69kV substation: Costruct substation | New | Koch Upriver | Valero West | Planned | 615 - 0783 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 3498 | 2016-03-31 |  | 69 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8240, 8469, 8477 | Y | N |  |  | 4307 | 3982
13TPIT0124 | Airport 69 kV Substation | Build new load serving station in the 69 kV line from Lone Tree to Twin Pines Switch. |  | Airport |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-04-01 |  | 69 | 0 | 0 | 0 |  | Victoria |  | Tier 4 |  |  |  | 5601, 5600, 5602 | Y | N |  |  | 1554 | 1538
15TPIT0051 | Kenedy Switch - Nixon - Seguin Transmission Line Upgrade | Upgrade the 54.2 mile Kenedy Switch (8184) - Nixon (78580) - Deer Creek (New) (7595) from 69kV to 138kV 795 ACSR Drake, 223 MVA. |  | Kenedy Switch | Deer Creek | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1012640 | 2016-04-01 |  | 138 | 0 | 54.2 | 0 |  | Karnes | Guadalupe | Tier 1 | 2012-09-01 | 2012-10-30 | 2013-03-31 | 78580 | Y | N |  |  | 3969 | 3725
3503 | Rebuild Seguin-Deer Creek to 138kV | Rebuild 6/1 miles (Capote to Deer Creek, back to Seguin is 138) single Ckt 69 to 138 kV, 795 ACSR, terminals at Seguin and Deer Creek. (This portion of the T-377 line segment will be out of service from Oct 1, 2015 - Mar 31, 2016) |  | Seguin | Deer Creek | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-04-30 |  | 138 | 0 | 6.1 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7228 | Y | N |  |  | 3710 | 3503
15TPIT0055 | Naval Base Station: Add 138/69 kV Auto | Construct new 138 kV line and add tranformation at Naval Base to remove contingency overloads during off-peak maintenance | In Service Update | NAVAL BASE |  | Under Construction | 607 - 0648 | AEP TCC | MICHAEL GLUECK GAREED@AEP.COM 918-599-2664 | 3485 | 2016-04-30 |  | 138 |  |  | 220 |  | Nueces |  | Tier 1 | 2012-07-15 | 2012-12-20 | 2013-01-04 | 8997, 8495 | Y | N |  |  | 3721 | 3514
4428 | CAMDEN 138kV Substation | Loop Ckt.26 SINTEK to Velasco into new 138kV CAMDEN substation |  | CAMDEN | SINTEK/Velasco | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-04-30 |  | 138 | 0 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43365, 43240, 43360 | Y | N |  |  | 4812 | 4428
13TPIT0151B | Gibbons Creek Upgrades Project | Gibbons Creek Upgrades Project Phase 2, replacing and upgrading of the Gibbons Creek auto transformer #1 to 600 MVA as well as removing its 2 reactors at tertiary side from the system |  | Gibbons Creek | Gibbons Creek |  |  | GARLAND | Paul Ricciardi PRicciardi@gpltexas.org 972-205-3476 |  | 2016-05-01 |  | 345 | 0 | 0 | 600 |  | Grimes | Grimes | Tier 3 |  |  |  | 967, 964, 965 | Y | N |  |  | 3931 | 3689
13TPIT0151C | Gibbons Creek Upgrades Project | Gibbons Creek Upgrades Project Phase 3, removing of the Gibbons Creek auto transformer #3 from the system and using as for a spare transformer |  | Gibbons Creek | Gibbons Creek |  |  | GARLAND | Paul Ricciardi PRicciardi@gpltexas.org 972-205-3476 |  | 2016-05-01 |  | 345 | 0 | 0 | 0 |  | Grimes | Grimes | Tier 3 |  |  |  | 969, 967, 964 | Y | N |  |  | 3932 | 3689
4179 | Tanner 138kV Substation | Build new 138kV Tanner distribution substation. Double tap off Ckt.24 Satsuma - Addicks and Ckt.76 Satsuma - Addicks. |  | Tanner |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-01 |  | 138 | 1.9 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 46311, 46312, 45610, 45611, 46300, 46302 | Y | N |  |  | 4534 | 4179
4398 | Razorback: Build new three breaker 138 kV station | Construct new Razorback station along the Uvalde to Castroville (STEC) 138 kV line |  | Uvalde | Castroville STEC | Planned | 611 - 0779 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 3494 | 2016-05-01 |  | 138 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 8241, 80241, 5083, 8234 | Y | N |  |  | 4777 | 4398
3966 | Zorn to Seguin Transmission Line Upgrade | Upgrade the 13.2 miles Zorn (7180) - York Creek (7227) - Seguin (7228) 138kV transmission line to single 1433 Merrimack conductor (478 MVA). |  | Zorn | York Creek - Seguin | Planned | ERCOT RTP # 2013-R83 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014341 | 2016-05-05 |  | 138 | 0 | 13.2 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7180, 7227, 7228 | Y | N |  |  | 4287 | 3966
09TPIT0122 | Shamburger - Tyler NW 138 kV line | Upgrade existing 138 kV line |  | Shamburger | Tyler NW | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6001-E | 2016-05-15 |  | 138 | 0 | 6.3 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3104, 3141 | Y | N | 2009-E6 |  | 1243 | 1240
06TPIT0047 | Elkton - Tyler West 138 kV line | Upgrade existing 138 kV line |  | Elkton | Tyler West | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6023-E | 2016-05-15 |  | 138 | 0 | 4 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3106, 3139 | Y | N |  |  | 1434 | 1433
14TPIT0056 | Northaven - Welch 138 kV line | Upgrade existing line |  | Northaven | Welch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4088-E | 2016-05-15 |  | 0 | 0 | 3 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2657, 2658, 2660, 2661 | Y | N |  |  | 2598 | 2493
14TPIT0055 | Seagoville - Wilmer 138 kV line | Upgrade existing line |  | Seagoville | Wilmer | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4081-E | 2016-05-15 |  | 0 | 0 | 10.9 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2434, 3076, 3077, 3079, 3083 | Y | N |  |  | 2599 | 2494
13TPIT0059 | Cedar Crest - Industrial 138 kV line | Upgrade existing line |  | Cedar Crest | Industrial | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4072-E | 2016-05-15 |  | 138 | 0 | 3.2 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2494, 2976, 2981 | Y | N | 2009-R23 |  | 2600 | 2495
13TPIT0113 | Renner 345/138 kV autotransformer | Replace existing 345/138 kV autotransformer with larger autotransformer |  | Renner |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3099B | 2016-05-15 |  | 345 | 0 | 0 | 600 |  | Collin |  | Tier 4 |  |  |  | 2359, 2358, 16358 | Y | N |  |  | 2826 | 1300
16TPIT0052 | Cedar Crest - South Oak Cliff 138 kV line | Upgrade existing line |  | Cedar Crest | South Oak Cliff | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4089-E | 2016-05-15 |  | 138 | 0 | 1.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2493, 2494, 3023, 3024 | Y | N |  |  | 3235 | 3066
17TPIT0023 | Northwest Carrollton - Norwood 138 kV Line | Upgrade existing double-circuit Northwest Carrollton - Carrollton line section |  | Northwest Carrollton | Carrollton | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4110-E | 2016-05-15 |  | 138 | 0 | 11.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2362, 2363, 2535, 2536, 2537, 2538, 2539 | Y | N |  |  | 3258 | 3089
14TPIT0012 | Mountain Creek - Norwood 138 kV line | Upgrade existing line |  | Mountain Creek | Norwood | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4074-E | 2016-05-15 |  | 138 | 0 | 7.2 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2407, 2412, 2804, 2805, 12804 | Y | N |  |  | 3263 | 3094
16TPIT0058 | Lufkin Switch - Lufkin 138 kV line | Upgrade existing line |  | Lufkin Switch | Lufkin | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6038-E | 2016-05-15 |  | 138 | 0 | 2.8 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  | 3118, 3340 | Y | N |  |  | 3281 | 3112
16TPIT0065 | Gresham Road - Nacogdoches 138 kV line | Upgrade existing line |  | Gresham Road | Nacogdoches | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6035-E | 2016-05-15 |  | 138 | 0 | 21.3 | 0 |  | Cherokee | Nacogdoches | Tier 3 |  |  |  | 3299, 3300, 3301, 3303 | Y | N |  |  | 3284 | 3115
17TPIT0029 | Tyler Grande - Tyler East 138 kV Line | Upgrade existing line |  | Tyler Grande | Tyler East | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6017-E | 2016-05-15 |  | 138 | 0 | 8.2 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3143, 3212, 3214, 3211, 3213 | Y | N |  |  | 3288 | 3119
16TPIT0059 | Midland East 138 kV capacitor | Install shunt capacitor | Studies indicate timing of project should be changed | Midland East |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8158-E | 2016-05-15 |  | 138 | 0 | 0 | 0 | 0,92 | Midland |  | Tier 4 |  |  |  | 1023 | Y | N |  |  | 3344 | 3173
17TPIT0011 | Carroll Springs 69 kV capacitors | Install shunt capacitor |  | Carroll Springs |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6041-E | 2016-05-15 |  | 69 | 0 | 0 | 0 | 0,27.6 | Anderson | Anderson | Tier 4 |  |  |  | 3270 | Y | N |  |  | 3591 | 3393
14TPIT0011 | Midessa - Windwood - Midland East 138 kV Line | Upgrade existing line |  | Midessa | Midland East | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8148-E | 2016-05-15 |  | 138 | 0 | 10.4 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1023, 1059, 1116, 1117 | Y | N |  |  | 3631 | 3431
16TPIT0044 | Brownwood 69 kV capacitors | Install shunt capacitor |  | Brownwood |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R782-E | 2016-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Brown |  | Tier 4 |  |  |  | 1662 | Y | N |  |  | 3694 | 3487
4210 | Paris Switch 345/138 kV autotransformer | Replace existing autotransformer |  | Paris Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R959 | 2016-05-15 |  | 345 | 0 | 0 | 600 |  | Lamar |  | Tier 4 |  |  |  | 1692, 1693, 1686 | Y | N |  |  | 4571 | 4210
4211 | Rivercrest 138/69 kV autotransformer | Replace existing autotransformer |  | Rivercrest Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R950 | 2016-05-15 |  | 138 | 0 | 0 | 100 |  | Red River |  | Tier 4 |  |  |  | 1780, 1781, 1787 | Y | N |  |  | 4572 | 4211
4215 | Midessa South - Spraberry 138 kV Line | Rebuild Spraberry - Odessa TI Tap 138 kV line section using double-circuit 138 kV structures. Install a second circuit from Midessa South to Spraberry |  | Midessa South | Spraberry | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8255 | 2016-05-15 |  | 138 | 16 | 0 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1124, 1329 | Y | N |  |  | 4576 | 4215
4220 | Screwbean 138 kV capacitors | Install shunt capacitors |  | Screwbean |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8224 | 2016-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Culberson |  | Tier 4 |  |  |  | 1095 | Y | N |  |  | 4590 | 4220
4221 | Polecat Switch 138 kV capacitors | Install shunt capacitors |  | Polecat Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8217 | 2016-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Glasscock |  | Tier 4 |  |  |  | 11337 | Y | N |  |  | 4591 | 4221
4222 | Odessa North 138 kV capacitors | Install shunt capacitors |  | Odessa North |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8216 | 2016-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Ector |  | Tier 4 |  |  |  | 1122 | Y | N |  |  | 4592 | 4222
4223 | Midkiff 138 kV capacitors | Install shunt capacitors |  | Midkiff |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8214 | 2016-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Upton |  | Tier 4 |  |  |  | 1210 | Y | N |  |  | 4593 | 4223
4224 | Chalk 69 kV capacitors | Install shunt capacitors |  | Chalk |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8219 | 2016-05-15 |  | 69 | 0 | 0 | 0 | 0,27.6 | Howard |  | Tier 4 |  |  |  | 1352 | Y | N |  |  | 4594 | 4224
4225 | Big Spring West 138 kV capacitors | Install shunt capacitors |  | Big Spring West |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8215 | 2016-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Howard |  | Tier 4 |  |  |  | 1324 | Y | N |  |  | 4595 | 4225
4229 | Edwards 138 kV capacitors | Install shunt capacitors |  | Edwards |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8256 | 2016-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Ector |  | Tier 4 |  |  |  | 1110 | Y | N |  |  | 4600 | 4229
4237 | Means - Fullerton 69 kV Line | Rebuild existing Means - Fullerton 69 kV line section as a double-circuit line with a 69 kV circuit and a 138 kV circuit |  | Means | Fullerton | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8161 | 2016-05-15 |  | 69 | 15.1 | 15.1 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1284, 1159, 1274, 1285 | Y | N |  |  | 4610 | 4237
4242 | Odessa - Odessa North 138 kV Line | Upgrade existing line |  | Odessa | Odessa North | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8211 | 2016-05-15 |  | 138 | 0 | 7.2 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1122, 1127 | Y | N |  |  | 4615 | 4242
4243 | Holt - XTO University 138 kV Line | Upgrade existing line |  | Holt | XTO University | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8212 | 2016-05-15 |  | 138 | 0 | 9.8 | 0 |  | Ector | Andrews | Tier 4 |  |  |  | 1141, 1281, 1283 | Y | N |  |  | 4616 | 4243
4251 | Everman - Wedgwood 138 kV Line | Upgrade existing double-circuit line |  | Everman | Wedgwood | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5210 | 2016-05-15 |  | 138 | 0 | 18 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1883, 1967, 2184, 2185, 2190, 2191, 2192, 2193, 2194, 2195 | Y | N |  |  | 4622 | 4251
4274 | Navarro - Corsicana 69 kV Line | Upgrade existing line |  | Navarro | Corsicana | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R793 | 2016-05-15 |  | 69 | 0 | 12.5 | 0 |  | Navarro | Navarro | Tier 4 |  |  |  | 3468, 3475, 3479, 3480, 13468 | Y | N |  |  | 4648 | 4274
4277 | Lott 69 kV capacitors | Install shunt capacitors |  | Lott |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R791 | 2016-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Falls |  | Tier 4 |  |  |  | 3642 | Y | N |  |  | 4652 | 4277
17TPIT0013 | Tyler Grande Switch shunt reactors | Install shunt reactors on tertiary of 345/138 kV autotransformer |  | Tyler Grande |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6047 | 2016-05-15 |  | 13.8 | 0 | 0 | 0 | 0,-75 | Smith | Smith | Tier 4 |  |  |  | 3338 | Y | N |  |  | 4663 | 4286
17TPIT0019 | Forney - Royse 138 kV Line | Upgrade existing line |  | Forney | Royse | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4111-E | 2016-05-15 |  | 138 | 0 | 18.32 | 0 |  | Kaufman | Rockwall | Tier 4 |  |  |  | 2438, 2471, 2710, 2711, 2712 | Y | N |  |  | 4664 | 3086
16TPIT0050 | Northaven - Preston North 138 kV Line | Upgrade existing line |  | Northaven | Preston North | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4108-E | 2016-05-15 |  | 138 | 0 | 5.9 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2597, 2614, 2616, 2659 | Y | N |  |  | 4670 | 3065
16TPIT0061 | Norwood - East Levee 138 kV Line | Upgrade existing line |  | Norwood | East Levee | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4107-E | 2016-05-15 |  | 138 | 0 | 7 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2405, 2811, 2813, 2815, 2819, 2482, 2814, 2823 | Y | N |  |  | 4671 | 3067
4299 | Big Brown - Navarro Switch 345 kV Line | Upgrade existing double-circuit line |  | Big Brown | Navarro Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R1705 | 2016-05-15 |  | 345 | 0 | 62 | 0 |  | Freestone | Navarro | Tier 4 |  |  |  | 3380, 68091 | Y | N |  |  | 4680 | 4299
4354 | Collin 138 kV series reactor | Install 138 kV series reactor on second 345/138 kV autotransformer |  | Collin |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R960 | 2016-05-15 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 29556, 29555, 2372, 29578 | Y | N |  |  | 4727 | 4354
4367 | Screwbean - Culberson 138 kV Line | Rebuild existing 138 kV line |  | Culberson | Screwbean | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8274 | 2016-05-15 |  | 138 | 0 | 25 | 0 |  | Culberson | Culberson | Tier 4 |  |  |  | 1095, 1096, 1097 | Y | N |  |  | 4741 | 4367
4527 | Fullerton Switching Station | Construct new switching station |  | Fullerton |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8277 | 2016-05-15 |  | 69 | 0 | 0 | 0 |  | Andrews |  | Tier 4 |  |  |  | 1272, 1274, 1284 | Y | N |  |  | 4927 | 4527
17TPIT0032 | Fisher Road 345/138 kV autotransformer | Install second autotransformer |  | Fisher Road |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R931-E | 2016-05-16 |  | 345 | 0 | 0 | 600 |  | Wichita |  | Tier 4 |  |  |  | 11426, 1425, 1426 | Y | N |  |  | 3388 | 3215
15TPIT0035A | Velasco to West Columbia Upgrades and Conversion to 138kV | Convert Retrieve substation to 138kV and energize with existing Ckt. 02 Lake Jackson to West Columbia. Upgrade Ckt. 02 Lake Jackson to Retrieve and parallel bundle a portion of the line with converted 69kV Ckt.47 Velasco to West Columbia. | Delay in project schedule | Lake Jackson | Retrieve | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-27 |  | 138 | 0 | 5.34 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 43140, 43145, 43370, 42640, 42880, 43380, 43390, 49032, 43360 | Y | N |  |  | 2485 | 2388
3824 | Dow: Install 2nd 800MVA Autotransformer | Install 2nd DOW-Velasco 800MVA autotransformer at DOW substation |  | DOW |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 993 | 2016-05-27 |  | 345 | 0.5 | 1.7 | 800 |  | Brazoria |  | Tier 3 | 2014-03-21 | 2014-04-30 |  | 42511, 49069, 43360, 42500 | Y | N |  |  | 4106 | 3824
15TPIT0035B | Velasco to West Columbia Upgrades and Conversion to 138kV | Upgrade Ckt. 02 Retrieve to West Columbia. Parallel bundle a portion of the line with converted 69kV Ckt.47 Velasco to West Columbia. | Delay in project schedule | Retrieve | West Columbia | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-28 |  | 138 | 0 | 11.9 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 43145, 43380 | Y | N |  | Cost included in project 15TPIT0035A. | 2486 | 2388
4424A | Gable Street Upgrades | Convert to 138kV and reconfigure existing Ckt.46 Gable Street to Blodgett tap to create new 138kV Ckt.70 Gable Street to East Side. |  | Gable Street | East Side | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-28 |  | 138 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47522, 47600, 47630, 47640 | Y | N |  |  | 4805 | 4424
15TPIT0035C | Velasco to West Columbia Upgrades and Conversion to 138kV | Parallel bundle a portion of Ckt. 02 Hofman to Lake Jackson with converted 69kV Ckt.47 Velasco to West Columbia. | Delay in project schedule | Hofman | Lake Jackson | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-29 |  | 138 | 0 | 3.9 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 42810, 42880 | Y | N |  | Cost included in project 15TPIT0035A. | 2487 | 2388
4424B | Gable Street Upgrades | Install 2nd autotransformer (200MVA) at Gable Street substation. |  | Gable Street |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-29 |  | 138 | 0 | 0 | 200 |  | Harris |  | Tier 4 |  |  |  | 49056, 47630, 47640 | Y | N |  | Cost included in main project. | 4806 | 4424
15TPIT0035D | Velasco to West Columbia Upgrades and Conversion to 138kV | Parallel bundle a portion of Ckt. 02 BASF to Hofman with converted 69kV Ckt.47 Velasco to West Columbia. | Delay in project schedule | BASF | Hofman | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-30 |  | 138 | 0 | 0.84 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 42150, 42810 | Y | N |  | Cost included in project 15TPIT0035A. | 2488 | 2388
4421A | Rothwood Substation Upgrades | Add 2nd 800MVA autotransformer at Rothwood substation |  | Rothwood |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-30 |  | 345 | 0 | 0 | 800 |  | Harris |  | Tier 4 |  |  |  | 49045, 46290, 46295 | Y | N |  |  | 4801 | 4421
4424C | Gable Street Upgrades | Install in-series reactor at Gable Street substation on Ckt.32 Gable Street to Downtown |  | Gable Street | Downtown | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-30 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47510, 47640 | Y | N |  | Cost included in main project. | 4807 | 4424
4451 | Plum to Flatonia Transmission Line Upgrade | Replace existing conductor and shield wire to achieve conductor rating of 221 MVA for the 0.45 mile portion of T133 and T122 between Flatonia substation and structure 1/3. |  | Plum | Flatonia | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2016-05-30 |  | 138 | 0 | 0.45 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7248, 7274 | Y | N |  |  | 4836 | 4451
4460 | Hidden Valley Cut-In to McNeil to Marshall Ford | Construct a new 138-kV bus with tie breaker to existing Austin Energy bus at Hidden Valley substation. Cut McNeil (7334) to Marshall Ford (7356) 138-kV line into the LCRA TSC 138-kV bus at Hidden Valley. |  | Hidden Valley | McNeil/Marshall Ford | Planned |  | LCRATSC/AEN | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2016-05-30 |  | 138 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 78207, 7334, 7356, 9207 | Y | N |  |  | 4845 | 4460
12TPIT0084 | Lookout 138 kV new substation and connections | Lookout 138 kV new substation and its connections to Apollo and to Firewheel | On Hold For Funding | Apollo | Firewheel | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2016-05-31 |  | 138 | 4.1 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 828, 12683, 802, 821 | Y | N |  |  | 765 | 764
15TPIT0035E | Velasco to West Columbia Upgrades and Conversion to 138kV | Parallel bundle a portion of Ckt. 02 Brazosport to Velasco with converted 69kV Ckt.47 Velasco to West Columbia. | Delay in project schedule | Brazosport | Velasco | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-31 |  | 138 | 0 | 1.32 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 42210, 43222 | Y | N |  | Cost included in project 15TPIT0035A. | 2489 | 2388
06TPIT0068 | Hamilton Road to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System |  | HAMILTON ROAD | PICACHO | Conceptual | 301-0449 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 1544 | 2016-05-31 |  | 138 |  | 8.76 |  |  | Val Verde | Val Verde | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8255, 8684 | Y | N |  |  | 3742 | 3535
3760 | Asherton to Carrizo Springs: 69 kV Transmission Line Rebuild | Rebuild 69 kV line from Asherton to Carrizo Spring |  | ASHERTON | CARRIZO SPRING | Under Construction | 661-0830 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 3526 | 2016-05-31 |  | 69 |  | 8.3 |  |  | Dimmit | Dimmit | Tier 4 |  |  |  | 8244, 8280 | Y | N | NA |  | 4005 | 3760
3901 | Lobo to Freer: Rebuild 69 kV line | Rebuild Lobo to Freer 69 kV line with 959.6 ACSS/TW |  | Lobo | Freer | Conceptual | 677 - 0846 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2596 | 2016-05-31 |  | 69 | 0 | 49.8 | 0 |  | Webb | Duval | Tier 3 |  |  |  | 8505, 80222 | Y | N |  |  | 4196 | 3901
3546 | Edroy 69 kV Station: Install Series Reactor | Construct a 15-ohm series reactor at Edroy on the terminal to Mathis 69 kV | Added ERCOT RPG estimate, changed Tier, ransmission status. | Edroy |  | Under Construction | 692-0862 | AEP TCC | Dave Goetz gareed@aep.com 918-599-2664 | 3527 | 2016-05-31 |  | 69 |  |  |  | 15,0 | San Patricio |  | Tier 1 | 2012-08-31 | 2012-12-27 | 2013-04-05 | 8424, 8407, 8408 | Y | N |  |  | 4198 | 3546
4186 | University 138kV Load Conversion | Convert University TR2 & TR3 load to 138kV. |  | University |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1123 | 2016-05-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 47750, 47752 | Y | N |  |  | 4541 | 4186
4187 | LaMarque Substation Expansion & Circuit Reconfigurations | Expand LaMarque 138kV substation and loop Ckt.93 into LaMarque to create PHR - LaMarque and LaMarque - West Galveston circuits. Reconfigure circuits south of LaMarque. |  | LaMarque | Hitchcock/West Galv | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 859 | 2016-05-31 |  | 138 | 0.5 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 42670, 42800, 42861, 43355, 43290, 43401, 43500 | Y | N |  |  | 4542 | 4187
4188 | Bertwood to Hardy Ckt.95 Upgrades | Upgrade 138kV Ckt.95 Bertwood to Hardy to increase thermal ratings. |  | Bertwood | Hardy | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1068 | 2016-05-31 |  | 138 | 0 | 7.5 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 40180, 45840 | Y | N |  |  | 4543 | 4188
4200 | Sage: Build 69 kV station | Construct new 69 kV in and out substation off the Crane loop, and demolish Crane Gulf #1 | Company Contact and Schedule Update | Sage |  | Planned | 697 - 0867 | AEP TNC | Eric Scott 918-599-2664 | 2266 | 2016-05-31 |  | 69 | 0 | 0 | 0 |  | Crane |  | Tier 4 |  |  |  | 6604, 6608 | Y | N |  |  | 4556 | 4200
3666 | Atlantic Best Tap to Santa Rita: Rebuild & convert to 138 kV | Rebuild Atlantic Best Tap to Santa Rita 69 kV line with 959.6 ACSS/TW and convert Santa Rita to 138 kV by rerouting the Big Lake to North McCamey line through Santa Rita | Project Title Update | Altantic Best Tap | Santa Rita | Planned | 644 - 0813 | AEP TNC | Bill Clarke 918-599-2664 | 1461 | 2016-05-31 |  | 138 | 0.7 | 5 | 0 |  | Reagan | Reagan | Tier 4 |  |  |  | 6504, 6541, 6542, 6555, 60361, 6536, 6544, 6589, 76032 | Y | N |  |  | 4634 | 3666
4421B | Rothwood Substation Upgrades | Reconfigure existing 138kV Rothwood circuits to create new Ckt.22 loop from Rothwood to Rayford to Springwood to Rothwood. |  | Rothwood | Rayford/Springwood/Rothwood | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-31 |  | 138 | 0.1 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 46051, 46261, 46270, 46295 | Y | N |  |  | 4802 | 4421
4422 | Stewart 10MVAr Reactor Bank | Install 10MVAR shunt reactor at Stewart substation. |  | Stewart |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-31 |  | 138 | 0 | 0 | 0 | 10,0 | Galveston |  | Tier 4 |  |  |  | 43290 | Y | N |  |  | 4803 | 4422
4424D | Gable Street Upgrades | Remove East Side capacitor bank. |  | East Side |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-31 |  | 138 | 0 | 0 | 0 | 0,-93.33 | Harris |  | Tier 4 |  |  |  | 47610, 47600, 47750 | Y | N |  | Cost included in main project. | 4808 | 4424
4462 | Clear Springs 345/138-kV Auto Transformer Addition | Energize the standby 345/138-kV 478 MVA auto transformer at Clear Springs substation. |  | Clear Springs |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2016-05-31 |  | 345 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7050, 7680, 77680 | Y | N |  |  | 4848 | 4462
4463 | Kendall Bus Tie Configuration | Close the Kendall bus tie between Kendall MB (7150) and (7152) |  | Kendall |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2016-05-31 |  | 138 | 0 | 0 | 0 |  | Kendall |  | Tier 4 |  |  |  | 7150, 7152 | Y | N |  |  | 4849 | 4463
4491 | Marconi: Build new 138 kV temporary tap | Interconnect San Roman Windfarm at Temporary Tap to connect San Roman to the Port Isabel to Laureles 138 kV line |  | Port Isabel | Laureles | Planned | 711 - 0882 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2905 | 2016-05-31 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8262, 5756, 8338 | Y | N |  |  | 4885 | 4491
4493 | Pharr 138 kV Loop | McColl Road & North McAllen to Pharr: Reroute 138 kV Line |  | MCCOLL ROAD & NORTH MCALLEN | PHARR | Under Construction | 3548 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 704-0874 | 2016-05-31 |  | 138 | 2.2 | 0 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 8368, 8372, 8380, 8908 | Y | N |  |  | 4887 | 4493
4525 | HO Clarke to Heights Ckt.34 | Upgrade 69kV Ckt.34 HO Clarke to Heights to increase thermal ratings |  | HO Clarke | Heights | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2016-05-31 |  | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47165, 47680 | Y | N |  |  | 4922 | 4525
09TPIT0037 | Blossom - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Harmony Hills to Skyline line | Delayed due to budget constraint | Blossom | Harmony Hills-Skyline | Planned | T-0178 | CPS | Ulrich Skerhut UKSkerhut@cpsenergy.com 210-353-2923 | S-0602 | 2016-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5022, 5195, 5368 | Y | N |  | There are no transformers associated with this project | 950 | 949
16TPIT0011 | JT Deely to Streich - 138 kV Substation Equipment Upgrade | Upgrade terminals at JT Deely and Streich Rd. to ensure a 2420 A rating and remove existing MLSE on JT Deely to Streich 138 kV transmission line |  | JT Deely | Streich Rd | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0674 | 2016-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5110, 5417 | Y | N |  | There are no transformers associated with this project | 977 | 976
07TPIT0050 | Dunlap to Techridge 138kV Circuit Relocation | This project will reroute the existing Ckt 975 Dunlap-Techridge from near the intersection of Howard Lane and Dessau Road to the Techridge substation. The reroute will use 3000 amp bundled 795 ACSS Drake conductor. |  | Dunlap Substation | Techridge Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | PLAN_117_P071 | 2016-06-01 |  | 138 | 0 | 2.7 | 0 |  | Travis | Travis | Tier 2 | 2009-01-26 | 2009-07-21 |  | 9045, 9190 | Y | N |  |  | 1014 | 1013
07TPIT0060 | Howard Lane to Techridge Reconductor | The project re-conductors Circuit 1004 (Techridge to Howard Lane) using 795 ACSS Drake conductors to increase the capacity to 4000 Amp. |  | Howard Lane Substation | Techridge Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | PLAN_117_P067 PLAN_117_P194 | 2016-06-01 |  | 138 | 0 | 1.72 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9190, 9217 | Y | N |  |  | 1029 | 1028
09TPIT0012 | Hill Country to Skyline - 345 kV 2nd Circuit | Build second 345 kV line from Hillcountry to Skyline. The second circuit will be installed on existing transmission structures |  | Hill Country | Skyline | Planned | S-0470 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0052 | 2016-06-01 |  | 345 | 11 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5211, 5371 | Y | N |  | There are no transformers associated with this project | 1404 | 1403
10TPIT0095 | VH Braunig - Grandview 138kV Line Reroute | Reroute VH Braunig - Grandview to become VH Braunig - Coliseum Rd | Delayed due to Rail Road permit | VH Braunig | Grandview |  | S-0554 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0130 | 2016-06-01 |  | 138 | 2.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5095, 5175 | Y | N |  | There are no transformers associated with this project | 1465 | 1464
14TPIT0071 | Princeton South - New Substation | Build a new 138-12.47 kV substation to accommodate load growth in Princeton. |  |  |  | Planned | 16TPIT0005 | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE02815 | 2016-06-01 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 37295 | N | N |  |  | 2063 | 2011
15TPIT0030 | Mainland - New Substation | Build a new 138-12.47 kV substation to accommodate load growth along I45 between Texas City and Dickinson. Cut TNMP's Freeway Park - Alvin 138 kV line into the new substation. |  | Mainland |  | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2016-06-01 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  | 38830, 38820, 39030 | Y | N |  |  | 2089 | 2025
16TPIT0030 | New 345kV line from Loma Alta to N Edinburgh | Construct a new 345 kV transmission line from N.Edinburg to Loma Alta (~106.5 mi) and station upgrades | New Changed Dollars to include the station costs associated with the project (Approved by RPG, see comments for breakout) | Loma Alta | N Edinburgh | Planned |  | SLU |  |  | 2016-06-01 |  | 345 | 106.5 | 0 | 0 |  | Cameron | Hidalgo | Tier 1 | 2011-05-03 | 2011-12-19 | 2012-01-17 | 5966, 8383, 5962 | Y | N |  |  | 2460 | 2371
15TPIT0045 | ETP Capacitor | Add 19.2 MVAR capacitor |  | ETP |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-06-01 |  | 138 | 0 | 0 | 0 | 0,19.2 | Jackson |  | Tier 4 |  |  |  | 5523 | Y | N |  |  | 2659 | 2553
16TPIT0038 | Rebuild STEC Mathis to AEP Mathis | Rebuild 69 kV 4-0 to 795 ACSR on 138 kV capable structures. Only rebuild the 4-0 to 795 ACSR leave tap at 336 ACSR |  | Mathis | AEP Mathis | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-06-01 |  | 69 | 0 | 5.3 | 0 |  | Live Oak | San Patricio | Tier 1 | 2012-09-05 | 2013-01-31 | 2013-03-12 | 5668, 8407 | Y | N |  |  | 3117 | 2948
3353 | Aransas Pass to Rockport: Convert 69 kV line to 138 kV | Expand Aransas Pass and Rockport 138 kV stations and add 138/69 kV autotransformer capacity at Rockport |  | Aransas Pass | Rockport | Planned | 624 - 0792 | AEP TCC | Dave Goetz 918-599-2664 | 3507 | 2016-06-01 |  | 138 | 0 | 0 | 90 |  | Medina |  | Tier 4 |  |  |  | 8427, 8430, 8432, 8434 | Y |  |  |  | 3542 | 3353
3394 | Add Long Road Station |  |  | North Denton | Arco | Planned |  | DME | Chuck Sears 940-349-7111 |  | 2016-06-01 |  | 138 | 0 | 0 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 925, 983, 985 | Y | N |  |  | 3592 | 3394
4010 | Rebuild Magnolia - Seminole 138 kV line. |  |  | Magnolia Sub | Seminole Sub | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE07216 | 2016-06-01 |  | 138 | 0 | 3.3 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38950, 38990 | Y |  |  |  | 4355 | 4010
4012 | Daffin Gin-Austrop: Upgrade Ckt 974 | Reconductor to 3000 amps as part of AU-DP Corridor Upgrade |  | Daffin Gin | Austrop | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2016-06-01 |  | 138 | 0 | 9.16 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9184, 9328 | Y |  |  |  | 4357 | 4012
4086 | Dunlap-Austrop: Upgrade Ckt 920 | Upgrade conductor and termination equipment to a minimum rating of 3000 amps as part of AU-DP Corridor Upgrade |  | Dunlap | Austrop | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2016-06-01 |  | 138 | 0 | 3.8 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9045, 9328 | Y |  |  |  | 4436 | 4086
4087 | Dunlap-Decker Plant: Upgrade Ckt 1027 | Reconductor to 3000 amps as part of AU-DP Corridor Upgrade |  | Dunlap | Decker Plant | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2016-06-01 |  | 138 | 0 | 4.85 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9045, 9188 | Y |  |  |  | 4437 | 4087
4140 | DME_Ndenton_NLakes |  |  | N Denton | N Lakes | Planned | N/A | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2016-06-01 |  | 69 | 0 | 2 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 912, 915 | Y | N | N/A |  | 4485 | 4140
4482 | Add Claytonville Station by tapping LST line |  |  | West Shackelford | Scurry | Planned |  | LST | Don Le 713-366-6105 |  | 2016-06-01 |  | 345 | 0 | 0 | 250 |  | Shackelford | Scurry | Tier 4 |  |  |  | 68001, 68002, 11318, 68000 | Y |  |  |  | 4875 | 4482
4495 | AEP_4495_Champlin | Convert existing breaker and half configuration to a six (6) breaker ring bus configuration |  | Champlin | Champlin | Planned | 694 - 0864 | AEP TCC | Glen Reed 918-599-2664 | 3541 | 2016-06-01 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8476 | Y | N |  |  | 4889 | 4495
4608 | Olsen-Walnut Springs Rebuild | Olsen-Clifton-Clifton Tap-Meridian Tap-Walnut Springs Rebuild with 795 ACSR. |  | 37470 | 37680 | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE09517 | 2016-06-01 |  | 69 | 0 | 24.77 | 0 |  | Bosque | Bosque | Tier 3 |  |  |  | 37470, 37600, 37620, 37650, 37680 | Y |  |  |  | 5015 | 4608
08TPIT0033 | Gilleland to Techridge 138kV Circuit | Establish a new 138kV circuit from Gilleland to Techridge and maintain a normally close tie between AEN and LCRA's switchyard at Gilleland. |  | Gilleland Substation | Techridge Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | PLAN_117_4276 PLAN_117_P207 | 2016-06-15 |  | 345 | 8 | 0 | 0 |  | Travis | Travis | Tier 2 |  | 2009-07-21 | 2009-07-21 | 9054, 7336, 9190 | Y | N |  |  | 1030 | 1029
14TPIT0038 | Northland to Mag Plant Circuit 979 Upgrade | Reconductor the existing Northland to Mag Plant circuit from single 795SCAR to bundle 795 ACSR Drake and increase rating to 2000 Amp |  | Northland Substation | Mag Plant Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | NEW | 2016-06-15 |  | 138 | 0 | 4.11 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9128, 9238 | Y | N |  | Will add the project to the base case | 2548 | 2443
4425 | New TR-JV Ckt 961 | Add 2nd Ckt from TR to HL to tie-in to HL-JV Ckt 961 bypassing HL and creating TR-JV Ckt. | [5 empty] | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2016-06-15 |  | 0 | 0 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9190, 9217, 9223 | Y | N |  |  | 4809 | 4425
4555 | Gillette Substation | Construct the new 138-kV Gillette substation (78582) on the existing LCRA TSC Milton (78583) to Nixon AE (78580) 138-kV transmission line. |  | Gillette | Milton / NixonAE | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013517 | 2016-06-17 |  | 138 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  | 78582, 78580, 78583 | Y | N |  |  | 4959 | 4555
11TPIT0002 | Lobo to North Edinburg: Construct 345 kV Line | Construct 345 kV series compensated line from Lobo to Cenizo to Del Sol to North Edinburg |  | Lobo | North Edinburg | Under Construction | 065 - 0273 | ETT | Rich Haley 918-599-2664 | 3421 | 2016-06-30 |  | 345 | 156 | 0 | 0 |  | Webb | Hidalgo | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-20 | 80220, 80225, 80307, 80355, 8383, 80219 | Y | N |  |  | 1325 | 1321
13TPIT0198 | Seawillow Substation | Construct 138kV-12.5kV distribution substation Seawillow (7559) on T-184 Lockhart and Luling. |  | Seawillow | Luling / Lockhart | Planned |  | LCRATSC/BBEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1013521 | 2016-06-30 |  | 138 | 0 | 0 | 0 |  | Caldwell |  | Tier 4 |  |  |  | 7559, 7216, 7224 | Y | N |  |  | 2772 | 2648
16TPIT0040 | Del Sol: Add a 100 MVAR Shunt Reactor | Construct 345 kV series compensated line from Lobo to Cenizo to Del Sol to North Edinburg | Updated Trans Status | Del Sol |  | Under Construction | 065 - 0273 | ETT | Rich Haley 918-599-2664 | 629 | 2016-06-30 |  | 345 | 0 | 0 | 0 | -100,0 | Starr |  | Tier 4 |  |  |  | 80355 | Y | N |  |  | 3310 | 3141
16TPIT0041 | Cenizo: Add a 100 MVAR Shunt Reactor | Construct 345 kV series compensated line from Lobo to Cenizo to Del Sol to North Edinburg | Updated Trans Status | Cenizo |  | Under Construction | 065 - 0273 | ETT | Rich Haley 918-599-2664 | 630 | 2016-06-30 |  | 345 | 0 | 0 | 0 | -100,0 | Webb |  | Tier 4 |  |  |  | 80220 | Y | N |  |  | 3311 | 3142
16TPIT0000 | Del Sol: Add a 24 Ohm, 3600 A Series Capacitor | Construct 345 kV series compensated line from Lobo to Cenizo to Del Sol to North Edinburg | Updated Trans Status | Del Sol |  | Under Construction | 065 - 0273 | ETT | Rich Haley 918-599-2664 | 629 | 2016-06-30 |  | 345 | 0 | 0 | 0 | 0,933.1 | Starr |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-20 | 80307, 80355 | Y | N |  | Modeling in 11TPIT0002 | 3312 | 3143
16TPIT0017 | Cenizo: Add a 24 Ohm 3600, A Series Capacitor | Construct 345 kV series compensated line from Lobo to Cenizo to Del Sol to North Edinburg | Updated Trans Status | Cenizo |  | Under Construction | 065 - 0273 | ETT | Rich Haley 918-599-2664 | 630 | 2016-06-30 |  | 345 | 0 | 0 | 0 | 0,933.1 | Webb |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-20 | 80220, 80225 | Y | N |  | Modeled in 11TPIT0002 | 3313 | 3144
15TPIT0067 | Tuleta 138 kV Station: Construct a new station | Construct 138 double circuit line from Kenedy Switch Station to Tuleta and Pettus respectively. Kenedy Switching station to Pettus will be energized at 69 kV. Upgrade 138 kV site at Kenedy Switching Station and construct new Tuleta 138 kV Station. |  | TULETA |  | Under Construction | 603-0765 | AEP TCC | FRANK PRITZLAFF GAREED@AEP.COM 918-599-2664 | 3483 | 2016-06-30 |  | 138 | 0 | 0 | 0 |  | Bee |  | Tier 4 |  |  |  | 8590 | Y | N |  | NA | 3689 | 3482
3745 | Del Sol: Add 345 kV breaker terminal for WF interconnect | Construct four 345 kV breaker ring exdable at Del Sol Station for the Generator Interconnect |  | DEL SOL |  | Under Construction | 666 - 0835 | AEP TCC | KENNETH 'RICH' HALEY GAREED@AEP.COM 918-599-2664 | 3530 | 2016-06-30 |  | 345 |  |  |  |  | Starr |  | Tier 4 |  |  |  | 80355 | Y | N |  |  | 3991 | 3745
3766 | Asherton Station: Replace 138/69 kV Autotransformer | Upgrade 138/69 kV Auto at Asherton Station | Changed Project Title, Project Description, Transmission Status, PM, Estimates and ISD | ASHERTON |  | Under Construction | 659-0828 | AEP TCC | Aaron Schwerman GAREED@AEP.COM 918-599-2664 | 3524 | 2016-06-30 |  | 138 |  |  | 130 |  | Dimmit |  | Tier 4 |  |  |  | 8280, 8283 | Y | N |  |  | 4011 | 3766
3767 | Three River 138 kV: Replace 138/69 kV Autotransformer | Replace 138/69 kV Auto at Three Rivers 138 kV Station | Changed Super project ID, Transmission Status, ISD, PM, and Estimate | THREE RIVER |  | Under Construction | 660-0829 | AEP TCC | Rick McCraken GAREED@AEP.COM 918-599-2664 | 3525 | 2016-06-30 |  | 138 |  |  | 130 |  | Live Oak |  | Tier 4 |  |  |  | 8400, 8403 | Y | N |  |  | 4012 | 3767
3898 | Pleasanton: Replace 138/69 kV autotransformer | Add 138/69 kV autotranformer capacity at Pleasanton |  | Pleasanton |  | Under Construction | 676 - 0845 | AEP TCC | Michael Tallon 918-599-2664 | 2595 | 2016-06-30 |  | 138 | 0 | 0 | 90 |  | Atascosa |  | Tier 4 |  |  |  | 8200, 8203 | Y | N |  |  | 4193 | 3898
3903 | Lobo 345 kV Station: Add 345/138 kV Auto | Add 2nd 345/138 kV Autotransformer at Lobo Switching Station |  | Lobo |  | Under Construction | 663 - 0832 | AEP TCC | KENNETH 'RICH' HALEY GAREED@AEP.COM 918-599-2664 |  | 2016-06-30 |  | 345 | 0 | 0 | 675 |  | Webb |  | Tier 4 |  |  |  | 80219, 80221 | Y | N |  |  | 4199 | 3903
3975 | Bessel 138 kV Station: Construct a new station | Construct four 138 kV breaker ring expandable to six breaker at Bessel 138 kV station | Updated In Service Date, Transmission Status | BESSEL |  | Under Construction | 671-0840 | AEP TCC | DAVE GOETZ GAREED@AEP.COM 918-599-2664 | 3532 | 2016-06-30 |  | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 80600, 80601, 8452, 8514 | Y | N | NA |  | 4300 | 3975
16TPIT0031 | Esmeralda: Build 138 kV station and add capacitor banks | Construct new Esmeralda station along the Big Lake to Friend Ranch 138 kV line, install one 14.4 Mvar and two 7.2 Mvar capacitor banks, and build a new 138 kV line from Esmeralda to Yucca with 795 ACSS | Project Title and Schedule Update | Esmeralda |  | Planned | 585 - 0738 | AEP TCC | Eric Scott 918-599-2664 | 2576 | 2016-06-30 |  | 138 | 0 | 0 | 0 | 0,28.8 | Crockett |  | Tier 4 |  |  |  | 6525, 6562, 60375 | Y | N |  |  | 4646 | 3241
4311 | Sand Bluff Reactor Addition | Add three breakers and move one 50 MVAR shunt reactor from Cottonwood to Sand Bluff. |  | Sand Bluff |  | Planned |  | WETT | Julius Horvath julius.horvath@windenergyoftexas.com 512-436-9585 |  | 2016-06-30 |  | 345 | 0 | 0 | 0 | 50,0 | Sterling |  | Tier 4 |  |  |  | 59902 | Y | N |  |  | 4688 | 4311
4319 | Cottonwood Reactor Addition | Add one new 100 MVAR reactor at Cottonwood. Move one existing 50 MVAR reactor to Sand Bluff |  | Cottonwood |  | Planned |  | WETT | Julius Horvath julius.horvath@windenergyoftexas.com 512-436-9585 |  | 2016-06-30 |  | 345 | 0 | 0 | 0 | 100,0 | Dickens |  | Tier 4 |  |  |  | 59904 | Y | N |  |  | 4696 | 4319
4481 | Linterna: Build a 138 kV tap | Construct new 138 kV hard tap off the Barrilla Junction to Fort Stockton line | New Project | Linterna |  | Planned | 706 - 0876 | AEP TNC | Brent Harris 918-599-2664 | 2812 | 2016-06-30 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60383, 6630, 6655 | Y | N |  |  | 4871 | 4481
4294 | AEP_MoveLVIII-345 | [6 empty] | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2016-06-30 |  | 138 | 0 | 0 | 0 | [7 empty] | 8835, 160884, 8394, 80355, 8399 | Y |  |  |  | 4891 | 4294
4411 | Transmission line upgrade | Upgrade and Reconductor 4.08 miles of transmission line from Switch Station Substation to Spring Creek Substation from 477 AAC to 1033 ACSS conductor. Replace 5.13 miles of static with OPGW. Replace and re-span poles as necessary. Project relieves contingency overload of Gibbons Creek (964) to Greens Prairie (32878), Switch Station (32000) to Post Oak (32001). |  | CSST | CSSC | Planned |  | COCS | Tony Mickalsky tmichalsky@cstx.gov 979-764-3438 |  | 2016-07-01 |  | 138 | 0 | 4.08 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32000, 32004 | Y | N |  |  | 4791 | 4411
4413 | Transmission line upgrade | Upgrade and Reconductor 2.11 miles of transmission line from Spring Creek Substation to Greens Prairie Substation from 477 AAC to 1033 ACSS conductor. Replace 3.81 miles of static with OPGW. Replace and re-span poles as necessary. Project relieves contingency overload conditions for loss of Gibbons Creek (964) to Greens Prairie (32878), Switch Station (32000) to Post Oak (32001). |  | CSSC | CSGP | Planned |  | COCS | Tony Mickalsky tmichalsky@cstx.gov 979-764-3438 |  | 2016-07-01 |  | 138 | 0 | 2.11 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32004, 32003 | Y |  |  |  | 4793 | 4413
4541 | Add new 345kV Abernathy station and 51 miles line from WR-AN |  |  | White River | Abernathy | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2016-07-01 |  | 345 | 51 | 0 | 0 |  | Floyd | Hale | Tier 4 |  |  |  | 79506, 79505 | Y | N |  |  | 4943 | 4541
4542 | Add new 345/138kV Einstein station |  |  | Einstein | Einstein | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2016-07-01 |  | 345 | 0.038 | 0 | 675 |  | Glasscock | Glasscock | Tier 2 |  |  |  | 79565, 79632, 59903, 79617, 79625 | Y | N |  |  | 4944 | 4542
4545 | Upgrade 138kV Brown - Vealmoor line |  |  | Brown | Vealmoor | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2016-07-01 |  | 138 | 0 | 15.3 | 0 |  | Martin | Borden | Tier 4 |  |  |  | 79512, 79551, 79553, 79600 | Y | N |  |  | 4947 | 4545
4461 | Moulton South Substation | Build a new 138-26.18 kV 18-24-30 MVA substation on the LCRA TSC Flatonia to Yoakum 138-kV transmission line. |  | Flatonia | Yoakum | Planned |  | LCRATSC/GVEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2016-07-01 |  | 138 | 0 | 0 | 0 |  | Lavaca |  | Tier 4 |  |  |  | 7237, 7236, 7238 | Y | N |  |  | 4969 | 4461
4583 | Addition of 138kV Boyd station and Boyd-Stiles line |  |  | Boyd | Stiles | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2016-07-01 |  | 138 | 6 | 0 | 0 |  | Reagan | Reagan | Tier 4 |  |  |  | 79561, 79614 | Y | N |  |  | 4991 | 4583
4584 | Addition of 2nd circuit on Pemkiff - Midkiff line |  |  | Pemkiff | Midkiff | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2016-07-01 |  | 138 | 0.3 | 0 | 0 |  | Upton | Upton | Tier 4 |  |  |  | 1210, 79555 | Y | N |  |  | 4992 | 4584
10TPIT0062 | Weil Road (inside Marion) - New Substation | Build new 138-26.18 kV 40 MVA substation off Marion 138 kV bus at the Marion Interchange, New Control House, Separation Fence, Security Equipment. |  | Weil Road |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-07-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7603, 7178, 7608 | Y | N |  |  | 2473 | 2384
11TPIT0107 | Steamboat: Reterminate 69 kV Happy Valley tap | Reterminate the Happy Valley tap into Steamboat | Schedule Update | Happy Valley | Steamboat | Planned | 341 - 0515 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 2092 | 2016-07-31 |  | 69 | 0 | 0.6 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6332, 6328, 6330, 6331, 60332 | Y | N |  |  | 299 | 302
13TPIT0121A | Tilden to Reveille 138 kV line | New station between Tilden and Reveille |  | Fowlerton |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-08-01 |  | 138 | 0 | 0 | 0 |  | McMullen | La Salle | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5705 | Y | N |  | project cost in last phase | 2355 | 2282
13TPIT0121B | Tilden to Reveille 138 kV line | Construct a new 138 kV double circuit capable line from Tilden to Fowlerton |  | Tilden | Fowlerton | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-08-02 |  | 138 | 17 | 0 | 0 |  | McMullen | La Salle | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5701, 5705 | Y | N |  | project cost in last phase | 2356 | 2282
13TPIT0121C | Tilden to Reveille 138 kV line | Construct a new 138 kV double circuit capable line from Fowlerton to Reveille |  | Fowlerton | Reveille | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-08-03 |  | 138 | 30 | 0 | 0 |  | McMullen | La Salle | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 5705, 8612 | Y | N |  |  | 2357 | 2282
15TPIT0044 | Fowlerton Capacitor | Add 19.2 MVAR capacitor |  | Fowlerton |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-08-04 |  | 138 | 0 | 0 | 0 | 0,19.2 | La Salle |  | Tier 4 |  |  |  | 5705 | Y | N |  |  | 2660 | 2554
4573 | Briarcrest to Atkins Cable Upgrade |  |  | 32864 | 32877 | Planned |  | BRYN |  |  | 2016-09-01 |  | 69 | 0.15 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32864, 32877 | Y |  |  |  | 4980 | 4573
18TPIT0001 | Wiederstein Substation | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer |  | Wiederstein |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-09-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7461 | Y | N |  |  | 3500 | 3319
14TPIT0098 | Cost Substation Addition | Build new station, add 138x69kV-13.09x26.18 dual kV, 12/16/20 MVA PWT w/associated control house, structures, bus, panels, etc |  | Cost |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-09-30 |  | 69 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  | 7622 | Y | N |  |  | 3502 | 3321
4202 | Jackalope: Build 138 kV station | Construct new 138 kV in and out substation off the Big Lake to North McCamey line | Schedule Update | Jackalope |  | Planned | 696 - 0866 | AEP TNC | Bill Clarke 918-599-2664 | 2810 | 2016-09-30 |  | 138 | 0 | 0 | 0 |  | Reagan |  | Tier 4 |  |  |  | 6595, 6536, 60361 | Y | N |  |  | 4558 | 4202
4503 | BRYN_4503_Rayburn_Tabor_Upgrade |  |  | 32861 | 32870 | Planned |  | BRYN |  |  | 2016-09-30 |  | 69 | 0 | 4.06 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32861, 32870 | Y |  |  |  | 4900 | 4503
4516 | City of Brady to North Brady: Reterminate 69 kV line | Rebuild the 69 kV line from the City of Brady Tap to North Brady double circuit with 959.6 ACSR/TW to allow retermination of the City of Brady Tap line into North Brady station with the addition of a breaker | New Project | City of Brady | North Brady | Planned | 715 - 0881 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2813 | 2016-09-30 |  | 69 | 0 | 0.8 | 0 |  | McCulloch | McCulloch | Tier 4 |  |  |  | 6382, 6006, 6380, 6383 | Y | N |  |  | 4913 | 4516
4116 | FM-725 Substation | Build a new 138-26.18 kV, 40 MVA substation on the GVEC McQueeney(7606) - Schumansville(7609) 138 kV transmission line |  | FM 725 | McQueeney-Schumansville | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-10-01 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7725, 7606, 7609 | Y | N |  |  | 4462 | 4116
4402 | Cenizo: Build new four breaker 345 kV station | Interconnect Javalina Windfarm at Cenizo to connect Bordas on the Lobo SS to North Edinburg 345 kV line |  | Cenizo |  | Planned | 700 - 0870 | ETT | Rich Haley 918-599-2664 | 3544 | 2016-10-15 |  | 345 | 0 | 0 | 0 |  | Webb |  | Tier 4 |  |  |  | 80646, 8295, 80230 | Y |  |  |  | 4781 | 4402
3507 | Nopal Substation | Build a new 138-26.18 kV 18/24/30 MVA substation to be served by Gillett to Nopal 138 kV transmission line |  | Nopal |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-10-29 |  | 138 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  | 7233 | Y | N |  |  | 3714 | 3507
15TPIT0050 | Loxley 138kV substation: STEC Interconnect | Loxley 138kV substation: STEC Interconnect. | Date Change | Pleasanton | Trumbo (CPS) | Planned | 044 - 0420 | AEP TCC | Glen Reed 918-599-2664 | 3472 | 2016-10-30 |  | 138 | 0 | 0 | 0 |  | Atascosa | Atascosa | Tier 4 |  |  |  | 80491, 5429, 8203 | Y | N |  |  | 3219 | 3050
3509 | Gillett Sub (LCRA) to Nopal Sub 138 kV Transmission Line | Add 138 Terminal at LCRA Gillett Station; Build approx 9 miles of single ckt 138 kV t-line, 795 ACSR |  | Gillett | Nopal | Planned | 15TPIT0063 | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-10-31 |  | 138 | 8.5 | 0 | 0 |  | Gonzales | Gonzales | Tier 4 |  |  |  | 7233, 78582 | Y | N |  |  | 3716 | 3509
4252 | Eagle Mountain - Rosen Heights 138 kV Line | Upgrade existing double-circuit line |  | Eagle Mountain | Rosen Heights Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5211 | 2016-11-15 |  | 138 | 0 | 20.2 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1860, 1864, 2065, 2066, 2067, 11860 | Y | N |  |  | 4623 | 4252
3965 | Twin Buttes Auto Transformer | Install a new 345/138 kV 672 MVA auto transformer at Twin Buttes substation |  | Twin Buttes |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014328 | 2016-11-22 |  | 345 | 0 | 0 | 672 |  | Tom Green |  | Tier 4 |  |  |  | 77280, 76009, 76011, 6013 | Y | N |  |  | 4286 | 3965
4492 | Marconi: Build new three breaker 138 kV station | Interconnect San Roman Windfarm at Marconi to connect San Roman to the Port Isabel to Laureles 138 kV line |  | Marconi |  | Planned | 712 - 0883 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2906 | 2016-11-30 |  | 138 | 0 | 0 | 0 |  | Cameron |  | Tier 4 |  |  |  | 8262, 8266, 5756, 8338 | Y | N |  |  | 4886 | 4492
17TPIT0002 | Hunt Lane to Pinn Road - 138 kV Transmission Line Rebuild | Rebuild approximately eight circuit miles of 138 kV transmission from Hunt Lane to Pinn Road |  | Hunt Lane | Pinn Rd | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0190 | 2016-12-01 |  | 138 | 0 | 8 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5054, 5305, 5345, 5427 | Y | N |  | There are no transformers associated with this project | 2383 | 2307
15TPIT0054 | Barney Davis To Naval Base Construct 138 kV line | Construct new 138 kV line and add tranformation at Naval Base to remove contingency overloads during off-peak maintenance |  | BARNEY DAVIS | NAVAL BASE | Planned | 607 - 0648 | AEP TCC | JOHN PULAY GAREED@AEP.COM 918-599-2664 | 3484 | 2016-12-05 |  | 138 | 7 |  |  |  | Nueces | Nueces | Tier 1 | 2013-07-15 | 2013-12-20 | 2013-01-24 | 8458, 8997 | Y | N |  |  | 3726 | 3519
15TPIT0046 | Permian Basin - Culberson 138 kV line | Construct new line. |  | Permian Basin | Culberson | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8070-E | 2016-12-15 |  | 138 | 88.7 | 0 | 0 |  | Ward | Culberson | Tier 4 | 2013-02-15 | 2013-02-15 |  | 1009, 1097 | Y | N |  |  | 2305 | 2232
16TPIT0062 | Pflugerville - Gilleland Creek 138 kV Line | Upgrade existing line |  | Pflugerville | Gilleland Creek | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R773-E | 2016-12-15 |  | 138 | 0 | 3.8 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 3665, 7336 | Y | N |  |  | 3248 | 3079
17TPIT0021 | Liggett - Norwood 138 kV Line | Upgrade existing double-circuit line |  | Liggett | Norwood | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4109-E | 2016-12-15 |  | 138 | 0 | 12.6 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 1922, 1924, 2053, 2054, 2055, 2408 | Y | N |  |  | 3257 | 3088
16TPIT0054 | Dialville - Palestine South 138 kV Line | Upgrade existing line |  | Dialville | Palestine South | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6019 | 2016-12-15 |  | 138 | 0 | 25 | 0 |  | Cherokee | Andrews | Tier 4 |  |  |  | 3160, 3271, 3296 | Y | N |  |  | 3283 | 3114
15TPIT0070 | Andrews Switch - Frankel City 69 kV Line | Rebuild existing Andrews - Fullerton 69 kV line section as a double-circuit line with a 69 kV circuit and a 138 kV circuit. Includes 16TPIT0046 Frankel City - Exxon Fullerton 69 kV Line. |  | Andrews | Fullerton | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8175 | 2016-12-15 |  | 69 | 14.8 | 14.8 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1270, 1267, 1271, 1274, 1272, 1275 | Y | N |  |  | 3327 | 3156
4209 | Rivercrest Switch - Rivercrest Tap 69 kV Line | Upgrade existing line |  | Rivercrest Switch | Rivercrest Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R955 | 2016-12-15 |  | 69 | 0 | 0.6 | 0 |  | Red River | Red River | Tier 4 |  |  |  | 1781, 1783 | Y | N |  |  | 4570 | 4209
4216 | Odessa EHV - Spraberry 138 kV Line | Upgrade existing line | Construction schedule change | Odessa EHV | Spraberry | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8257 | 2016-12-15 |  | 138 | 0 | 21.5 | 0 |  | Ector | Midland | Tier 4 |  |  |  | 1027, 1137, 1139, 1329 | Y | N |  |  | 4578 | 4216
4245 | Wink - Odessa Basin 69 kV Line | Rebuild existing line |  | Wink | Odessa Basin | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8203 | 2016-12-15 |  | 69 | 0 | 35 | 0 |  | Winkler | Ector | Tier 3 |  |  |  | 1075, 1251, 1252, 1254, 1253, 1258 | Y | N |  |  | 4619 | 4245
4268 | Breckenridge - Leon Switch 69 kV Line | Upgrade existing line |  | Breckenridge | Leon Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R783 | 2016-12-15 |  | 69 | 0 | 28.8 | 0 |  | Stephens | Eastland | Tier 3 |  |  |  | 271, 1622, 1615, 1623, 1625 | Y | N |  |  | 4641 | 4268
4273 | Corsicana - Trinidad 69 kV Line | Upgrade existing line |  | Corsicana | Trinidad | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R794 | 2016-12-15 |  | 69 | 0 | 26.5 | 0 |  | Navarro | Henderson | Tier 4 |  |  |  | 3128, 3466, 3467, 3468, 3469 | Y | N |  |  | 4647 | 4273
4212 | Lamar Blossom 138 kV capacitors | Install shunt capacitors |  | Lamar Blossom |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R974 | 2016-12-15 |  | 138 | 0 | 0 | 0 | 0,18.4 | Lamar |  | Tier 4 |  |  |  | 1771 | Y | N |  |  | 4651 | 4212
4281 | Powell 69 kV capacitors | Install shunt capacitors |  | Powell |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R796 | 2016-12-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Navarro |  | Tier 4 |  |  |  | 3467 | Y | N |  |  | 4656 | 4281
4521 | Midkiff Switching Station | Upgrade switching station |  | Midkiff |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8276 | 2016-12-15 |  | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  | 1210 | Y | N |  |  | 4918 | 4521
4524 | Culberson 138 kV Switching Station | Rebuild 138 kV bus |  | Culberson Switching station |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8070B | 2016-12-15 |  | 138 | 0 | 0 | 0 |  | Culberson |  | Tier 4 | 2013-02-15 | 2013-02-15 |  | 1097 | Y | N |  |  | 4921 | 4524
4529 | North Andrews - Bakke - Andrews 69 kV Line | Rebuild existing 69 kV line section as a double-circuit line with a 69 kV circuit and a 138 kV circuit |  | North Andrews | Andrews | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8294 | 2016-12-15 |  | 69 | 6.9 | 6.9 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1277, 1159, 1160, 1267, 1270 | Y | N |  |  | 4929 | 4529
4548 | Permian Basin Switching Station | Construct new switching station |  | Permian Basin Switching Station |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8261 | 2016-12-15 |  | 138 | 0 | 0 | 0 |  | Ward |  | Tier 4 |  |  |  | 1009, 1010, 1103, 1019, 1105, 1107, 6656 | Y | N |  |  | 4950 | 4548
4559 | Midkiff - Garden City 138 kV Line | Rebuild existing Midkiff - Garden City 69 kV Line as a double-circuit line with a 69 kV circuit and a 138 kV circuit |  | Midkiff | Garden City | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8290 | 2016-12-15 |  | 138 | 20 | 20 | 0 |  | Upton | Glasscock | Tier 3 |  |  |  | 1210, 1218, 1333, 1352 | Y | N |  |  | 4965 | 4559
13TPIT0149 | Oaks to Loxley | Build new 138 kV 795 ACSR circuit from Oaks to a new AEP switching station Loxley in the Leon Creek to Pleasanton line |  | Oaks | Loxley | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-12-20 |  | 138 | 6 | 0 | 0 |  | Atascosa | Atascosa | Tier 3 | 2011-12-16 | 2012-04-25 |  | 5713, 80491 | Y | N |  |  | 2233 | 2161
13TPIT0070 | Nash Creek Substation | Replace existing PWT with new 69kVx13.09 kV, new Control House, CSW, structures, containment foundations, bus, panels, etc |  | Nash Creek |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-12-30 |  | 69 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7596 | Y | N |  |  | 3503 | 3322
10TPIT0148 | Las Pulgas Tap - Renamed from Willacy Tap Switch 138kV | Move normally open 138kV connection to the AEP Raymondville #2 bus and add breakers at Las Pulgas to serve E Raymondville and La Sara from Las Pulgas. |  | Las Pulgas |  | Planned | 12TPIT0103 | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2016-12-31 |  | 138 | 0 | 0 | 0 |  | Willacy | Willacy | Tier 4 |  |  |  | 5745, 5790, 8302, 80309 | Y | N |  |  | 2407 | 2330
16TPIT0032 | Esmeralda to Yucca: Build 138 kV line | Construct new Esmeralda station along Big Lake to Friend Ranch 138 kV line and build new 138 kV line from Esmeralda to Yucca with bundled 959.6 ACSS | Schedule Update | Esmeralda | Yucca | Planned | 585 - 0745 | AEP TNC | Eric Scott 918-599-2664 | 2577 | 2016-12-31 |  | 138 | 13 | 0 | 0 |  | Crockett |  | Tier 4 |  |  |  | 6034, 6035, 6036, 6531, 6525 | Y | N |  |  | 2761 | 2637
14TPIT0109 | Kenedy Switch to Tuleta: Build double circuit 138 kV line | Construct 138 double circuit line from Kenedy Switch Station to Tuleta and Pettus respectively. Kenedy Switching station to Pettus will be energized at 69 kV. Upgrade 138 kV site at Kenedy Switching Station and construct new Tuleta 138 kV Station. |  | KENEDY SWITCHING STATION | TULETA | Under Construction | 603 - 0765 | AEP TCC | Frank Pritzlaff gareed@aep.com 918-599-2664 | 3483 | 2016-12-31 |  | 138 | 16.9 | 16.9 | 0 |  | Karnes | Bee | Tier 4 |  |  |  | 8590, 8593, 8186 | Y | N | NA | NA | 3169 | 3000
3402 | Abilene Northwest to Ely Tap: Rebuild 69 kV line | Rebuild Abilene Northwest to Ely Tap 69 kV line with 959.6 ACSS/TW | Schedule Update | Abilene Northwest | Ely Tap | Planned | 630 - 0798 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2589 | 2016-12-31 |  | 69 | 0 | 8.2 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6225, 6241 | Y | N |  |  | 3600 | 3402
14TPIT0082 | Kenedy Switch to Pettus: Rebuild 69 kV line | Construct 138 double circuit line from Kenedy Switch Station to Tuleta and Pettus respectively. Kenedy Switching station to Pettus will be energized at 69 kV. Upgrade 138 kV site at Kenedy Switching Station and construct new Tuleta 138 kV Station. | Construct 138 double circuit line from Kenedy Switch Station to Tuleta and Pettus respectively. Kenedy Switching station to Pettus will be energized at 69 kV. Upgrade 138 kV site at Kenedy Switching Station and construct new Tuleta 138 kV Station. | KENEDY SWITCHING STATION | PETTUS | Under Construction | 603-0765 | AEP TCC | FRANK PRITZLAFF GAREED@AEP.COM 918-599-2664 | 3473 | 2016-12-31 |  | 69 |  | 15.9 | 0 |  | Karnes | Bee | Tier 4 |  |  |  | 8184, 8188, 8593 | Y | N |  |  | 3669 | 3464
3479 | Cassava: Build 69 kV station | Construct new Cassava station along the Big Lake to Mathis Field 69 kV line (at Barnhart Phillips Tap location) | Company Contact Update | Cassava |  | Planned | 635 - 0804 | AEP TNC | Gregory Gibbs 918-599-2664 | 2590 | 2016-12-31 |  | 69 | 0 | 0 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6003, 60359, 6035, 6526, 6532 | Y | N |  |  | 3686 | 3479
3696 | Friend Ranch to Ozona: Rebuild 69 kV line | Rebuild Friend Ranch to Ozona line with 959.6 ACSS/TW |  | Friend Ranch | Ozona | Planned | 657 - 0826 | AEP TNC | Eric Scott 918-599-2664 | 1821 | 2016-12-31 |  | 69 | 0 | 3.4 | 0 |  | Crockett | Crockett | Tier 4 |  |  |  | 6550, 6560 | Y | N |  |  | 3939 | 3696
13TPIT0160 | Whitepoint: Add 138 kV breaker terminal for WF interconnect | Construct a 138 kV breaker terminal at Whitepoint for the Generator Interconnect |  | Whitepoint |  | Under Construction | 573-0750 | AEP TCC | Frank Pritzlaff gareed@aep.com 918-599-2664 | 3454 | 2016-12-31 |  | 138 |  |  |  |  | San Patricio |  | Tier 4 |  |  |  | 8961 | Y | N |  |  | 3976 | 3731
3825 | Jordan: Install 2nd 800MVA Autotransformer | Install 2nd 800MVA autotransformer at Jordan substation |  | Jordan |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 992 | 2016-12-31 |  | 345 | 0 | 0 | 800 |  | Chambers |  | Tier 4 |  |  |  | 49078, 40850, 40855 | Y | N |  |  | 4107 | 3825
3953 | Marfa to Alamito Creek: Rebuild 69 kV line | Rebuild Marfa to Alamito Creek 69 kV line with 959.6 ACSS/TW |  | Marfa | Alamito Creek | Planned | 669 - 0838 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2805 | 2016-12-31 |  | 69 | 0 | 0.7 | 0 |  | Presidio | Presidio | Tier 4 |  |  |  | 6678, 6681 | Y | N |  |  | 4273 | 3953
3998 | Stewart Road to Weslaco Unit: Rebuild 138 kV line | Rebuild 138 kV line from Stewart Road to Weslaco Unit |  | STEWART ROAD | WESLACO UNIT | Planned | 680-0849 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 3536 | 2016-12-31 |  | 138 |  | 15 |  |  | Hidalgo | Hidalgo | Tier 3 |  |  |  | 8348, 8951 | Y | N |  |  | 4324 | 3998
4168 | PH Robinson Autotransformer A2 Upgrade | Replace existing 600MVA PH Robinson autotransformer A2 with 800MVA autotransformer. |  | P.H. Robinson |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 994 | 2016-12-31 |  | 345 | 0 | 0 | 200 |  | Galveston |  | Tier 4 |  |  |  | 42000, 42015, 49048 | Y | N |  |  | 4517 | 4168
4231 | Creosote: Build 138 kV station | Construct 138 kV, six breaker ring bus on the existing 138 kV line from Barrilla Junction to Permian Basin |  | Creosote |  | Planned | 689 - 0859 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2606 | 2016-12-31 |  | 138 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 6657, 60377, 6656, 6673, 38375 | Y | N |  |  | 4602 | 4231
3705 | Solstice: Build 138 kV station | Construct new Solstice station along the Barrilla Junction to Fort Stockton Plant 138 kV line | Project Title, Project Description, Company Contact Update, and Cost Update | Solstice |  | Planned | 658 - 0827 | AEP TNC | Brent Harris 918-599-2664 | 1822 | 2016-12-31 |  | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 60383, 60385, 6630, 6655, 6673, 6680 | Y | N |  |  | 4870 | 3705
4522 | Hoefs Road: Build a 69 kV station | Construct new 69 kV in and out substation off the Barrilla Junction to Verhalen line | New Project | Hoefs Road |  | Planned | 690 - 0860 | AEP TNC | Brent Harris 918-599-2664 | 2607 | 2016-12-31 |  | 69 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 6654 | Y | N |  |  | 4919 | 4522
4531 | Solstice to Clovis: Build 138 kV line | Construct new 138 kV line from Solstice to Clovis | New Project | Solstice | Clovis | Planned | 705 - 0875 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2811 | 2016-12-31 |  | 138 | 4.5 | 0 | 0 |  | Pecos | Pecos | Tier 4 |  |  |  | 60383, 60384, 6630, 6655, 60385 | Y | N |  |  | 4931 | 4531
3911 | Cheniere LNG | Cheniere LNG |  | Hecker |  | Planned | 616 - 0784 | AEP TCC | Teresa Trotman gareed@aep.com 918-599-2664 | 3534 | 2017-01-02 |  | 138 | 0 | 0 | 0 |  | San Patricio |  | Tier 4 |  |  |  | 8568, 8565, 8961, 80470 | Y | N |  |  | 4209 | 3911
3894 | Fowlerton 345 station and 345/138 autotransformer | Add 345 kV bus and autotransformer |  | Fowlerton |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2017-02-01 |  | 345 | 0 | 0 | 600 |  | McMullen |  | Tier 4 |  |  |  | 5709, 5901, 80219, 5705 | Y | N |  |  | 4189 | 3894
4407 | Potencia: Build new 345/138 kV station | Interconnect La Paloma Generation at Potencia along the La Palma to Rio Hondo 345 kV and 138 kV lines and add 345/138 kV autotransformer capacity at Potencia |  | Potencia |  | Planned | 701 - 0871 | AEP TCC | Jason Bryant 918-599-2664 | 3545 | 2017-03-31 |  | 345 | 0 | 0 | 675 |  | Cameron |  | Tier 3 |  |  |  | 8460, 8461, 8314, 8317, 8318, 8319 | Y |  |  |  | 4786 | 4407
16TPIT0018 | Hicks Switch Autotransformer | Install 345/138 kV autotransformer |  | Hicks Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5145-E | 2017-05-14 |  | 345 | 0 | 0 | 600 |  | Tarrant |  | Tier 4 |  |  |  | 2082, 1860, 2075, 2076, 12065, 2081 | Y | N |  |  | 2700 | 2584
11TPIT0179 | Hicks Switch - Elizabeth Creek 138 kV line | Construct new double-circuit 138 kV line |  | Hicks Switch | Elizabeth Creek | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M523-E | 2017-05-14 |  | 138 | 30.4 | 0 | 0 |  | Tarrant | Tarrant | Tier 2 | 2013-02-01 | 2013-03-01 |  | 1866, 1867, 2082 | Y | N |  |  | 2786 | 2662
11TPIT0050 | Roanoke Switch - Elizabeth Creek 138 kV line | Construct new double-circuit line. |  | Roanoke Switch | Elizabeth Creek | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M509-E | 2017-05-14 |  | 138 | 3.8 | 0 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1867, 640, 1852, 1854, 1866 | Y | N |  |  | 3058 | 2884
12TPIT0080 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer |  | Forney Sw. Sta. |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4037 | 2017-05-15 |  | 345 | 0 | 0 | 600 |  | Kaufman |  | Tier 4 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | N | 2007-R2 |  | 2594 | 2489
16TPIT0057 | Hutto Switching Station - Taylor 138 kV Line | Upgrade existing line |  | Hutto Switching Station | Taylor | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R775 | 2017-05-15 |  | 138 | 0 | 15.6 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 3658, 3666, 3673 | Y | N |  |  | 3240 | 3071
16TPIT0055 | Elkton - Jacksonville 138 kV Line | Upgrade existing line |  | Elkton | Jacksonville | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6029-E | 2017-05-15 |  | 138 | 0 | 20.2 | 0 |  | Smith | Cherokee | Tier 4 |  |  |  | 3106, 3251, 3253 | Y | N |  |  | 3279 | 3110
17TPIT0010 | Brownsboro 69 kV capacitors | Install shunt capacitor |  | Brownsboro |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6025-E | 2017-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Henderson | Henderson | Tier 4 |  |  |  | 3236 | Y | N |  |  | 3285 | 3116
17TPIT0020 | Forest Grove - Trinidad 138 kV Line | Upgrade existing line |  | Forest Grove | Trinidad | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6034 | 2017-05-15 |  | 138 | 0 | 14.5 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3127, 3131, 3276, 29266 | Y | N |  |  | 3322 | 3151
17TPIT0026 | Stryker Creek - Lufkin 138 kV Line | Upgrade existing line |  | Stryker Creek | Lufkin | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6040-E | 2017-05-15 |  | 138 | 0 | 44.3 | 0 |  | Cherokee | Angelina | Tier 3 |  |  |  | 3110, 3340, 3341, 3342, 3343 | Y | N |  |  | 3324 | 3153
17TPIT0031 | Elkton 345/138 kV autotransformer | Replace existing autotransformer and install tertiary reactor |  | Elkton |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6032-E | 2017-05-15 |  | 345 | 0 | 0 | 600 | -37.5,0 | Smith | Smith | Tier 4 |  |  |  | 3105, 3106, 29150 | Y | N |  |  | 3326 | 3155
14TPIT0008 | Holt - Emma Tap - Andrews 69 kV Line | Upgrade existing line. |  | Holt | Andrews | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8144-E | 2017-05-15 |  | 69 | 0 | 16.2 | 0 |  | Ector | Andrews | Tier 4 |  |  |  | 1142, 1262, 1267 | Y | N | 2009-R5 |  | 3331 | 3160
15TPIT0094 | Texaco Mabee 138 kV capacitors | Install shunt capacitors |  | Texaco Mabee |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8152-E | 2017-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Midland |  | Tier 4 |  |  |  | 1177 | Y | N |  |  | 3339 | 3168
17TPIT0024 | Payne - Anna Switch 138 kV Line | Upgrade existing line |  | Payne | Anna Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R938-E | 2017-05-15 |  | 138 | 0 | 20.8 | 0 |  | Grayson | Collin | Tier 4 |  |  |  | 1713, 1748, 1754, 1758, 2374 | Y | N |  |  | 3386 | 3213
16TPIT0048 | Trinidad - Athens 69 kV Line | Upgrade existing line |  | Trinidad SES | Athens | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6033-E | 2017-05-15 |  | 69 |  | 17.5 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3128, 3239 | Y | N |  |  | 3590 | 3392
4228 | McDonald Rroad - Polecat Creek 138 kV Line | Upgrade existing line |  | McDonald Road | Polecat Creek | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8207 | 2017-05-15 |  | 138 | 0 | 7.2 | 0 |  | Howard | Glasscock | Tier 4 |  |  |  | 1333, 1334, 1335, 11337 | Y | N |  |  | 4599 | 4228
4236 | Odessa EHV - Big Three Odessa 138 kV Line | Upgrade existing line |  | Odessa EHV | Big Three Odessa | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8210 | 2017-05-15 |  | 138 | 0 | 4.4 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1027, 1111 | Y | N |  |  | 4609 | 4236
4254 | DeSoto Switching Station - Sterrett 138 kV Line | Upgrade existing line |  | De Soto | Sterrett | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4122 | 2017-05-15 |  | 138 | 0 | 2.7 | 0 |  | Dallas | Ellis | Tier 4 |  |  |  | 2317, 2424, 2426 | Y | N |  |  | 4625 | 4254
4255 | Odessa Basin 69 kV Switching Station | Upgrade existing switching station |  | Odessa Basin |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8247 | 2017-05-15 |  | 69 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  | 1123, 1254, 1258 | Y | N |  |  | 4626 | 4255
4257 | Stryker Creek - Gresham Road 138 kV line | Upgrade existing line |  | Stryker Creek | Gresham Road | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6054 | 2017-05-15 |  | 138 | 0 | 9.1 | 0 |  | Cherokee | Rusk | Tier 4 |  |  |  | 3110, 3301 | Y | N |  |  | 4628 | 4257
4258 | Centerville Switch - Lake Hubbard 138 kV Line | Upgrade existing double-circuit 138 kV line |  | Centerville Sw | Lake Hubbard | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4126 | 2017-05-15 |  | 138 | 0 | 13.5 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2401, 2402, 2439, 2450 | Y | N |  |  | 4629 | 4258
4263 | Tyler West - Tyler NW 138 kV Line | Upgrade existing line |  | Tyler West | Tyler NW | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6053 | 2017-05-15 |  | 138 | 0 | 3.7 | 0 |  | Smith | Smith | Tier 4 |  |  |  | 3139, 3141 | Y | N |  |  | 4636 | 4263
14TPIT0010 | Handley - Pantego - Sherry 138 kV line | Upgrade existing line |  | Handley | Sherry | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5155-E | 2017-05-15 |  | 138 | 0 | 8.9 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1919, 1950, 2245, 2247, 2250, 2251 | Y | N |  |  | 4638 | 2582
4267 | Andrews County South - North Andrews 138 kV Line | Upgrade existing line |  | Andrews County South | North Andrews | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8235 | 2017-05-15 |  | 138 | 0 | 18 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1150, 1153, 1155, 1157, 1159 | Y | N |  |  | 4640 | 4267
11TPIT0033 | Saginaw - North Main 138 kV Line | Upgrade existing 138 kV line |  | Saginaw | North Main | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5070-E | 2017-05-15 |  | 138 | 0 | 5.5 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1957, 1961, 2146, 2148 | Y | N |  |  | 4642 | 4269
4275 | Hutto Switching Station 138 kV capacitors | Install shunt capacitors |  | Hutto Switching Station |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R798 | 2017-05-15 |  | 138 | 0 | 0 | 0 | 0,18.4 | Williamson |  | Tier 4 |  |  |  | 3666 | Y | N |  |  | 4649 | 4275
4280 | Allen Switching Station 138 kV series reactor | Install series reactor on 345/138 kV autotransformer #2 |  | Allen Switching Station |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R961 | 2017-05-15 |  | 138 | 0 | 0 | 0 |  | Collin |  | Tier 4 |  |  |  | 12514, 2512, 2514, 12512 | Y | N |  |  | 4655 | 4280
4282 | Lewisville Switch - Lewisville Jones Street 138 kV Line | Upgrade existing line |  | Lewisville Switch (Brazos) | Lewisville Jones Street (TNMP) | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R966 | 2017-05-15 |  | 138 | 0 | 0.3 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 645, 1973 | Y | N |  |  | 4657 | 4282
17TPIT0014 | Copperas Cove 138 kV capacitors | Install shunt capacitor |  | Copperas Cove |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R786-E | 2017-05-15 |  | 138 | 0 | 0 | 0 | 0,18.4 | Coryell |  | Tier 4 |  |  |  | 3630 | Y | N |  |  | 4658 | 3108
17TPIT0028 | Temple Switch - Belton 138 kV Line | Upgrade existing line |  | Temple Switch | Belton | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R784 | 2017-05-15 |  | 138 | 0 | 12.9 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 3415, 3602, 3610, 3611, 3612 | Y | N |  |  | 4659 | 3182
4304 | Tradinghouse - Sam Switch 345 kV Line | Upgrade existing double-circuit line |  | Tradinighouse | Sam Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R1706 | 2017-05-15 |  | 345 | 0 | 45.4 | 0 |  | McLennan | Hill | Tier 4 |  |  |  | 3405, 13405, 68090 | Y | N |  |  | 4685 | 4304
4330 | Sargent Road - Industrial BLVD 138 kV Line | Upgrade existing line |  | Sargent Road | Industrial BLVD | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4128 | 2017-05-15 |  | 138 | 0 | 5.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2947, 2972, 2975 | Y | N |  |  | 4707 | 4330
4518 | Midessa South 345/138 kV autotransformer | Install 345/138 kV autotransformer in the existing Midessa South Switching Station |  | Midessa South |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8259 | 2017-05-15 |  | 345 | 0 | 0 | 600 |  | Midland |  | Tier 4 |  |  |  | 1125, 1058, 11028, 1124 | Y | N |  |  | 4915 | 4518
4549 | Permian Basin - Barilla Junction (AEP) 138 kV Line | Rebuild Oncor's section of the existing line |  | Permian Basin | Barilla Junction (AEP) | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8272 | 2017-05-15 |  | 138 | 0 | 15 | 0 |  | Ward | Pecos | Tier 3 |  |  |  | 1009, 6656 | Y | N |  |  | 4951 | 4549
4230 | Midland East - Goddard 138 kV Line | Upgrade existing line |  | Midland East | Goddard | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8205 | 2017-05-17 |  | 138 | 0 | 9 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1023, 1184 | Y | N |  |  | 4601 | 4230
3682A | Katy Area Upgrades | Convert Franz Substation to loop service from 138kV Ckt.09. Install new conductor and reconfigure/upgrade existing lines to create new Ckt.09 Zenith to Franz to Katy. |  | Zenith | Katy | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 860 | 2017-05-29 |  | 138 | 6.4 | 1.6 | 0 |  | Harris | Waller | Tier 2 | 2013-12-18 | 2014-05-15 |  | 44260, 44261, 44262, 44420, 44421, 44422, 44910, 45770 | Y | N |  |  | 3921 | 3682
3682B | Katy Area Upgrades | Convert Katy substation ckt 09 tap to loop service to modify Ckt.09 Flewellen to Katy to Franz. |  | Katy |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 860 | 2017-05-30 |  | 138 | 0 | 0 | 0 |  | Waller |  | Tier 2 | 2013-12-18 | 2014-05-15 |  | 44420, 44421, 44230, 44422, 45770 | Y | N |  | Cost included in project 17TPIT3682A. | 3922 | 3682
4446 | Luling to Nixon Transmission Line Overhaul | Upgrade the 15.62 mile Luling (7223) - Malone - Darst Creek - Deer Creek (7597) 69kV transmission line to 795 ACSR Drake (111 MVA), 138kV capable with OPGW shield wire. |  | Luling | Deer Creek | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014350 | 2017-05-30 |  | 69 | 0 | 15.62 | 0 |  | Caldwell | Guadalupe | Tier 3 |  |  |  | 7223, 7597, 78195, 78579 | Y | N |  |  | 4834 | 4446
4458 | Altair to Glidden Transmission Line Overhaul | Upgrade the 12.2 mile Altair (78106) - Stafford Hill (78520) - Columbus (78111) - Glidden (78107) 69-kV transmission line to 795 ACSR Drake (111 MVA), 138-kV capable with OPGE shield wire. |  | Altair | Glidden | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2017-05-30 |  | 69 | 0 | 12.2 | 0 |  | Colorado | Colorado | Tier 4 |  |  |  | 78106, 78107, 78111, 78520 | Y | N |  |  | 4843 | 4458
15TPIT0057 | Wylie 138 kV new switchyard and connections | Wylie 138 kV switchyard and its connections to Olinger, to Firewheel, to Elm Grove, and to Nevada | On Hold For Funding | New switches at Wylie | Switches at Olinger, at Friewheel, at Elm Grove, and at Nevada | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2017-05-31 |  | 138 | 0 | 36.75 | 0 |  | Collin | Dallas | Tier 4 |  |  |  | 833, 811, 818, 821, 855 | Y | N |  |  | 2750 | 2629
17TPIT0008 | Marion to Cibolo T-Line (T-302) Circuit Addition | Add another 138 kV circuit, to existing Marion to Cibolo T-Line (T-302), 1192 ACSR, 4.81 miles |  | Marion | Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2017-05-31 |  | 138 | 4.81 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 4 |  |  |  | 7178, 7608 | Y | N |  |  | 2962 | 2792
20TPIT0000 | Parkway Substation | Replace T1, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2017-05-31 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7611 | Y | N |  |  | 3504 | 3323
3663 | College Hills: Replace 138/69 kV autotransformer | Add 138/69 kV autotranformer capacity at College Hills |  | College Hills |  | Planned | 641 - 0810 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 1805 | 2017-05-31 |  | 138 | 0 | 0 | 90 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6468, 6470 | Y | N |  |  | 3900 | 3663
3664 | San Angelo North: Replace 138/69 kV autotransformer | Add 138/69 kV autotranformer capacity at San Angelo North |  | San Angelo North |  | Planned | 642 - 0811 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 1806 | 2017-05-31 |  | 138 | 0 | 0 | 90 |  | Tom Green | Tom Green | Tier 4 |  |  |  | 6462, 6464 | Y | N |  |  | 3901 | 3664
3673 | TNC Mason to LCRA Ft. Mason: Rebuild 69 kV line | Rebuild TNC Mason to LCRA Ft. Mason 69 kV line with 959.6 ACSR/TW |  | TNC Mason | LCRA Ft. Mason | Planned | 646 - 0815 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 1810 | 2017-05-31 |  | 69 | 0 | 0.15 | 0 |  | Mason | Mason | Tier 4 |  |  |  | 6393, 76388 | Y | N |  |  | 3910 | 3673
3682C | Katy Area Upgrades | Install a second 800MVA autotransformer at Zenith Substation. |  | Zenith |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 860 | 2017-05-31 |  | 345 | 0 | 0 | 800 |  | Harris |  | Tier 2 | 2013-12-18 | 2014-05-15 |  | 49090, 44900, 44910 | Y | N |  | Cost included in project 17TPIT3682A. | 3923 | 3682
14TPIT0067 | Red Creek: Replace 345/138 kV autotransformers | Replace both 345/138 kV autotransformers at Red Creek with 480 MVA autotransformers | Project Title and Company Contact Update | Red Creek |  | Planned | 566 - 0740 | AEP TNC | Rick McCracken 918-599-2664 | 2570 | 2017-05-31 |  | 345 | 0 | 0 | 960 |  | Tom Green |  | Tier 4 |  |  |  | 6295, 6769, 6444, 6442 | Y | N |  |  | 4185 | 1824
3900 | LaPalma to Stewart Road: Rebuild 69 kV line | Rebuild La Palma to Stewart Road 69 kV line with 959.6 ACSS/TW and add 138/69 kV autotransformer capacity at Stewart Road |  | La Palma | Stewart Road | Conceptual | 678 - 0847 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2597 | 2017-05-31 |  | 69 | 0 | 40.9 | 130 |  | Cameron | Hidalgo | Tier 3 |  |  |  | 8310, 8748, 8751, 8949, 8951 | Y | N |  |  | 4195 | 3900
3963 | Lockhart to Luling Transmission Line Upgrade | Upgrade the 16.9 miles Lockhart to Luling City 138kV line from existing 136 MVA to 221 MVA. Replace existing 45 MVA auto with 70 MVA auto. Upgrade both Lockhart and Luling to breaker and a half configuration. |  | Lockhart | Luling | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014350 | 2017-05-31 |  | 138 | 0 | 16.9 | 70 |  | Caldwell | Caldwell | Tier 4 |  |  |  | 7216, 7224, 7559, 7215 | Y | N |  |  | 4284 | 3963
4487 | Sagan: Build new 69 kV station | Construct new Sagan station along the Valero East to Valero West 69 kV line, add 138/69 kV autotransformer capacity at Sagan, and build new Sagan to Champlin 138 kV line with 959.6 ACSS/TW |  | Champlin | Valero West | Planned | 709 - 0879 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2903 | 2017-05-31 |  | 138 | 1 | 0 | 130 |  | Nueces |  | Tier 4 |  |  |  | 8859, 8477 | Y | N |  |  | 4881 | 4487
4489 | Eagle Pass to Escondido: Rebuild 138kV line | Rebuild Eagle Pass to Escondido Circuit #1 with 959.6 ACSS/TW |  | Eagle Pass | Escondido | Planned | 708 - 0878 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2902 | 2017-05-31 |  | 138 | 0 | 1.5 | 0 |  | Maverick |  | Tier 4 |  |  |  | 8270, 8260 | Y | N |  |  | 4883 | 4489
4490 | LaPalma: Add 2nd 345/138 kV autotransformer | Add 345/138 kV autotransformer capacity at LaPalma |  | LaPalma |  | Conceptual | 710 - 0880 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2904 | 2017-05-31 |  | 345 | 0 | 0 | 675 |  | Cameron |  | Tier 4 |  |  |  | 8356, 8317, 8314 | Y | N |  |  | 4892 | 4490
16TPIT0013 | Skyline to Spruce - 345 kV Substation Equipment Upgrade | Replace the Line MDS at Skyline and Spruce (both circuits) and ensure all terminals have a 2420 A rating and remove existing MLSE on Skyline to Spruce 345 kV transmission lines (both circuits) |  | Skyline | Spruce | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0468 | 2017-06-01 |  | 345 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5371, 5400 | Y | N |  | There are no transformers associated with this project | 971 | 970
16TPIT0010 | Bulverde - New 138kV Substation | Loop new 138kV substation into the existing Green Mountain to Stonegate transmission line |  | Green Mountain | Stonegate | Planned | T-0189 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0665 | 2017-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5051, 5180, 5415 | Y | N |  | There are no transformers associated with this project | 972 | 971
10TPIT0025 | Rinard Creek 138kV substation | Establish 138kV Rinard Ck substation with (2) 30MVA transformers and will cut into existing Ckt 987 (Lytton Springs to Slaughter Lane). |  | Rinard Creek substation | Rinard Creek Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | PLAN_117_P151 PLAN_117_P152 | 2017-06-01 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9262, 9075, 9267 | Y | N |  |  | 1031 | 1030
16TPIT0007 | McNeil to MagPlant Ckt 977 Upgrade | Reconductor existing McNeil to MagPlant circuit from 2000 to 3000 Amp. Relocate McNeil to Summit Circuit 907 and McNeil to MagPlant Circuit 977 to separate structures |  | McNeil Substation | Mag Plant Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | P396 | 2017-06-01 |  | 138 | 0 | 3.24 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9077, 9238 | Y | N |  | Will add the ptoject to the base case. | 1032 | 1031
11TPIT0084 | Hidden Lakes - New Substation | Build a new 138-12.47 kV substation to accommodate new subdivision growth along the FM 517 and FM 646 corridors in Dickinson, Texas |  | Leave blank | Leave blank | Planned |  | TNMP | Anthony Hudson Anthony.Hudson@tnmp.com. 281-581-4712 | STE02416 | 2017-06-01 |  | 138 | 0 | 0 | 0 |  | Galveston |  | Tier 4 |  |  |  | 38900, 38890, 42015 | Y | N |  |  | 1264 | 1261
16TPIT0005 | Farmersville West to Princeton South - new 138 kV line. | Build approximately 7.5 miles of 138 kV transmission line from Farmersville West Substation to Princeton South Substation. |  | Farmersville West | Princeton South | Planned | New projects added on rows 18 and 19. Please add TPIT numbers here after they have been assigned. | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE08016 | 2017-06-01 |  | 138 | 7.5 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 37291, 37295 | Y | N |  |  | 2064 | 2012
16TPIT0003 | Longneck to Princeton South - new 138 kV line | Build 3.5 miles of 138kV transmission line from Longneck Substation to Princeton South Substation. | Budget | Longneck | Princeton South | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07317 | 2017-06-01 |  | 138 | 3.5 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 37250, 37280, 37295 | N | N |  |  | 2065 | 2013
3334 | Fort Sam to Kirby MLSE Upgrade | Upgrade terminals at Fort Sam and ensure a rating of 2000 A at both Fort Sam and Kirby terminals. |  | Fort Sam | Kirby | Planned | S-0747 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2017-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5160, 5250 | Y | N |  | There are no transformers associated with this project | 3517 | 3334
3819 | Rebuild San Miguel Tap to North Calliham | Rebuild 4-0 ACSR 69 kV to higher rated and 138 kV capable line, as originally recommended in 2013 RTP. |  | Sam Miguel Tap | North Calliham | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2017-06-01 |  | 69 | 0 | 15.8 | 0 |  | Atascosa | McMullen | Tier 4 |  |  |  | 5693, 5698 | Y | N |  |  | 4101 | 3819
4081 | CPSE_Skyline to Marion Reconfiguration | Reconfigure 4 - 345 kV transmission lines. Skyline to Marion and Skyline to Elm Creek will become double circuit lines from Skyline to Elm Creek. Hill Country to Marion and Hill Country to Elm Creek become double circuit lines from Hill Country to Marion. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0231 | 2017-06-01 |  | 345 | 0 | 0 | 0 |  | Bexar | Guadalupe | Tier 1 | 2014-06-27 |  |  | 5133, 5211, 5371, 7044 | Y | N |  |  | 4431 | 4081
4139 | DME_Locust-Spencer |  |  | Pockrus | Spencer | Planned | N/A | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2017-06-01 |  | 69 | 0 | 1.91 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 902, 904, 914, 981 | Y | N | N/A |  | 4484 | 4139
4443 | CPSE_Fort Sam to Tenth Street MLSE | Upgrade terminals at Fort Sam and ensure a rating of 2000 A at Fort Sam for the Fort Sam to Tenth Street transmission circuit. |  | Forth Sam | Tenth Street | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2017-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5160, 5420 | Y |  |  |  | 4830 | 4443
19TPIT0000 | Weser Substation | Replace 5.6 MVA with 69-13.09 kV, 20 MVA transformer |  | Weser |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2017-06-30 |  | 69 | 0 | 0 | 0 |  | Goliad |  | Tier 4 |  |  |  | 7239 | Y | N |  |  | 3519 | 3336
3761 | Victoria to Fannin: 69 kV Transmission Line Rebuild | Rebuild Victoria to Fannin 69 kV line | Add Super project, and transmission status, ISD | VICTORIA | FANNIN | Under Construction | 662-0831 | AEP TCC | Frank Pritzlaff gareed@aep.com 918-599-2664 | 3527 | 2017-06-30 |  | 69 |  | 13.5 |  |  | Victoria | Victoria | Tier 4 |  |  |  | 5736, 8169 | Y | N |  |  | 4006 | 3761
3897 | Add New FM758 Sub | Construct a new 138-kV FM758 (7758) substation, which will cut into the LCRA TSC Clear Springs (7680) to Freiheit (7462) 138-kV transmission line |  | FM758 | Freiheit Road / Clear Springs | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2017-06-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7758, 7462, 7680 | Y | N |  |  | 4847 | 3897
4496 | AEP_4496_Las Pulgas | Loop STEC radial 138kV Raymondville #2 to East Raymondville line into Las Pulgas. |  | Las Pulgas |  | Planned | 615 - 3446 | AEP TCC | Glen Reed 918-599-2664 | 516 | 2017-06-30 |  | 138 | 0 | 0 | 0 |  | Willacy |  | Tier 4 |  |  |  | 80309 | Y | N |  |  | 4890 | 4496
3463 | Shady Bus Split | Reconfigure 69kV bus |  |  |  | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2017-07-01 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  |  | 3668 | 3463
4546 | Upgrade 138kV Vealmoor - Salt Mine line |  |  | Vealmoor | Salt Mine | Planned |  | SLU | Brad Schwarz 512-289-7425 |  | 2017-07-01 |  | 138 | 0 | 54.5 | 0 |  | Borden | Mitchell | Tier 4 |  |  |  | 79559, 79603, 79604, 79600, 79605 | Y | N |  |  | 4948 | 4546
4574 | Briarcrest to Nall Cable Upgrade |  |  | 32877 | 32872 | Planned |  | BRYN |  |  | 2017-09-01 |  | 69 | 0 | 0.5 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32872, 32877 | Y |  |  |  | 4981 | 4574
16TPIT0024 | Hamilton Road to Escondido: Rebuild 138kV Line | Rebuild Hamilton Road to Escondido 138 kV line | Reformated project number to match other numbers | Hamilton Road | Escondido | Conceptual | 602 - 0764 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 3471 | 2017-09-30 |  | 138 | 0 | 53.7 | 0 |  | Val Verde | Maverick | Tier 3 |  |  |  | 8255, 8260, 8264, 8692 | N | N |  | 0 | 2655 | 2550
4504 | BRYN_4504_Rayburn_Nall_Upgrade |  |  | 32861 | 32872 | Planned |  | BRYN |  |  | 2017-09-30 |  | 69 | 0 | 1.06 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32861, 32872 | Y |  |  |  | 4901 | 4504
4577 | BRYN_4577_Dansby_Rebuild | Convert Dansby 69kV bus to Breaker and a Half configuration |  |  |  | Planned |  | BRYN |  |  | 2017-09-30 |  | 69 | 0 | 0 | 200 |  | Brazos |  | Tier 4 |  |  |  | 32897, 32875 | Y |  |  |  | 4984 | 4577
4456 | Gilleland Creek Auto Transformer | Install a new 345/138 kV 672 MVA auto transformer at Gilleland Creek substation. |  | Gilleland Creek |  | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2017-10-31 |  | 345 | 0 | 0 | 672 |  | Travis |  | Tier 4 |  |  |  | 77998, 7340, 7336 | Y | N |  |  | 4841 | 4456
16TPIT0009 | Five Points to Westside - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from Five Points to Westside to be upgraded to 326 MVA, minimum |  | Five Points | Westside | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0195 | 2017-12-01 |  | 138 | 0 | 3.8 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5150, 5490 | Y | N |  | There are no transformers associated with this project | 974 | 973
17TPIT0005 | St. Jo Autos | Replace 40 MVA autos with 60 MVA autos |  | St. Jo | St. Jo | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12005 | 2017-12-01 |  | 138 | 0 | 0 | 40 |  | Cooke |  | Tier 4 |  |  |  | 750, 746 | Y | N |  |  | 2316 | 2243
17TPIT0001 | 36th St to Merida - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from 36th Street to Merida |  | 36th Street | Merida | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0196 | 2017-12-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5310, 5427 | Y | N |  | There are no transformers associated with this project | 2384 | 2308
07TPIT0236 | N. Terrell Tap - Rose Hill 138 kV line | Rebuild existing line |  | N. Terrell Tap | Rose Hill | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3059-E | 2017-12-15 |  | 138 | 0 | 8.7 | 0 |  | Kaufman | Kaufman | Tier 4 |  |  |  | 2714, 2715, 2717, 2719, 2723 | Y | N |  |  | 3100 | 2925
17TPIT0027 | Stryker Creek - Jacksonville 138 kV Line | Upgrade existing line |  | Stryker Creek | Jacksonville | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6030 | 2017-12-15 |  | 138 | 0 | 16.4 | 0 |  | Cherokee | Cherokee | Tier 4 |  |  |  | 3110, 3112, 3253 | Y | N |  |  | 3289 | 3120
08TPIT0104 | Elgin Switching Station - Elgin 69 kV line conversion to 138 | Rebuild existing 69 kV line and convert to 138 kV operation |  | Elgin Switching Station | Elgin | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R471-E | 2017-12-15 |  | 138 | 0 | 5.9 | 0 |  | Williamson |  | Tier 4 |  |  |  | 3655, 3650, 3651, 3674, 13674 | Y | N |  |  | 3478 | 1335
4207 | Bowman - Lake Wichita 138 kV Line | Upgrade existing line |  | Bowman | Lake Wichita | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R952 | 2017-12-15 |  | 138 | 0 | 5.6 | 0 |  | Archer | Wichita | Tier 4 |  |  |  | 1424, 1446 | Y | N |  |  | 4564 | 4207
4213 | Morgan Creek - Sun Switching Station 138 kV Line | Upgrade existing line |  | Morgan Creek | Sun Switching Station | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R9005 | 2017-12-15 |  | 138 | 0 | 33.9 | 0 |  | Mitchell | Scurry | Tier 3 |  |  |  | 1032, 1064 | Y | N |  |  | 4574 | 4213
4234 | Permian Basin - Moss 138 kV Line | Upgrade existing line |  | Permian Basin | Moss | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8208 | 2017-12-15 |  | 138 | 0 | 35.2 | 0 |  | Ward | Ector | Tier 3 |  |  |  | 1009, 1019 | Y | N |  |  | 4607 | 4234
4261 | Centerville Switch - Centerville - Lake Hubbard 138 kV Line | Upgrade existing double-circuit 138 kV line |  | Centerville Switch | Lake Hubbard | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4127 | 2017-12-15 |  | 138 | 0 | 26 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2401, 2402, 2439, 2450, 2917, 2918 | Y | N |  |  | 4632 | 4261
4303 | Lake Creek - Tradinghouse 345 kV Line | Upgrade existing double-circuit line |  | Lake Creek | Tradinghouse | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R1709 | 2017-12-15 |  | 345 | 0 | 19 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3402, 3409, 3405, 13405 | Y | N |  |  | 4684 | 4303
3505 | Cibolo Substation | Add T3, 40 MVA 138-26.18 kV power transformer, CSW and low side |  | Cibolo |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2017-12-29 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7608 | Y | N |  |  | 3712 | 3505
3480 | Cassava to Yucca: Rebuild 69 kV line | Rebuild 69 kV line as 138 kV from Cassava (Barnhart Phillips Tap) to Yucca with 795 ACSR and add 138/69 kV autotransformer capacity at Cassava | Company Contact Update | Cassava | Yucca | Planned | 635 - 0804 | AEP TNC | Gregory Gibbs 918-599-2664 | 2591 | 2017-12-31 |  | 138 | 12.3 | 0 | 90 |  | Taylor | Taylor | Tier 4 |  |  |  | 6034, 6035, 6531, 60360, 6036, 60359 | Y | N |  |  | 3687 | 3480
16TPIT0034 | Coleto Creek to Tuleta: New 138 kV Line | Build a double circuit capable 138 kV circuit from Coleto Creek station to new Tuleta station. |  | COLETO CREEK | TULETA | Planned | 606-0771 | AEP TCC | FRANK PRITZLAFF GAREED@AEP.COM 918-2599-2664 | 3481 | 2017-12-31 |  | 138 | 56 | 0 | 0 |  | Goliad | Bee | Tier 1 | 2012-08-31 | 2012-12-27 | 2013-04-05 | 8595, 8162, 8590 | Y | N |  |  | 3702 | 3495
3774 | Olinger-Ben Davis Line Upgrade | Olinger to Ben Davis 138 kV line upgrade to 436 MVA ratings |  | Olinger | Ben Davis | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2017-12-31 |  | 138 | 0 | 17.25 | 0 |  | Collin | Dallas | Tier 4 |  |  |  | 818, 968 | Y | N |  |  | 4019 | 3774
3775 | Firewheel-WylieSW Line Upgrade | Firewheel to Wylie Switch 138 kV line upgrade to 436 MVA ratings |  | Firewheel | WylieSW | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2017-12-31 |  | 138 | 0 | 17.77 | 0 |  | Dallas | Collin | Tier 4 |  |  |  | 821, 833 | Y | N |  |  | 4020 | 3775
3776 | Big Lake to Powell Field Junction Tap: Rebuild 69 kV line | Rebuild Big Lake to Powell Field Junction Tap 69 kV line with 959.6 ACSS/TW |  | Big Lake | Powell Field Junction Tap | Planned | 667 - 0836 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2594 | 2017-12-31 |  | 69 | 0 | 12.76 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  | 6533, 6546, 6547, 6548 | Y | N |  |  | 4021 | 3776
4459 | Goldthwaite to Lampasas Transmission Line Upgrade | Convert the 18.2 mile Goldthwaite (7073) - San Saba (7078) 69-kV to 795 ACSR Drake 138-kV (223 MVA) and Convert the 33.3 mile San Saba (7078) - Lometa (7080) - Lampasas (7082) 69-kV to 795 ACSR Drake 138-kV (223 MVA). |  | Goldthwaite | Lampasas | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2017-12-31 |  | 138 | 0 | 51.5 | 0 |  | Mills | Lampasas | Tier 1 | 2014-11-11 |  |  | 7073, 7074, 7078, 7080, 7082, 7064, 7070, 7075 | Y | N |  |  | 4844 | 4459
4485 | Add new 345kV Limestone - Gibbons Crk double circuit line |  |  | Limestone | Gibbons Creek | Planned |  | CTT | Tim cook Tcook@lspower.com 636-534-3250 |  | 2018-05-01 |  | 345 | 70 | 0 | 0 |  | Limestone | Grimes | Tier 1 | 2013-07-29 | 2014-02-20 | 2014-04-08 | 967, 46020 | Y | Y |  |  | 4879 | 4485
07TPIT0140 | Tri Corner - Watermill 345 kV circuit | Upgrade existing circuit and connect to circuit from Trinidad |  | Tri Corner | Watermill | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4045B | 2018-05-15 |  | 345 | 0 | 11.4 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2427, 3123 | Y | N |  |  | 1824 | 1782
11TPIT0034 | Sargent Road 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  | Sargent Road |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M486-E | 2018-05-15 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 4 |  |  |  | 2946, 2949 | Y | N |  |  | 1826 | 1784
14TPIT0089 | North Main Switch third transmission source | Construct a third 138 kV line into North Main Switch |  | North Main Tap | North Main Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5161-E | 2018-05-15 |  | 138 | 4.4 | 4.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1961, 2158, 2105, 3011 | Y | N |  |  | 3110 | 2941
19TPIT0001 | Sargent Road - Cedar Crest 138 kV Line | Upgrade existing Sargent Road - Saint Augustine Tap line section |  | Sargent Road | Saint Augustine Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4090-E | 2018-05-15 |  | 138 | 0 | 3.9 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2941, 2951 | Y | N |  |  | 3264 | 3095
17TPIT0025 | Payne - Anna Tap 138 kV Line | Upgrade existing line |  | Payne | Anna Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R945-E | 2018-05-15 |  | 138 | 0 | 23 | 0 |  | Grayson | Collin | Tier 3 |  |  |  | 1740, 1750, 1751, 1753, 2528, 1752, 1758, 12704 | Y | N |  |  | 3387 | 3214
08TPIT0069 | Lake Creek - East Waco 138 kV line | Upgrade existing 138 kV line |  | Lake Creek | East Waco | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R470 | 2018-05-15 |  | 138 | 0 | 10.5 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3410, 3438, 3452 | Y | N |  |  | 3539 | 1348
4239 | Paul Davis - Paul Davis Tap 138 kV Line | Rebuild existing line as a double-circuit line |  | Paul Davis | Paul Davis Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8220 | 2018-05-15 |  | 138 | 12 | 12 | 0 |  | Dawson | Martin | Tier 4 |  |  |  | 1170, 1168, 1169, 18880 | Y | N |  |  | 4612 | 4239
4240 | Paul Davis - Texaco Mabee 138 kV Line | Construct new line. |  | Paul Davis | Texaco Mabee | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8213 | 2018-05-15 |  | 138 | 10 | 0 | 0 |  | Martin | Andrews | Tier 2 |  |  |  | 1169, 11175, 1177, 11177 | Y | N |  |  | 4613 | 4240
4253 | Eagle Mountain - Sansom 138 kV Line | Upgrade existing double-circuit Eagle Mountain - Sansom line section |  | Eagle Mountain | Sansom | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5213 | 2018-05-15 |  | 138 | 0 | 15 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1860, 1865, 2085, 2086, 11860 | Y | N |  |  | 4624 | 4253
4270 | Handley - Hemphill 138 kV Line | Upgrade existing line |  | Handley | Hemphill | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5214 | 2018-05-15 |  | 138 | 0 | 7.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1950, 2164, 2167 | Y | N |  |  | 4643 | 4270
4301 | Trinidad - Tri Corner 345 kV Line | Upgrade existing double-circuit line |  | Trinidad | Tri Corner | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4045A | 2018-05-15 |  | 345 | 0 | 80.6 | 0 |  | Henderson | Dallas | Tier 4 |  |  |  | 2432, 3124 | Y | N |  |  | 4682 | 4301
4355 | Cedar Hill - Sorcey Road 138 kV Line | Upgrade existing line |  | Cedar Hill | Sorcey Road | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4131 | 2018-05-15 |  | 138 | 0 | 4.8 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 3051, 3052, 3053, 3055 | Y | N |  |  | 4729 | 4355
4523 | Paul Davis Switching Station | Convert existing substation to a new 138 kV switching station |  | Paul Davis |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8288 | 2018-05-15 |  | 138 | 0 | 0 | 0 |  | Martin |  | Tier 4 |  |  |  | 1169 | Y | N |  |  | 4920 | 4523
4551 | China Grove - Amoco 69 kV Line | Rebuild existing line |  | China Grove | Amoco | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8310 | 2018-05-15 |  | 69 | 0 | 2.9 | 0 |  | Mitchell | Scurry | Tier 4 |  |  |  | 1319, 1373, 1375, 1374, 1376 | Y | N |  |  | 4953 | 4551
4554 | Snyder - Ennis Creek 69 kV Line | Rebuild existing line |  | Snyder | Ennis Creek | Planned |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8309 | 2018-05-15 |  | 69 | 0 | 10.9 | 0 |  | Scurry | Scurry | Tier 4 |  |  |  | 1306, 1400, 1401, 1402, 1411, 1412 | Y | N |  |  | 4956 | 4554
4246 | Odessa North second 138/69 kV autotransformer | Install second autotransformer |  | Odessa North |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8225 | 2018-05-18 |  | 138 | 0 | 0 | 150 |  | Ector |  | Tier 4 |  |  |  | 1123, 1122 | Y | N |  |  | 4620 | 4246
3937 | Brazos Valley Connection | Construct 345kV double circuit from Gibbons Creek to Zenith. |  | Gibbons Creek | Zenith | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 717 | 2018-05-30 |  | 345 | 63 | 0 | 0 |  | Harris | Grimes | Tier 1 | 2013-07-25 | 2014-02-20 | 2014-04-08 | 967, 44900 | Y | Y |  |  | 4893 | 3937
18TPIT0002 | Martinez - New 138kV Substation | Loop new 138kV substation into the existing 138kV Deely to Walzem line and the future 138kV Deely to Converse line |  | Deely | Walzem - Skyline | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2018-05-31 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5294, 5110, 5368, 5485 | Y | N |  | There are no transformers associated with this project | 2336 | 2263
22TPIT0000 | Parkway Substation | Replace T2, 20 MVA with a 40 MVA 138-13.09 kV transformer |  | Parkway |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2018-05-31 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7611 | Y | N |  |  | 3505 | 3324
3671 | Moran to Putnam: Rebuild 69 kV line | Rebuild Albany to Putnam 69 kV line with 959.6 ACSR/TW |  | Moran | Putnam | Planned | 645 - 0814 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 1807 | 2018-05-31 |  | 69 | 0 | 12.86 | 0 |  | Shackelford | Callahan | Tier 4 |  |  |  | 6209, 6307 | Y | N |  |  | 3908 | 3671
3683 | Ab South to Ab West TX Gulf Tap: Rebuild 69 kV line | Rebuild Abilene South to Abilene Power Station 69 kV line with 959.6 ACSR/TW |  | Abilene South | Abilene West Texas Gulf Tap | Planned | 651 - 0820 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 1815 | 2018-05-31 |  | 69 | 0 | 2.15 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6258, 6284 | Y | N |  |  | 3924 | 3683
3777 | Ozona to Midway Lane: Rebuild 69 kV line | Rebuild Ozona to Midway Lane 69 kV line with 959.6 ACSS/TW |  | Ozona | Midway Lane | Planned | 667 - 0836 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2594 | 2018-05-31 |  | 69 | 0 | 16.96 | 0 |  | Crockett | Crockett | Tier 4 |  |  |  | 6549, 6560 | Y | N |  |  | 4022 | 3777
3848 | Shell Powell Tap to SWTEC Powell Field: Rebuild 69 kV line | Rebuild Shell Powell Tap to SWTEC Powell Field with 959.6 ACSR/TW |  | Shell Powell Tap | SWTEC Powell Field | Planned | 670 - 0839 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2806 | 2018-05-31 |  | 69 | 0 | 5 | 0 |  | Reagan | Crockett | Tier 4 |  |  |  | 6540, 6545 | Y | N |  |  | 4132 | 3848
4323 | CPSE_Braunig to Brooks_MLSE | Upgrade terminal at Brooks and ensure a rating of 1364 A (minimum) at both Braunig and Brooks terminals |  | Braunig | Brooks | In-Service |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0669 | 2018-05-31 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5030, 5045 | Y | Y |  |  | 4700 | 4323
4453 | Henne to McCarty Lane Transmission Line Upgrade | Upgrade the 6.6 mile Henne (7172) - McCarty Lane (7182) 138-kV transmission line to single 959 ACSS Suwannee, 380 MVA. |  | Henne | McCarty Lane | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2018-05-31 |  | 138 | 0 | 6.6 | 0 |  | Comal | Hays | Tier 4 |  |  |  | 7172, 7182 | Y | N |  |  | 4838 | 4453
4454 | Henne to Comal Transmission Line Upgrade | Upgrade the 7.6 mile Henne (7174) - Comal (7176) 138-kV transmission line from 159 MVA to 380 MVA using single 959 ACSS Suwannee conductors. |  | Henne | Comal | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2018-05-31 |  | 138 | 0 | 7.6 | 0 |  | Comal | Comal | Tier 4 |  |  |  | 7174, 7176 | Y | N |  |  | 4839 | 4454
4488 | Campwood to Uvalde: Rebuild 69 kV line | Rebuild Campwood to Uvalde 69 kV line with 959.9 ACSS/TW and energize as 138 kV and add 138/69 kV autotransformer capacity at Campwood |  | Campwood | Uvalde | Planned | 707 - 0877 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 2901 | 2018-05-31 |  | 138 | 0 | 37.1 | 90 |  | Real | Uvalde | Tier 2 |  |  |  | 8230, 8633, 8231 | Y | N |  |  | 4882 | 4488
14TPIT0041 | Coliseum to Kirby - 138 kV Transmission Line Rebuild | Rebuild 4.2 miles of 138 kV transmission line from Coliseum to Holbrook to Kirby and ensure a minimum conductor rating of 331 MVA |  | Colesium | Kirby | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0164 | 2018-06-01 |  | 138 | 0 | 4.2 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5095, 5160, 5218, 5250, 5420 | Y | N |  | There are no transformers associated with this project | 956 | 955
15TPIT0004 | Converse - New 138kV Substation | Loop new 138kV substation into existing 138kV Deely to Skyline line |  | Converse | Martinez-Skyline | Planned | T-0177 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0601 | 2018-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5098, 5294, 5368 | Y | N |  | There are no transformers associated with this project | 968 | 967
16TPIT0006 | Climax to Longneck - Rebuild and conversion from 69 kV to 13 | Rebuild Climax to Longneck 69 kV transmission line and convert to 138 kV. |  | Climax | Longneck | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07618 | 2018-06-01 |  | 138 | 7.5 | 4.2 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 37260, 37250 | Y | N |  |  | 2066 | 2014
15TPIT0031 | Brooks to Chavaneaux - 138 kV Transmission Line Rebuild | Rebuild approximately four circuit miles of 138 kV transmission from Brooks to Chavaneaux |  | Brooks | Chavaneaux | Conceptual |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0207 | 2018-06-01 |  | 138 | 0.1 | 4 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5085, 5330 | Y | N |  | There are no transformers associated with this project | 2380 | 2304
3272 | Potranco - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to AMD line. |  | Cagnon | AMD | Planned | S-0753 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0219 | 2018-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5346, 5002, 5053 | Y | N |  | There are no transformers associated with this project | 3448 | 3272
3273 | Southton - New 138kV Substation | A new 138kV substation from 138kV Braunig to Brooks. |  | Southton | Braunig-Brooks | Planned | S-0750 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0217 | 2018-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5394, 5030, 5045 | Y | N |  | There are no transformers associated with this project | 3449 | 3273
3276 | JT Deely to Martinez MLSE Upgrade | Upgrade terminal at JT Deely to ensure a rating of 2386 A (minimum). |  | JT Deely | Martinez | Planned | S-0759 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2018-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5294, 5110 | Y | N |  | There are no transformers associated with this project | 3452 | 3276
3298 | Skyline - Install a Fourth 345kV Autotransformer. | Install one 600 MVA autotransformer at Skyline switchyard. |  |  |  | Planned | S-0670 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2018-06-01 |  | 345 | 0 | 0 | 600 |  | Bexar | Bexar | Tier 4 |  |  |  | 5372, 5371, 5368 | Y | N |  | There are no transmission line additions associated with this project | 3474 | 3298
3595 | Bevo to AEP Carrizo Springs 69 kV line | Add 2 mile line by double circuiting two existing circuits, as recommended in 2013 RTP. |  | Bevo | Carrizo Springs | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-06-01 |  | 69 | 0 | 2 | 0 |  | Dimmit | Dimmit | Tier 1 | 2012-04-12 | 2012-08-12 | 2012-09-12 | 5871, 8244 | Y | N |  |  | 3809 | 3595
3817 | George West autotransformer upgrade | Upgrade autotransformer at George West to 150 MVA as recommended in 2013 RTP. |  | George West Switch |  | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-06-01 |  | 138 | 0 | 0 | 150 |  | Live Oak |  | Tier 4 |  |  |  | 5686, 5688 | Y | N |  |  | 4099 | 3817
3818 | Rebuild Calallen to Robstown | Rebuild 4-0 ACSR 69 kV to higher rated and 138 kV capable line, as originally recommended in 2013 RTP. |  | Calallen | Robstown | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-06-01 |  | 69 | 0 | 6.26 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 5626, 5634 | Y | N |  |  | 4100 | 3818
3820 | Rebuild Sandia to AEP Mathis | Rebuild 69 kV 4-0 to 795 ACSR on 138 kV capable structures, as originally recommended in 2013 RTP. Only rebuild the 4-0 to 795 ACSR leave tap at 336 ACSR. |  | Sandia | AEP Mathis | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-06-01 |  | 69 | 0 | 7.93 | 0 |  | Jim Wells | San Patricio | Tier 4 |  |  |  | 5666, 8407 | Y | N |  |  | 4102 | 3820
3821 | Pearsall to Palo Duro 138 kV line upgrade | Upgrade Pearsall to Palo Duro 138 kV line as recommended in 2013 RTP |  | Pearsall | Paloduro | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-06-01 |  | 138 | 0 | 10.8 | 0 |  | Frio | Frio | Tier 4 |  |  |  | 5866, 5895 | Y | N |  |  | 4103 | 3821
3822 | San Miguel to Sigmor 138 kV line upgrade | Upgrade San Miguel to Sigmor 138 kV line as recommended in 2013 RTP |  | San Miguel | Sigmor | Planned |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2018-06-01 |  | 138 | 0 | 26.3 | 0 |  | Atascosa | Live Oak | Tier 3 |  |  |  | 5689, 5706, 8404 | Y | N |  |  | 4104 | 3822
3992 | Rebuild Dickinson - League City 138 kV line. | Rebuilding Dickinson to League City 138 kV (G138-09). |  | Dickinson Sub | League City Sub | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE07215 | 2018-06-01 |  | 138 | 0 | 3.6 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38850, 38920 | Y |  |  |  | 4318 | 3992
4082 | CPSE_Howard to Somerset Rebuild | Rebuild approximately seven miles of 138 kV transmission circuit from Howard to Somerset. The Howard to Somerset circuit should be upgraded to 469 MVA, minimum. |  | Howard | Somerset | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0232 | 2018-06-01 |  | 138 | 0 | 7.56 | 0 |  | Bexar | Bexar | Tier 2 | 2014-05-07 | 2014-09-04 |  | 5230, 5390 | Y | N |  |  | 4432 | 4082
4138 | DME_Hickory_Locust |  |  | Hickory | Locust | Planned | N/A | DME | Chuck Sears cxsears@cityofdenton.com 940-349-7111 |  | 2018-06-01 |  | 69 | 0 | 2.5 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 910, 914, 926 | Y | N | N/A |  | 4483 | 4138
4321 | Add Eagle Station |  |  | Hickory | Locust | Planned |  | DME | Chuck Sears 940-349-7111 |  | 2018-06-01 |  | 69 | 0 | 0 | 0 |  | Denton |  | Tier 4 |  |  |  | 926, 910, 914 | Y | N |  |  | 4698 | 4321
11TPIT0011 | Northeast 138kV Substation | Establish a 138kV substation with (2) 30MVA transformers and 4 distribution circuits with underground get-a-ways. The station will cut into existing Gilleland - Techridge line. | Original Project title is "East Substation" | Northeast Substation | Northeast Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | PLAN_117_P142 PLAN_117_P143 PLAN_117_P144 | 2018-06-15 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9195, 9054, 9190 | Y | N |  |  | 1053 | 1052
3877 | Meadow Lake Substation | Build a new 138-26.18 kV 24/32/40 MVA substation, tie into Cushman - Hwy123 138kV Ckt |  | Meadow Lake | Cushman / Hwy 123 | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7221 | N | N |  |  | 4167 | 3877
15TPIT0069 | AEP_Angstrom | Add 138 kV PST |  | RAYMONDVILLE #2 | LOYOLA | Planned | 592 - 0769 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 3479 | 2018-06-30 |  | 138 | 0 | 0 | 0 |  | Kenedy |  | Tier 4 |  |  |  | 8134, 8530, 5648, 8899 | Y | N | NA |  | 4385 | 3354
13TPIT0045 | Blumenthal Substation | Construct a new 11.5 mile 138 kV transmission line from a tap point on the Kendall CTEC (7147) - Mountain Top (7148)138 kV transmission line to the new Blumenthal substation (7418) using 336 ACSR Linnet. | Delayed from initial May 2013 in-service date | Blumenthal | Kendall CTEC-Mountain Top | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1010656 | 2018-09-27 |  | 138 | 8.4 | 0 | 0 |  | Kendall |  | Tier 2 |  |  |  | 7418, 7419, 7147, 7148 | Y | N |  |  | 991 | 990
4505 | BRYN_4505_New_Annex | Construction of a New Annex Substation at 138kV |  |  |  | Planned |  | BRYN |  |  | 2018-09-30 |  | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32853 | Y |  |  |  | 4902 | 4505
4567 | BRYN_4567_New_Annex_Line | Loop in new Annex Substation at 138kV |  | 32897 | 32863 | Planned |  | BRYN |  |  | 2018-09-30 |  | 138 | 0.75 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32853, 32863, 32897 | Y |  |  |  | 4974 | 4567
4572 | Atkins Bus Work for Power Transformer addition |  |  | 32864 |  | Planned |  | BRYN |  |  | 2018-09-30 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  | No MOD changes necessary | 4979 | 4572
4271 | Handley - Sherry 138 kV Line | Upgrade existing Hurst - Brookhollow line section |  | Handley | Sherry | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5216 | 2018-11-15 |  | 138 | 0 | 9.8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2116, 2121, 2134, 2244 | Y | N |  |  | 4644 | 4271
13TPIT0187 | Harlandale to Sommers - 138 kV Transmission Line Rebuild | Rebuild approximately 40 circuit miles of 138 kV transmission from Harlandale to Sommers |  | Harlandale | Sommers | Planned | S-0732 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0192 | 2018-12-01 |  | 138 | 0.1 | 40 | 0 |  | Bexar | Bexar | Tier 3 |  |  |  | 5190, 5385, 5395 | Y | N |  | There are no transformers associated with this project | 2379 | 2303
15TPIT0020 | Braunig to Highland Hills-Brooks - 138 kV Substation Equipme | Replace Line and Bus Switches at Brooks and ensure a 1385 A rating and remove existing MLSE on the Brooks to Southton 138 kV transmission line |  | Braunig_W | Highland Hills-Brooks | Planned | T-0194 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2018-12-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 3 |  |  |  | 5030, 5045, 5175, 5205, 5394 | Y | N |  | There are no transformers associated with this project | 2385 | 2309
4550 | China Grove - Snyder 69 kV Line | Rebuild existing line |  | China Grove | Snyder | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8311 | 2018-12-15 |  | 69 | 0 | 13.1 | 0 |  | Mitchell | Scurry | Tier 4 |  |  |  | 1306, 1319, 1376 | Y | N |  |  | 4952 | 4550
4552 | Permian Basin - Crane 69 kV Line | Rebuild existing line |  | Permian Basin | Crane | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8305 | 2018-12-15 |  | 69 | 0 | 42.3 | 0 |  | Ward | Crane | Tier 3 |  |  |  | 1015, 1198, 1202, 1203, 1204, 1206, 1205, 1207, 1238 | Y | N |  |  | 4954 | 4552
4553 | Permian Basin - Northern Natural 69 kV Line | Rebuild existing line |  | Permian Basin | Northern Natural | Planned |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8295 | 2018-12-15 |  | 69 | 0 | 46.5 | 0 |  | Ward | Pecos | Tier 4 |  |  |  | 1015, 1238, 1239, 1240, 1241, 1242 | Y | N |  |  | 4955 | 4553
3948 | Steamboat to Tuscola: Rebuild 69 kV line | Rebuild Winters to Steamboat and Steamboat to Tuscola | Schedule Update | Steamboat | Tuscola | Planned | 685 - 0855 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 1851 | 2018-12-31 |  | 69 | 0 | 9.856 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 6328, 6331, 60332 | Y | N |  |  | 4266 | 3948
3949 | Steamboat to Winters: Rebuild 69 kV line | Rebuild Winters to Steamboat and Steamboat to Tuscola | Schedule Update | Steamboat | Winters | Planned | 685 - 0855 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 1850 | 2018-12-31 |  | 69 | 0 | 9.944 | 0 |  | Taylor | Runnels | Tier 4 |  |  |  | 6333, 60332 | Y | N |  |  | 4267 | 3949
10TPIT0027 | West Batesville, Install 138 kV ring bus | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus | CHANGES | WEST BATESVILLE |  | Conceptual | 383 - 0560 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 2168 | 2019-03-31 |  | 138 | 0 | 0 | 0 |  | Zavala |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8236 | N | N | NA | NA | 3751 | 3543
10TPIT0028 | Escondido to West Batesville, build 138 kV Line | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus | CHANGES | ESCONDIDO | WEST BATESVILLE | Conceptual | 383 - 0560 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 2169 | 2019-03-31 |  | 138 | 46.2 | 0 | 0 |  | Maverick | Zavala | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8260 | N | Y | NA | NA | 3752 | 3544
4241 | Texaco Mabee Tap - Texaco Mabee 138 kV Line | Rebuild existing line as a double-circuit line |  | Texaco Mabee Tap | Texaco Mabee | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8221 | 2019-05-15 |  | 138 | 11.4 | 11.4 | 0 |  | Midland | Andrews | Tier 4 |  |  |  | 1171, 1169, 1175, 1177, 1179, 11175, 1184, 11177, 11179 | Y | N |  |  | 4614 | 4241
4259 | Wichita Falls second 138/69 kV autotransformer | Install 138/69 kV autotransformer |  | Wichita Falls |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R970 | 2019-05-15 |  | 138 | 0 | 0 | 150 |  | Wichita |  | Tier 4 |  |  |  | 1448, 1449 | Y | N |  |  | 4630 | 4259
4285 | Prairie Creek - Parkdale 138 kV Line | Upgrade existing double-circuit line |  | Prairie Creek | Parkdale | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4132 | 2019-05-15 |  | 138 | 0 | 5.6 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2441, 2442, 2445, 2743, 2762, 2763 | Y | N |  |  | 4662 | 4285
4300 | Venus - Navarro Switch 345 kV Line | Upgrade existing double-circuit line |  | Venus | Navarro Sw | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R1710 | 2019-05-15 |  | 345 | 0 | 93.4 | 0 |  | Ellis | Navarro | Tier 4 |  |  |  | 1906, 1907, 68091 | Y | N |  |  | 4681 | 4300
10TPIT0019 | Everman - Cleburne Switch 138 kV Line | Upgrade existing Everman - Mansfield line section |  | Everman | Mansfield | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5218 | 2019-05-15 |  | 138 | 0 | 7.7 | 0 |  | Tarrant | Johnson | Tier 4 |  |  |  | 1883, 2208 | Y | N |  |  | 4754 | 3092
4445 | Kerrville Stadium to Harper Road Transmission Line Upgrade | Upgrade the 1.6 mile Kerrville Stadium (7138) - Harper Road (7140) 138-kV transmission line to bundled 795 ACSR Drake, 440 MVA. |  | Kerrville Stadium | Harper Road | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2019-05-30 |  | 138 | 0 | 1.6 | 0 |  | Kerr | Kerr | Tier 4 |  |  |  | 7138, 7140 | Y | N |  |  | 4833 | 4445
3669 | Albany Foundry to Moran: Rebuild 69 kV line | Rebuild Albany to Putnam 69 kV line with 959.6 ACSR/TW |  | Albany Foundry | Moran | Planned | 645 - 0814 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 1808 | 2019-05-31 |  | 69 | 0 | 10 | 0 |  | Shackelford | Shackelford | Tier 4 |  |  |  | 6202, 6209 | Y | N |  |  | 3906 | 3669
4465 | Wirtz to FlatRock to Paleface Transmission Line Upgrade | Upgrade the 17.34 mile Wirtz (7104) - Flat Rock (7111) - Paleface (7477) 138-kV transmission line to single 795 ACSR Drake, 221 MVA. |  | Wirtz | Paleface | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2019-05-31 |  | 138 | 0 | 17.34 | 0 |  | Burnet | Travis | Tier 4 |  |  |  | 7104, 7111, 7477 | Y | N |  |  | 4851 | 4465
4473 | Zorn to Marion 2nd 345-kV Transmission Line Addition | Add 345-kV Zorn (7042) to Marion (7044) 2nd circuit using bundled Suwannee. Portion of the CPS-Tie Project. |  | Zorn | Marion | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2019-05-31 |  | 345 | 18 | 0 | 0 |  | Guadalupe | Guadalupe | Tier 1 | 2014-06-29 |  |  | 7042, 7044 | Y | N |  |  | 4859 | 4473
11TPIT0008 | Rainey St 138kV substation | Establish a new 138kV Rainey St substation with (2) 50MVA transformers and cut into existing Ckt 1015 (Pedernales to Seaholm). |  | Rainey St Substation | Rainey St Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | PLAN_117_P158 PLAN_117_P166 PLAN_117_P167 | 2019-06-01 |  | 138 | 0.1 | 0 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9261, 9118, 9132 | Y | N |  |  | 1033 | 1032
3277 | Shepherd Road - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Valley line. |  | Shepherd Road | Cagnon-Valley | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2019-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5378, 5053, 5465 | Y | N |  | There are no transformers associated with this project | 3453 | 3277
4083 | CPSE_Merida to Westside Rebuild | Rebuild approximately four miles of 138 kV transmission circuit from Merida to Westside. The Merida to Westside circuit should be upgraded to 349 MVA, minimum. |  | Merida | Westside | Planned | S-0773 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0235 | 2019-06-01 |  | 138 | 0 | 4 | 0 |  | Bexar | Bexar | Tier 1 |  |  |  | 5310, 5490 | Y | N |  |  | 4433 | 4083
4084 | Barton-Vega: Upgrade Ckt 928 | Reconductor to 2000 amps |  | Barton | Vega | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2019-06-01 |  | 138 | 0 | 4.05 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9158, 9285 | Y |  |  |  | 4434 | 4084
4320 | CPSE_Brooks to Chavaneaux MLSE | Upgrade terminals at Brooks and Chavaneaux to ensure a 1364 A rating (minimum) |  | Brooks | Chavaneaux |  |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0733 | 2019-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5045, 5085 | Y | Y |  |  | 4697 | 4320
4438 | BenDavis-Murphy 138kV Line Upgrade | BenDavis-Murphy 138kV Line Upgrade |  | Ben Davis | Murphy | Planned |  | GARLAND/GPL-TMPA and Oncor | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2019-06-01 |  | 138 | 0 | 4.3 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 968, 2696 | Y | Y |  |  | 4824 | 4438
4606 | Moulton South Substation 138/69-kV Autotransformer | Add Moulton South Substation 138/69-kV Autotransformer |  | Moulton South | Moulton | Conceptual |  | LCRATSC/GVEC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2019-07-01 |  | 138 | 0 | 0 | 45 |  | Lavaca |  | Tier 4 |  |  |  | 7588, 7237 | N | N |  |  | 5013 | 4606
3967 | Leander - Parmer - Round Rock Transmission Line Addition | Construct a new 138kV transmission line from Leander to Parmer (new substation) to Round Rock (approx 13 miles) using bundled 795 ACSR Drake (446 MVA) conductor. |  | Leander | Round Rock | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 | 1014352 | 2019-08-23 |  | 138 | 13 | 0 | 0 |  | Williamson | Williamson | Tier 2 | 2013-12-10 | 2014-05-22 |  | 7367, 3668, 7525 | Y | N |  |  | 4288 | 3967
4575 | BRYN_4575_New_Steele_Store |  |  |  |  | Planned |  | BRYN |  |  | 2019-09-30 |  | 138 | 0 | 0 | 0 |  | Burleson |  | Tier 4 |  |  |  | 32852 | Y |  |  |  | 4982 | 4575
4576 | BRYN_4576_Annex_to_Steele_Store |  |  | 32853 | 32852 | Planned |  | BRYN |  |  | 2019-09-30 |  | 138 | 10 | 0 | 0 |  | Brazos | Burleson | Tier 4 |  |  |  | 32852, 32853 | Y |  |  |  | 4983 | 4576
3754 | Heartland to Yellowjacket: Build 69 kV line | Build new 69 kV line from Heartland to Yellowjacket with 959.6 ACSR/TW | Project Title, Project Description, Schedule, and Cost Update | Heartland | Yellowjacket | Planned | 637 - 0806 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2592 | 2019-11-30 |  | 69 | 32 | 0 | 0 |  | Mason | McCulloch | Tier 2 | 2014-01-23 | 2014-11-17 |  | 6379, 60386, 6363, 6378, 6381, 6406 | Y | N |  |  | 4910 | 3754
4519 | Heartland: Build 69 kV station | Construct new 69 kV ring bus | New Project | Heartland |  | Planned | 637 - 0806 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2609 | 2019-11-30 |  | 69 | 0 | 0 | 0 |  | McCulloch |  | Tier 2 | 2014-01-23 | 2014-11-17 |  | 60386 | Y | N |  |  | 4916 | 4519
4530 | Heartland to South Brady Tap: Rebuild existing & build new | Construct a new 69 kV line from Heartland to South Brady Tap and rebuild the existing line from Heartland to South Brady Tap | New Project | Heartland |  | Planned | 637 - 0806 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 2610 | 2019-11-30 |  | 69 | 1.11 | 1.11 | 0 |  | McCulloch | McCulloch | Tier 2 | 2014-01-23 | 2014-11-17 |  | 6379, 60386, 6378, 6381, 6406 | Y | N |  |  | 4930 | 4530
13TPIT0106 | Killeen SS to Ding Dong | Rebuild 477 ACSR line with 955 ACSS |  | Killeen SS | Ding Dong | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 11037 | 2019-12-01 |  | 138 | 0 | 23.8 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 115, 117, 136, 3423 | Y | N |  |  | 2726 | 2608
14TPIT0057 | Cedar Hill - Mayfield Tap North 138 kV line | Upgrade existing line |  | Cedar HIll Switch | Mayfield Tap North | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5041-E | 2020-05-15 |  | 138 | 0 | 4.3 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 1912, 2422 | Y | N |  |  | 3101 | 2926
15TPIT0093 | Round Rock Westinghouse 138 kV capacitors | Install shunt capacitors |  | Round Rock Westinghouse |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R780 | 2020-05-15 |  | 138 | 0 | 0 | 0 | 0,36.8 | Williamson |  | Tier 4 |  |  |  | 3669 | Y | N |  |  | 3256 | 3087
4356 | Elm Mott - Bosque 138 kV Line | Upgrade existing line |  | Elm Mott | Bosque | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R1707 | 2020-05-15 |  | 138 | 0 | 19.3 | 0 |  | McLennan | Bosque | Tier 4 |  |  |  | 249, 252, 3407 | Y | N |  |  | 4730 | 4356
3670 | Albany to Albany Foundry: Rebuild 69 kV line | Rebuild Albany to Putnam 69 kV line with 959.6 ACSR/TW |  | Albany | Albany Foundry | Planned | 645 - 0814 | AEP TNC | Glen Reed gareed@aep.com 918-599-2664 | 1809 | 2020-05-31 |  | 69 | 0 | 5.13 | 0 |  | Shackelford | Shackelford | Tier 4 |  |  |  | 6202, 6207, 6213 | Y | N |  |  | 3907 | 3670
4477 | Austrop to Sandow Double 345-kV Transmission Line Upgrade | Upgrade 33.98-mile Austrop (7040) to Sandow (13429) 345-kV double circuit transmission lines to bundled 959 Suwannee conductor (1921 MVA). |  | Austrop | Sandow | Conceptual |  | LCRATSC/Oncor | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-05-31 |  | 345 | 0 | 67.96 | 0 |  | Travis | Milam | Tier 1 |  |  |  | 7040, 13429 | Y | N |  |  | 4863 | 4477
4479 | Cut T511 Gilleland Ck to CLear Springs to AEN Dunlap | Cut-In the existing Gilleland Creek (7340) to Clear Springs (7050) T511 345kV transmission line into Austin Energy's Dunlap (9044) substation. |  | Gilleland Creek | Clear Springs | Conceptual |  | LCRATSC/AEN | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2020-05-31 |  | 345 | 4 | 0 | 0 |  | Travis | Guadalupe | Tier 1 |  |  |  | 7050, 7340, 9044 | Y | N |  |  | 4868 | 4479
13TPIT0104 | Jack County Auto | Install 345-138 kV, 700 MVA auto at Jack County |  | Jack County | Jack County | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 11038 | 2020-06-01 |  | 345 | 0 | 0 | 700 |  | Jack |  | Tier 4 |  |  |  | 575, 579 | Y | N |  |  | 1184 | 1181
15TPIT0000 | Bird Pond Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138-12.5 transformer |  | Bird Pond | Bird Pond | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32858, 962, 964 | Y | N |  |  | 1855 | 1812
12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV OW Sommers to Kirby line |  | Sulpher Springs | OW Sommers-Kirby | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0385 | 2020-06-01 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5416, 5250, 5395 | Y | N |  | There are no transformers associated with this project | 3190 | 3021
3297 | Tezel Road - New 138kV Substation | Loop new 138 kV substation into the existing 138 kV Helotes to Bandera line. |  |  |  | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2020-06-01 |  | 0 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 5421, 5020, 5200 | Y |  |  | There are no transformers associated with this project | 3665 | 3297
4065 | Add Graham Road Substation |  |  | BTU South | BTU Greens Prairie | Planned |  | COCS | Tony Mickalsky tmichalsky@cstx.gov 979-764-3438 |  | 2020-06-01 |  | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32007, 32878, 32880 | Y |  |  |  | 4415 | 4065
06TPIT0082 | Buena Vista to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System |  | BUENA VISTA | PICACHO | Planned | 301-0449 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 1547 | 2020-06-30 |  | 138 |  | 3 |  |  | Val Verde | Val Verde | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8688 | Y | N |  |  | 3745 | 3537
4571 | Atkins Substation Upgrade | Rebuild Atkins 69kV bus |  | 32864 |  | Planned |  | BRYN |  |  | 2020-09-30 |  | 69 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  | No MOD Changes Necessary | 4978 | 4571
12TPIT0185 | Airline to Westside: Add 138kV Circuit | Add a Second 138kV Circuit between Airline and Westside | Change transmission status, ISD | AIRLINE | WESTSIDE | Planned | 587-0747 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 3464 | 2020-12-31 |  | 138 | 6.22 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8490 | N | N | NA | NA | 3753 | 3545
3999 | Airline to Holly: Build new 138 kV line | Build a new 138 kV line from Airline to Holly using the existing structures | Change transmission status, ISD | AIRLINE | HOLLY | Planned | 548-0747 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 3464 | 2020-12-31 |  | 138 | 1.69 |  |  |  | Nueces | Nueces | Tier 4 |  |  |  | 8486, 8490 | Y | N |  |  | 4325 | 3999
15TPIT0008 | Triple R - New Substation (7627) | Build a 138-26.18kV. 40 MVA substation on the GVEC Wilson-Sutherland Springs (T549) 138 kV transmission line |  | Triple R | Wilson/Sutherland Springs | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2020-12-31 |  | 138 | 0 | 0 | 0 |  | Wilson |  | Tier 4 |  |  |  | 7627, 5418, 7615 | Y | N |  |  | 4459 | 3367
11TPIT0036 | Caddo - New Substation | Construct a new 69-13.09x26.18-kV 10 MVA substation on GVEC La Vernia-GVEC Nixon 69 kV transmission line |  | Caddo | La Vernia/GVEC Nixon | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2020-12-31 |  | 69 | 0 | 0 | 0 |  | Wilson |  | Tier 4 |  |  |  | 7628, 7614, 7616 | Y | N |  |  | 4460 | 3368
16TPIT0067 | Teaselville Tap 138 kV capacitors | Install shunt capacitor |  | Teaselville |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6042 | 2021-05-15 |  | 138 | 0 | 0 | 0 | 0,9.2 | Cherokee |  | Tier 4 |  |  |  | 3224 | Y | N |  |  | 3319 | 3148
16TPIT0060 | Midland East - Spraberry 138 kV Line | Upgrade existing line |  | Midland East | Spraberry | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8147-E | 2021-05-15 |  | 138 | 0 | 18.8 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1023, 1132, 1133, 1329 | Y | N |  |  | 3343 | 3172
11TPIT0027 | East Richardson Switch - Ben Davis Switch (TMPA) 138 kV line | Create a new 138 kV line by reconfiguring existing lines |  | East Richardson Switch | Ben Davis Switch | Conceptual | M375A | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M375D-E | 2021-05-15 |  | 138 | 0 | 0 | 0 |  | Collin | Dallas | Tier 4 |  |  |  |  | N | N |  |  | 3358 | 3187
11TPIT0028 | Allen Switch - West Plano Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | Allen Switch | West Plano Switch | Conceptual | M375A | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M375C-E | 2021-05-15 |  | 138 | 3.5 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  |  | N | N |  |  | 3360 | 3189
16TPIT0053 | Corsicana West 138 kV capacitors | Install shunt capacitors |  | Corsicana West |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R771 | 2021-05-15 |  | 138 | 0 | 0 | 0 | 0,18.4 | Navarro |  | Tier 4 |  |  |  | 3456 | Y | N |  |  | 3615 | 3415
3430 | Midland County Northwest Sw. Sta. - Midessa 138 kV Line | Construct new 138 kV line |  | Midland County Northwest | Midessa | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8201-E | 2021-05-15 |  | 138 | 7.2 | 0 | 0 |  | Midland | Midland | Tier 3 |  |  |  | 1059, 1183 | Y | N |  |  | 3630 | 3430
4284 | Edgewood 138 kV capacitors | Install shunt capacitors |  | Edgewood |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6056 | 2021-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Rains |  | Tier 4 |  |  |  | 3181 | Y | N |  |  | 4661 | 4284
4290 | Crockett 138/69 kV autotransformer | Replace existing autotransformer |  | Crockett | Crockett | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6039 | 2021-05-15 |  | 138 | 0 | 0 | 50 |  | Houston | Houston | Tier 4 |  |  |  | 3354, 3289, 29108 | Y | N |  |  | 4669 | 4290
4298 | Big Brown - Jewett 345 kV Line | Upgrade existing double-circuit line |  | Big Brown | Jewett | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R1704 | 2021-05-15 |  | 345 | 0 | 65.6 | 0 |  | Freestone | Leon | Tier 4 |  |  |  | 3380, 3390, 3391 | Y | N |  |  | 4679 | 4298
12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Howard line. |  | Masterson Rd. | Cagnon-Howard | Planned | T-0910 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0538 | 2021-06-01 |  | 138 | 20 | 0 | 0 |  | Bexar | Bexar | Tier 2 |  |  |  | 5296, 5053, 5054, 5230, 5378 | Y | N |  | There are no transformers associated with this project | 2291 | 2218
11TPIT0037 | Add New Santa Clara Substation | Build a new 138-26.18 kV 40 MVA substation on the GVEC McQueeney(7606)-Cibolo(7608) 138 kV transmission line |  | Santa Clara | McQueeney/Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2021-06-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7605, 7606, 7608 | Y | N |  |  | 4461 | 3369
14TPIT0079 | Glen Rose to Meridian Rebuild | Rebuild Glen Rose to Meridian with 959 ACSS, 138 kV construction (operate at 69 kV) |  | Glen Rose | Meridian | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12044 | 2021-07-01 |  | 69 | 0 | 18.18 | 0 |  | Somervell | Bosque | Tier 4 |  |  |  | 315, 319 | Y | N |  |  | 2310 | 2237
13TPIT0133 | Devine Switch breaker addition | Adds breakers to Devine Switch to allow closing of normally open Devine Switch to Devine. Creates 3- terminal switching station |  | Devine Switch |  | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-01-01 |  | 69 | 0 | 0 | 0 |  | Medina |  | Tier 4 |  |  |  | 5828, 5857 | Y | N |  |  | 1579 | 1549
08TPIT0132 | Melon Creek to Tatton: Build 69 KV Line | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138-69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. |  | Melon Creek | Tatton | Conceptual | 100 - 0100 | AEP TCC | Glen Reed 918-599-2664 | 2028 | 2022-03-31 |  | 69 | 9 | 0 | 0 |  | Refugio | Aransas | Tier 2 |  |  |  | 80066, 8410, 8800 | Y | N |  |  | 1175 | 1172
08TPIT0131 | Melon Creek: Install 138/69kV Auto | Construct Melon Creek substation on Airco to Rincon 138kV line with 138/69kV, 93 MVA auto. Build new 69kV line from Melon Creek to Tatton. Rebuild 69kV line from Refugio to Tatton. |  | Melon Creek |  | Conceptual | 100 - 0100 | AEP TCC | Glen Reed 918-599-2664 | 2021 | 2022-03-31 |  | 138 | 0 | 0 | 50 |  | Refugio |  | Tier 4 |  |  |  | 8144, 8418, 80065, 80066, 80067 | N | N |  |  | 3148 | 2979
10TPIT0017 | Allen Switch - Plano Custer - Collin Junction 138 kV line | Upgrade existing double-circuit 138 kV line |  | Allen Switch | Collin Junction | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3047-E | 2022-05-15 |  | 138 | 0 | 9 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 651, 2509, 2510, 2524, 2525, 2526 | Y | N |  |  | 1059 | 1058
07TPIT0234 | Collin Switch - NW. Carrollton 345 kV line | Upgrade existing 345 kV line |  | Collin Switch | NW. Carrollton | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3061-E | 2022-05-15 |  | 345 | 0 | 19.3 | 0 |  | Collin | Dallas | Tier 4 | 2006-10-01 | 2007-02-01 |  |  | N | N |  | The ERCOT Staff determined this project is not economically justified in their February 2007 study. | 3363 | 3192
3797 | Shropshire 69 kV station | Add new station for AEP load on 69 kV |  | Shropshire |  | Conceptual |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2022-06-01 |  | 69 | 0 | 0 | 0 |  | Matagorda |  | Tier 4 |  |  |  | 5555, 5549, 5554 | Y | N |  |  | 4048 | 3797
06TPIT0083 | Del Rio to Buena Vista, reconductor 138 kV line | Reconductor Del Rio 138 kV System |  | DEL RIO | BUENA VISTA | Planned | 301-0449 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 1546 | 2022-06-30 |  | 138 |  | 3 |  |  | Val Verde | Val Verde | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8690 | Y | N |  |  | 3748 | 3540
06TPIT0084 | Hamilton Road to Del Rio reconductor 138 kV line | Reconductor Del Rio 138 kV System | CHANGES | HAMILTON ROAD | DEL RIO | Conceptual | 301-0449 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 1545 | 2022-06-30 |  | 138 | 0 | 3 | 0 |  | Val Verde | Val Verde | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8255 | N | N | NA | NA | 3749 | 3541
07TPIT0083 | Picacho to CFE, construct new 138 kV line | Convert Amistad to CFE Amistad 12.5 kV distribution to 138 kV line | CHANGES | PICACHO | CFE | Conceptual | 301 - 0449 | AEP TCC | GLEN REED GAREED@AEP.COM 918-599-2664 | 1548 | 2022-06-30 |  | 138 | 8.8 | 0 | 0 |  | Val Verde | Val Verde | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8684 | N | N | NA | NA | 3750 | 3542
07TPIT0252 | Greta: Install 1-7.2 MVAR 69 kV Cap Bank | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138-69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. |  | Greta |  | Conceptual | 100 - 0100 | AEP TCC | Glen Reed 918-599-2664 | 2045 | 2022-07-31 |  | 69 | 0 | 0 | 0 | 0,7.2 | Refugio |  | Tier 4 |  |  |  | 8409 | Y | N |  |  | 1174 | 1171
12TPIT0006 | Olmos(7613)- New Substation | Build a new 138-13.09 kV 20 MVA substation on the Olmos switching station site |  | Olmos | Olmos Switching Station | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2022-11-30 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7239 | Y | N |  |  | 3566 | 3371
12TPIT0025 | Refugio - Tatton: Rebuild Irreparable 69 kV Line | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138-69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. |  | Refugio | Tatton | Conceptual | 100 - 0100 | AEP TCC | Glen Reed 918-599-2664 | 2027 | 2022-12-30 |  | 69 | 0 | 12.6 | 0 |  | Refugio | Aransas | Tier 4 |  |  |  | 8410, 8800 | Y | N |  |  | 1167 | 1164
07TPIT0122 | Royse - Dalrock 138 kV line | Upgrade existing 138 kV line |  | Royse | Dalrock | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3035-E | 2023-05-15 |  | 138 | 0 | 6.8 | 0 |  | Rockwall | Rockwall | Tier 4 |  |  |  |  | N | N |  |  | 3274 | 3105
07TPIT0138 | Oates (GPL) - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  | Oats (GPL) | Garland Bobtown Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M322-E | 2023-05-15 |  | 138 | 0 | 1.5 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | N | N |  |  | 3276 | 3107
07TPIT0119 | Lavon Switch - Allen Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | Lavon Switch | Allen Switch | Conceptual | M375A | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M375B-E | 2023-05-15 |  | 138 | 8.9 | 0 | 0 |  | Collin | Collin | Tier 4 |  |  |  |  | N | N |  |  | 3364 | 3193
3915 | Hutto Switching Station - Round Rock 138 kV Line | Upgrade existing 138 kV line |  | Hutto Switching Station | Round Rock | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R795 | 2023-05-15 |  | 138 |  | 9.1 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 3666, 3668, 3670 | Y | N |  |  | 4215 | 3915
09TPIT0116 | Gatesville Tap - Gatesville TDC 69 kV line | Upgrade existing 69 kV line |  | Gatesville Tap | Gatesville TDC | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R497-WA | 2024-05-15 |  | 69 | 0 | 4.4 | 0 |  | McLennan | Coryell | Tier 4 |  |  |  | 3583, 3586, 3587 | N | N |  |  | 466 | 466
10TPIT0091 | Elm Mott - Waco Northcrest 138 kV line upgrade | Upgrade existing 138 kV line |  | Elm Mott | Waco Northcrest | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R714-E | 2024-05-15 |  | 138 | 0 | 3.6 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3407, 3575 | N | N |  |  | 1336 | 1332
09TPIT0047 | N. Waco - NE. Waco 138 kV line | Upgrade existing 138 kV line |  | N. Waco | NE. Waco | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R477-E | 2024-05-15 |  | 138 | 0 | 1.9 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3551, 3552 | N | N |  |  | 1355 | 1351
09TPIT0066 | Boggy Creek 138 kV Switching Station and associated line | Construct 138 kV switching station and add second circuit to a 138 kV line |  | Boggy Creek | Little River | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R488-E | 2024-05-15 |  | 138 | 0 | 3.5 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 3424, 3415, 3425 | Y | N |  |  | 1365 | 1361
16TPIT0045 | Eddy - Troy 69 kV Line | Upgrade existing line |  | Eddy | Troy | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R774-E | 2024-05-15 |  | 69 | 0 | 6.8 | 0 |  | Bell | McLennan | Tier 4 |  |  |  | 3580, 3581 | N | N |  |  | 3242 | 3073
09TPIT0043 | Coppell - North Lake 138 kV line | Construct 138 kV line |  | Coppell | North Lake | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M549-E | 2024-05-15 |  | 138 | 4.8 | 0 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | N | N |  |  | 3247 | 3078
15TPIT0074 | Little River 69 kV capacitors | Install shunt capacitors |  | Little River |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R772 | 2024-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Bell |  | Tier 4 |  |  |  | 3645 | N | N |  |  | 3253 | 3084
11TPIT0033 | Saginaw - American MFG Tap 138 kV line | Upgrade existing 138 kV line |  | Saginaw | American MFG Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5070-E | 2024-05-15 |  | 138 | 0 | 1.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | N | N |  |  | 3262 | 3093
15TPIT0078 | Palestine - Carroll Springs 69 kV Line | Upgrade existing line | Construction Schedule Change | Palestine | Carroll Springs | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6045-E | 2024-05-15 |  | 69 | 0 | 22.1 | 0 |  | Anderson | Anderson | Tier 3 |  |  |  | 3270, 3273, 3274 | Y | N |  |  | 3269 | 3100
06TPIT0036 | Ennis Switch - Ennis 138 kV line | Upgrade existing 138 kV line |  | Ennis Switch | Ennis | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M280-E | 2024-05-15 |  | 138 | 0 | 6.3 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  |  | N | N |  |  | 3273 | 3104
07TPIT0073 | Venus - Webb 345 kV line | Upgrade existing 345 kV line |  | Venus | Webb | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5098-E | 2024-05-15 |  | 345 | 0 | 11.3 | 0 |  | Ellis | Dallas | Tier 4 |  |  |  |  | N | N |  |  | 3278 | 3109
08TPIT0111 | Lufkin Switching Station - Texas Foundries Tap 138 kV line | Upgrade existing 138 kV line |  | Lufkin Switching Station | Texas Foundries tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R389-E | 2024-05-15 |  | 0 | 0 | 0.7 | 0 |  | Angelina | Angelina | Tier 4 |  |  |  | 3118, 3333 | N | N |  |  | 3286 | 3117
09TPIT0046 | N. Midlothian - Midlothian TXI Tap 138 kV line | Upgrade existing 138 kV line |  | N. Midlothian | Midlothian TXI Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3031-E | 2024-05-15 |  | 138 | 0 | 6.2 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  |  | N | N |  |  | 3295 | 3126
09TPIT0050 | Rowlett - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  | Rowlett | Garland Bobtown Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3032-E | 2024-05-15 |  | 138 | 0 | 4.1 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  |  | N | N |  |  | 3296 | 3127
10TPIT0053 | Kaufman South 138 kV Capacitors | Install 138 kV capacitors |  | Kaufman South |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3064-E | 2024-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Kaufman |  | Tier 4 |  |  |  |  | N | N |  |  | 3297 | 3128
10TPIT0054 | Royse 138/69 kV autotransformer | Install larger autotransformer |  | Royse |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3065-E | 2024-05-15 |  | 138 | 0 | 0 | 120 |  | Rockwall |  | Tier 4 |  |  |  |  | N | N |  |  | 3298 | 3129
13TPIT0061 | Terrell Switch - North Terrell Tap 138 kV line | Upgrade existing line |  | Terrell Switch | North Terrell Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M363-E | 2024-05-15 |  | 138 | 0 | 7.9 | 0 |  | Kaufman | Kaufman | Tier 4 |  |  |  |  | N | N |  |  | 3299 | 3130
15TPIT0073 | Frankston 69 kV capacitors | Install shunt capacitors |  | Frankston |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6044 | 2024-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Anderson | Anderson | Tier 4 |  |  |  | 3255 | N | N |  |  | 3317 | 3146
15TPIT0097 | Moss 345/138 kV autotransformer | Install autotransformer |  | Moss |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8275 | 2024-05-15 |  | 345 | 0 | 0 | 600 |  | Ector | Ector | Tier 4 |  |  |  | 18526, 1018, 1019 | N | N |  |  | 3340 | 3169
08TPIT0007 | Austin Ranch - Hebron 138 kV line | Upgrade existing 138 kV line |  | Austin Ranch | Hebron | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3002-E | 2024-05-15 |  | 138 | 0 | 0.7 | 0 |  | Denton | Denton | Tier 4 |  |  |  |  | N | N |  |  | 3366 | 3195
09TPIT0024 | Electra - KMA Tap 69 kV line | Upgrade existing 69 kV line |  | Electra | KMA Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R185-E | 2024-05-15 |  | 69 | 0 | 9.9 | 0 |  | Wichita | Wichita | Tier 4 |  |  |  |  | N | N |  |  | 3368 | 3197
11TPIT0014 | Muenster - St. Jo (BEC) 69 kV line | Upgrade existing 69 kV line |  | Muenster | St. Jo | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R186B-E | 2024-05-15 |  | 69 | 0 | 7.8 | 0 |  | Cooke | Cooke | Tier 4 |  |  |  |  | N | N |  |  | 3370 | 3199
07TPIT0014 | Plano West - Richardson Tap 138 kV line | Upgrade existing 138 kV line |  | Plano West | Richardson Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M364-E | 2024-05-15 |  | 138 | 0 | 1.9 | 0 |  | Collin | Dallas | Tier 4 |  |  |  |  | N | N |  |  | 3371 | 3200
09TPIT0067 | Bonham Switch 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  | Bonham Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R516-E | 2024-05-15 |  | 138 | 0 | 0 | 100 |  | Fannin |  | Tier 4 |  |  |  |  | N | N |  |  | 3372 | 3201
09TPIT0118 | Fisher Road - Wichita Falls 138 kV line | Upgrade existing 138 kV line. |  | Fisher Road | Wichita Falls | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R191-E | 2024-05-15 |  | 138 | 0 | 1.5 | 0 |  | Wichita | Wichita | Tier 4 |  |  |  |  | N | N |  |  | 3373 | 3202
09TPIT0051 | Salado Sw- Cedar Valley Sw(BEC) 138 kV line and Sw.Sta | Establish two new 138 kV switching stations and connect them with a new 138 kV line |  | Saldo Switch | Cedar Valley Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R469-E | 2024-05-15 |  | 138 | 7 | 0 | 0 |  | Bell | Bell | Tier 2 |  |  |  |  | N | N |  |  | 3377 | 3206
15TPIT0048 | Odessa EHV - Moss 345 kV Line | Add second circuit to an existing line |  | Odessa EHV | Moss | Conceptual | R8100-E & R8100B-E | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8135- E | 2024-07-15 |  | 345 | 15 | 0 | 0 |  | Ector | Ector | Tier 1 | 2013-02-15 | 2013-09-15 |  | 1028, 11010 | N | N |  | Estimated cost is included in total estimated cost for 15TPIT0047. | 2701 | 2585
15TPIT0047 | Permian Basin - Moss 345 kV Line | Construct new double-circuit line. |  | Moss | Permian Basin | Conceptual | R8135-E & R8100B-E | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8100C-E | 2024-07-15 |  | 345 | 90 | 0 | 0 |  | Ector | Ward | Tier 1 | 2013-02-15 | 2013-09-15 |  | 1018, 11010 | N | N |  |  | 3008 | 2835
15TPIT0049 | Permian Basin 345 kV Switching Station | Construct 345 kV switching station and install 345/138 kV autotransformer |  | Permian Basin |  | Conceptual | R8100C-E & R8100B-E | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8100B-E | 2024-07-15 |  | 345 | 0 | 0 | 600 |  | Ward |  | Tier 1 | 2013-02-15 |  | 2013-09-15 | 11010, 1010 | N | N |  | Estimated cost is included in total estimated cost for 15TPIT0047. | 3009 | 2836
07TPIT0115 | Elgin Switch - Taylor 138 kV line | Upgrade existing 138 kV line |  | Elgiin Switch | Taylor | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R026-E | 2025-05-15 |  | 138 | 0 | 11.4 | 0 |  | Bastrop | Bastrop | Tier 4 |  |  |  | 3650, 3658 | N | N |  |  | 1344 | 1340
08TPIT0110 | Temple - Little River 69 kV line | Rebuild existing 69 kV line |  | Temple | Little River | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R097-E | 2025-05-15 |  | 69 | 0 | 7.4 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 3644, 3645 | N | N |  |  | 1345 | 1341
07TPIT0210 | Hilltop - White Settlement 69 kV line | Rebuild 4/0 ACSR section of line |  | Hilltop | White Settlement | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5135-E | 2025-05-15 |  | 69 | 0 | 14.3 | 0 |  | Parker | Tarrant | Tier 4 |  |  |  | 506, 2089 | N | N |  |  | 2685 | 2569
14TPIT0101 | Penwell 138 kV Switching Station | Construct new switching station |  | Penwell |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8106-E | 2025-05-15 |  | 138 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  | 1012, 1010, 1019 | Y | N |  |  | 2996 | 2823
09TPIT0068 | W. Weatherford - Weatherford 69 kV line | Rebuild existing 69 kV line |  | W. Weatherford | Weatherford | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R515-E | 2025-05-15 |  | 69 | 0 | 7.5 | 0 |  | Parker | Parker | Tier 4 |  |  |  |  | N | N |  |  | 3249 | 3080
13TPIT0062 | Cedar Hill Switch second 345/138 kV autotransformer | Install autotransformer |  | Cedar Hill Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4071-E | 2025-05-15 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 4 |  |  |  |  | N | N |  |  | 3270 | 3101
07TPIT0069 | Sterrett - Sardis 138 kV line | Upgrade existing 138 kV line |  | Sterrett | Sardis | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M361-E | 2025-05-15 |  | 138 | 0 | 2 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  |  | N | N |  |  | 3271 | 3102
12TPIT0078 | Southeast Nacogdoches - Lufkin Switch 345 kV line | Construct new 345 kV line, add second circuit to existing structures and add 345 kV circuit breakers at existing switching stations |  | Southeast Nacogdoches | Lufkin Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R862 | 2025-05-15 |  | 345 | 8 | 13 | 0 |  | Nacogdoches | Angelina | Tier 2 | 2008-07-01 |  | 2008-09-01 | 3117, 3119 | N | N | 2007-E4 |  | 3287 | 3118
17TPIT0012 | Willow Springs 69 kV capacitors | Install shunt capacitor |  | Willow Springs |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6026-E | 2025-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Anderson | Anderson | Tier 4 |  |  |  | 3269 | Y | N |  |  | 3290 | 3121
17TPIT0022 | Nacogdoches - Nacogdoches North 138 kV Line | Upgrade existing line |  | Nacogdoches | Nacogdoches North | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6037-E | 2025-05-15 |  | 138 | 0 | 3.9 | 0 |  | Nacogdoches | Nacogdoches | Tier 4 |  |  |  | 3303, 3310 | N | N |  |  | 3323 | 3152
17TPIT0030 | Tyler West Switch | Construct new switching station |  | Tyler West |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6022-E | 2025-05-15 |  | 138 | 0 | 0 | 0 |  | Smith | Smith | Tier 4 |  |  |  |  | N | N |  |  | 3325 | 3154
16TPIT0056 | Getty Vealmoor 138 kV capacitors | Install shunt capacitors |  | Getty Vealmoor |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8159-E | 2025-05-15 |  | 138 | 0 | 0 | 0 | 0,18.4 | Howard |  | Tier 4 |  |  |  | 1395 | Y | N |  |  | 3346 | 3175
13TPIT0063 | Salado 138 kV Switch | Construct 138 kV switching station |  | Salado |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R445B-E | 2025-05-15 |  | 138 | 0 | 0 | 0 |  | Bell |  | Tier 4 |  |  |  |  | N | N |  |  | 3367 | 3196
16TPIT0063 | Saginaw Switch 138/69 kV autotransformers | Replace existing autotransformer |  | Saginaw Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5201-E | 2025-05-15 |  | 138 | 0 | 0 | 300 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1957, 1958 | N | N |  |  | 3383 | 3210
06TPIT0042 | Lake Wichita Switch - Wichita Falls Switch 69 kV line | Upgrade existing 69 kV line |  | Lake Wichita Switch | Wichitia Falls Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R933-E | 2025-05-15 |  | 138 | 0 | 6.3 | 0 |  | Archer | Wichita | Tier 4 |  |  |  | 1447, 1449 | Y | N |  |  | 3390 | 3217
16TPIT0049 | Wichita Falls - Wichita Falls North Tap 69 kV line | Upgrade existing line |  | Wichita Falls | Wichita Falls North Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R942-E | 2025-05-15 |  | 69 | 0 | 0.9 | 0 |  | Wichita | Wichita | Tier 4 |  |  |  | 1449, 1504 | Y | N |  |  | 3391 | 3218
10TPIT0034 | Leon Switch #2 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  | Leon |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R517 | 2025-05-15 |  | 138 | 0 | 0 | 100 |  |  |  | Tier 4 |  |  |  |  | N | N |  |  | 3696 | 3489
06TPIT0092 | Wichita Falls Switch - Wichita Falls North 69 kV line | Upgrade existing 69 kV line |  | Wichita Falls Switch | Wichita Falls North | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R168A-E | 2025-05-15 |  | 69 | 0 | 3.6 | 0 |  | Archer | Wichita | Tier 4 |  |  |  |  | N | N |  |  | 3755 | 3198
15TPIT0077 | Oak Creek 69 kV capacitors | Install shunt capacitors |  | Oak Creek |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8154-E | 2025-12-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Nolan |  | Tier 4 |  |  |  | 1406 | Y | N |  |  | 3374 | 3203
15TPIT0087 | Morgan Creek - Barber Lake - China Grove 138 kV Lines | Upgrade two existing lines |  | Morgan Creek Sw | China Grove Sw | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8141-E | 2025-12-15 |  | 138 | 0 | 28 | 0 |  | Mitchell | Mitchell | Tier 4 |  |  |  | 1032, 1189, 1190, 1318, 19520, 19521 | N | N |  |  | 3743 | 3164
11TPIT0048 | Austin Ranch 138 kV capacitors | Install capacitors |  | Austin Ranch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3074-E | 2026-05-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Denton |  | Tier 4 |  |  |  | 2378 | N | N |  |  | 1051 | 1050
14TPIT0029 | Lake Creek - Robinson 138 kV line | Rebuild 138 kV line |  | Lake Creek | Robinson | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R476 | 2026-05-15 |  | 138 | 0 | 8.3 | 0 |  | McLennan | McLennan | Tier 4 |  |  |  | 3410, 3567 | N | N | 2007-R8 |  | 1353 | 1349
16TPIT0064 | Simpson Stuart - Lancaster Witt 138 kV Line | Upgrade existing line |  | Simpson Stuart | Lancaster Witt | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4112-E | 2026-05-15 |  | 138 | 0 | 3 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2988, 3068 | Y | N |  |  | 3241 | 3072
00TPIT0004 | DeCordova - Benbrook 345 kV line upgrade | Upgrade existing 345 kV line |  | DeCordova | Benbrook | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5034-E | 2026-05-15 |  | 345 | 0 | 27 | 0 |  | Hood | Tarrant | Tier 4 |  |  |  |  | N | N |  |  | 3243 | 3074
07TPIT0001 | Liggett - Trinity Switch 345 kV line | Construct Liggett - Trinity 345 kV line | Studies indicate timing of project should be changed | Liggett | Trinity Switch | Conceptual | M5014-E | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5015-E | 2026-05-15 |  | 345 | 12.8 | 0 | 0 |  | Dallas | Tarrant | Tier 2 |  |  |  |  | N | N |  |  | 3244 | 3075
07TPIT0002 | Trinity Switch 345/138 kV autotransformer | Create Trinity Switch and install a 600 MVA 345/138 kV autotransformer |  | Trinity Switch |  | Conceptual | M5015-E | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5014-E | 2026-05-15 |  | 345 | 0 | 0 | 600 |  | Tarrant |  | Tier 4 |  |  |  |  | N | N |  |  | 3245 | 3076
07TPIT0012 | Trinity Switch - Richland 138 kV line | Upgrade existing 138 kV line |  | Trinity Switch | Richland | Conceptual | M5014-E | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5069-E | 2026-05-15 |  | 138 | 0 | 0.5 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | N | N |  |  | 3246 | 3077
10TPIT0009 | Trinity Switch - Hurst 138 kV Line | Upgrade existing 138 kV line. |  | Trinity Switch | Hurst | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5040-E | 2026-05-15 |  | 138 | 0 | 4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  |  | N | N |  |  | 3250 | 3081
16TPIT0068 | Venus - Chaparral Steel Tap 138 kV Line | Upgrade existing line |  | Venus | Chaparral Steel Tap | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4113-E | 2026-05-15 |  | 138 | 0 | 5.5 | 0 |  | Ellis | Ellis | Tier 4 |  |  |  | 1908, 2300 | Y | N |  |  | 3251 | 3082
08TPIT0071 | North Lake 345/138 kV autotransformer | Install a 345/138 kV autotransformer |  | North Lake |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M3020-E | 2026-05-15 |  | 345 | 0 | 0 | 600 |  | Dallas |  | Tier 4 |  |  |  |  | N | N |  |  | 3267 | 3098
16TPIT0047 | Reynolds Street 69 kV capacitors | Install shunt capacitors |  | Reynolds Street |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6045-E | 2026-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Cherokee | Cherokee | Tier 4 |  |  |  | 3245 | N | N |  |  | 3318 | 3147
17TPIT0018 | Wink 138/69 kV autotransformer | Replace existing autotransformer |  | Wink |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8181-E | 2026-05-15 |  | 138 | 0 | 0 | 100 |  | Winkler |  | Tier 4 |  |  |  | 1075, 1074 | Y | N |  |  | 3352 | 3181
12TPIT0019 | Pleasant Valley second 138/69 kV autotransformer | Install second 138/69 kV autotransformer |  | Pleasant Valley |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R555-E | 2026-05-15 |  | 138 | 0 | 0 | 100 |  | Wichita |  | Tier 4 |  |  |  |  | N | N |  |  | 3361 | 3190
07TPIT0118 | Lavon 345/138 kV Switching Station | Construct 345/138 kV switching station |  | Lavon Switch |  | Conceptual | M375B, M375C | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M375A-E | 2026-05-15 |  | 345 | 0 | 0 | 600 |  | Collin |  | Tier 4 |  |  |  |  | N | N |  |  | 3362 | 3191
17TPIT0015 | Ennis Creek Switch 138/69 kV autotransformer | Replace existing autotransformer | Studies indicate timing of project should be changed | Ennis Creek Switch |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8179-E | 2026-05-15 |  | 138 | 0 | 0 | 50 |  | Scurry |  | Tier 4 |  |  |  | 1411, 1410 | Y | N |  |  | 3376 | 3205

## CompletedTPIT020115NoCost
FEBRUARY BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 2/1/2015
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
12TPIT0099 | Knippa to Sabinal 69 kV line, transfer to new 138-69 double | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | IN-SERVICE | Knippa | Sabinal | In-Service | 291 - 0046 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 1521 | 2014-01-10 |  | 69 | 0 | 8.5 | 0 |  | Uvalde | Medina |  |  |  |  | 8628, 8630 | Y | N |  |  | 206 | 209
12TPIT0100 | Uvalde to Knippa 69 kV line, tranfer to new 138-69 double ci | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | IN-SERVICE | Uvalde | Knippa | In-Service | 291 - 0046 | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 | 1520 | 2014-01-10 |  | 69 | 0 | 4.5 | 0 |  | Uvalde | Medina |  |  |  |  | 8231, 8628 | Y | N |  |  | 291 | 294
08TPIT0109A | Payne - Collin Switching Station 138 kV line |  |  | Payne | EPCO | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R519-E | 2014-01-15 |  | 138 |  | 14.8 | 0 |  | Grayson | Collin | Tier 3 |  |  |  | 1758, 12468 | Y | N | 2009-R12 |  | 3380 | 2174
13TPIT0152 | Wink Switch - Loving 138 kV line | Rebuild existing 138 kV line | Construction schedule change | Wink Switch | Mason | In-Service |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8066-E | 2014-01-15 |  | 138 | 0 | 40 | 0 |  | Winkler | Reeves | Tier 3 | 2012-05-15 | 2012-06-15 |  | 1074, 1092 | Y | N |  | Wink - Loving complete in 11/2013, Loving - El Mar complete in 12/2013 and El Mar - Mason complete in 5/2014 | 3160 | 2991
14TPIT0088 | Moss - Holt Switch 138 kV line | Reconductor existing 138 kV line |  | Moss | Holt Switch | In-Service |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8065B-WAC | 2014-01-15 |  | 138 | 0 | 18 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1019, 1141, 1143 | Y | N |  |  | 2807 | 2683
14TPIT0112A | SEADOC 138 kV Customer Substation | Construct service to new 138kV SEADOC customer-owned double-tap substation. Tap existing Ckt.02 Booster to Seaway Switchrack. |  | SEADOC | Booster/Seaway Switchrack | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-01-30 |  | 138 | 0.1 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43220, 43226, 42210, 43360 | Y | N |  | Cost included in project 14TPIT0112B. | 2871 | 2744
13TPIT0142 | Broadview 72 MVAR Capacitor Bank | Install 72 MVAR capacitor bank on the East bus and remove both back-to-back capacitor banks from the West bus |  |  |  | Planned |  | CPS | Hector Torres HVTorres@cpsenergy.com 210-353-2404 | S-0395 | 2014-01-31 |  | 138 | 0 | 0 | 0 | 0,72 | Bexar | Bexar | Tier 4 |  |  |  | 5040 | Y | N |  | There are no transformers associated with this project | 1930 | 1881
15TPIT0034H | Freeport Area Upgrades and Conversion to 138kV | Upgrade Ckt.10 Velasco to Surfside |  | Velasco | Surfside | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 637 | 2014-01-31 |  | 69 | 0 | 2.5 | 0 |  | Brazoria | Brazoria | Tier 3 | 2012-06-14 | 2012-07-24 |  | 43310, 43370 | Y | N |  | Substation Cost included in project 15TPIT0034B. | 3530 | 2389
13TPIT0011 | Palo Alto - New 138kV Substation | Loop new 138kV substation into the existing 138kV Leon Creek to Chavaneaux line |  | Palo Alto | Leon Creek-Chavaneaus | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0527 | 2014-01-31 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 | 2011-02-08 | 2011-09-22 |  | 5330, 5085, 5260 | Y | N |  | There are no transformers associated with this project | 953 | 952
14TPIT0112B | SEADOC 138 kV Customer Substation | Construct service to new 138kV SEADOC customer-owned double-tap substation. Tap existing Ckt.02 Velasco to Brazosport. |  | SEADOC | Velasco/Brazosport | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-01-31 |  | 138 | 5.3 | 0 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43222, 5915, 42150, 42195, 42210, 43140, 43220, 43360, 42500, 43221, 43370 | Y | N |  |  | 2872 | 2744
3582 | Skyline 80 MVAR Capacitor Bank | Install 80 MVAR capacitor bank on the North bus |  |  |  | Planned | S-0707 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2014-02-05 |  | 138 | 0 | 0 | 0 | 0,80 | Bexar | Bexar | Tier 4 |  |  |  | 5368, 5435 | Y | N |  | There are no transformers associated with this project | 3796 | 3582
12TPIT0142 | Choate to Fashing Rebuild |  |  | Choate | Coy City | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-02-07 | 2014-03-01 | 69 | 0 | 30 | 0 |  | Atascosa | Karnes | Tier 2 | 2011-12-16 | 2012-04-25 |  | 5716, 5720 | Y | N |  |  | 1550 | 1536
12TPIT0181 | Lon Hill to Calallen: Rebuild 69kV line | Rebuild Lon Hill - Calallan 69kV Line | Date Change | Lon Hill | Calallan | In-Service | 581 - 0736 | AEP TCC | Teresa Trotman 918-599-2664 | 3461 | 2014-02-19 |  | 69 | 0 | 2.1 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 5626, 8448 | Y | N |  | 0 | 1818 | 1776
2379 | Wirtz-JC-Mt. Top | Close 69-kV loop on Wirtz-Johnson City - Mt. Top | This switching to be performed after completion of the Mt. Top - Blanco- Devils Hill project | Wirtz | Mt. Top | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2014-02-28 |  | 69 | 0 | 0 | 0 |  | Burnet | Blanco | Tier 4 |  |  |  | 7107, 7516 | Y | N |  |  | 2468 | 2379
13TPIT0110 | Rio Hondo: Replace 345 kV Series Capacitors | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Replace Series Capacitors at North Edinburg and Rio Hondo |  | Rio Hondo |  | Under Construction | 071 - 0281 | AEP TCC | Michael Glueck 918-599-2664 | 3185 | 2014-02-28 |  | 345 | 0 | 0 | 0 | 0,933.1 | Cameron |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 8903, 8318, 8902 | Y | N |  |  | 2522 | 2417
15TPIT0019 | Blockhouse (7527) | Add a 31.2 MVAR Capacitor Bank at the Blockhouse (7527) substation | Project moved up due to outage schedules on Buttercup-Whitestone project, Material Lead times result delay to Feb 2014. Still on schedule to coordinate with BC-WS outages. | Blockhouse |  | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2014-02-28 |  | 138 | 0 | 0 | 0 | 0,31.2 | Williamson |  | Tier 4 |  |  |  | 7527 | Y | N |  |  | 1007 | 1006
05TPIT0072 | Mountain Top-Blanco-Devil's Hill | Close the 69-kV switch (SW 458) at the Blanco substation (7482) to loop the load located at the Blanco substation. Upgrade the capacity of the 138-69-kV auto-transformer (T2) at the Devil's Hill substation (7493) from 20-MVA to 45-MVA. | Devils Hill Auto Installed. Construction for Blanco bus to close Loop not scheduled to complete until July 2013. Material delivery delaying energization to Dec 2014. | Mountain Top | Devil's Hill | Under Construction |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 | 1005443 | 2014-02-28 |  | 138 | 0 | 0 | 45 |  | Blanco | Comal | Tier 4 |  |  |  | 7482, 7484 | Y | N |  |  | 3709 | 3502
14TPIT0126 | Geronimo Substation Upgrade | Convert the 138-kV ring bus to a double bus-double breaker configuration and extend the 138-kV bus for termination of GVEC's McQueeney (7606) - Geronimo (7604) 138-kV transmission line. |  | Geronimo |  | Planned | 10TPIT0063, 15TPIT0029 | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-03-04 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 2 |  |  |  | 7604 | Y | N |  | Coordinate with GVEC | 3495 | 3315
14TPIT0129 | Glidden to Colorado Transmission Upgrade to 138kV | Rebuild Rock Island, Sheridan, and Colorado substations to 138kV and convert to 138kV by tapping 138kV bus at Glidden substation. | ERCOT approval through RPG review process was granted March 27, 2012 | Glidden | Colorado | Planned | 13TPIT0150 | SBEC | Don Roberts droberts@sbec.org | WO#12-5327 WO#12-5328 WO#12-5329 WO#12-5330 WO#12-5331 | 2014-03-31 |  | 138 | 0 | 27 | 0 |  | Colorado | Colorado | Tier 3 |  |  |  | 7636, 7639, 7640, 77639, 77640, 5536, 7257, 7258 | Y | N |  |  | 3733 | 3526
13TPIT0177 | Colorado - Nada Transmission Line Upgrade | Upgrade the 20 mile Colorado (7636) - Nada (5536) 69-kV transmission line to 795 ACSR 69-kV, 111 MVA. |  | Colorado | Nada | Planned | 13TPIT0150 (STEC) | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-04-01 |  | 69 | 0 | 20 | 0 |  | Colorado | Colorado | Tier 2 | 2012-02-01 |  |  |  | Y | N |  |  | 2190 | 2118
2946 | New Choke Canyon substation | New substation in San Miguel to Sigmor 138 kV line |  | AEPCHKCN |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-04-01 | 2014-04-30 | 138 | 0 | 0 | 0 |  | Live Oak |  | Tier 4 |  |  |  | 5689, 5706, 8404 | Y | N |  |  | 3115 | 2946
11TPIT0174 | Nall to Briarcrest Upgrade | Upgrade 0.82 miles of conductor from 2-0 ACSR to 795 ACSR and replace transmission poles as needed. |  | Nall Lane Substation | Briarcrest Substation | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2014-04-01 |  | 69 | 0 | 0.82 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32872, 32877 | Y | N |  |  | 1827 | 1430
12TPIT0109 | Laguna to Naval Base | Upgrade the 3.09-mile Laguna (8494)-Naval Base (8495) 69 kV transmission line to 69kV 959.6 ACSS , 191 MVA with 138 kV capable structures. |  | Laguna | Naval Base | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-04-01 |  | 69 | 0 | 3.1 | 0 |  | Nueces | Nueces | Tier 4 | 2012-07-06 | 2012-12-15 | 2013-01-15 | 8494, 8495 | Y | N |  |  | 988 | 987
13TPIT0108 | Nelson Sharpe to Ajo: Reconductor 345kV Line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Replace Series Capacitors at North Edinburg and Rio Hondo | In-Service, Updated Cost | Nelson Sharpe | Ajo | In-Service | 071 - 0281 | AEP TCC | Michael Glueck 918-599-2664 | 3181 | 2014-04-03 | 2014-04-03 | 345 | 0 | 36.2 | 0 |  | Kleberg | Kenedy | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 80076, 85000 | Y | N |  |  | 1423 | 1422
14TPIT0131 | Dansby to Triangle Park Tap | 138kV loop-in of Dansby to Jack Creek. Double circuit will be approximately 0.5 miles long. |  | Dansby | Triangle Park | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2014-04-09 |  | 138 | 1 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  |  | Y |  |  |  | 3666 | 3461
3138 | Dansby to Triangle Park Temp | Temporary T-Line to serve Triangle Park Sub while project is under construction |  | Dansby | Triangle Park | Planned | 14TPIT0131 | BRYN | James Tanneberger 979-821-5763 |  | 2014-04-09 |  | 138 | 0.5 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32854, 32881, 32897 | Y |  |  |  | 3307 | 3138
13TPIT0180 | Salem Autotransformer Replacement | Replace failed autotransformer at the Salem substation | A spare autotransformer will be in service at Salem temporarily until the replacement is installed. The in-service date for the spare is June 15, 2012. | Salem |  | In-Service |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-04-11 |  | 345 | 0 | 0 | 672 |  | Washington |  | Tier 4 |  |  |  | 7058, 7289, 77289 | Y | N |  |  | 4328 | 3597
14TPIT0051 | North Edinburg: Replace 345 kV Series Capacitors | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Replace Series Capacitors at North Edinburg and Rio Hondo | In-Service, Updated Cost | North Edinburg |  | Under Construction | 071 - 0281 | AEP TCC | Michael Glueck 918-599-2664 | 3184 | 2014-04-11 | 2014-04-11 | 345 | 0 | 0 | 0 | 0,933.1 | Hidalgo |  | Tier 1 | 2011-03-10 | 2011-08-25 | 2011-09-01 | 8383, 8901, 8905 | Y | N |  |  | 1890 | 1846
15TPIT0041 | Knob Creek 345 kV Switching Station Phase II | Expand 345 kV switching station | Construction Schedule Change | Knob Creek |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R749B-E | 2014-04-15 |  | 345 | 0 | 0 | 0 |  | Bell |  | Tier 4 |  |  |  | 3413, 3414, 3699 | Y | N |  |  | 3272 | 3103
3684 | Jerry: Build new 138 kV station | Construct new Jerry station along the Big Lake to Twin Buttes 138 kV line | Company Contact Update and IN-SERVICE | Jerry |  | In-Service | 656 - 0825 | AEP TNC | Eric Scott 918-599-2664 | 1820 | 2014-04-17 |  | 138 | 0 | 0 | 0 |  | Reagan |  | Tier 4 |  |  |  | 6559, 6648, 6535, 76011 | Y | N |  |  | 3925 | 3684
14TPIT0058A | Mont Belvieu Area Upgrades | Build new 345kV JORDAN substation. Install new 800 MVA autotransformer. |  | JORDAN |  | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-04-25 |  | 345 | 0 | 0 | 800 |  | Chambers |  | Tier 3 | 2012-02-03 | 2012-03-05 |  | 40850, 41114, 49077, 41111, 41700, 40855 | Y | N |  |  | 2913 | 2758
14TPIT0058B | Mont Belvieu Area Upgrades | Loop existing Ckt.99 Cedar Bayou - Northbelt into new JORDAN substation to create new Ckt.99 JORDAN - Cedar Bayou. |  | JORDAN | Cedar Bayou | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-04-26 |  | 345 | 0.2 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2012-02-03 | 2012-03-05 |  | 40000, 40240, 40850, 46100 | Y | N |  | Cost included in project 14TPIT0058A. | 2914 | 2758
14TPIT0058C | Mont Belvieu Area Upgrades | Loop existing Ckt.99 Cedar Bayou - Northbelt into new JORDAN substation to create new Ckt.99 JORDAN - Northbelt. |  | JORDAN | Northbelt | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-04-27 |  | 345 | 0.2 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2012-02-03 | 2012-03-05 |  | 40000, 40255, 40850, 40900, 45822, 46331, 45821, 45972, 46031, 46100 | Y | N |  | Cost included in project 14TPIT0058A. | 2915 | 2758
13TPIT0119A | Vanderbilt to Ricebird 138 kV circuit |  |  | Ricebird | ETP | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-04-28 | 2014-05-01 | 138 | 22 | 0 | 0 |  | Jackson | Jackson | Tier 2 | 2011-10-07 | 2012-01-26 |  | 5523, 78104 | Y | N |  | project costs were included with 13tpit0119a | 2674 | 2558
14TPIT0058D | Mont Belvieu Area Upgrades | Build new circuit out of JORDAN 138kV substation and reconnect portion of existing DUNCAN - BARHIL circuit to create new Ckt.59 JORDAN - BARHIL. |  | JORDAN | BARHIL | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-04-28 |  | 138 | 0.87 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2012-02-03 | 2012-03-05 |  | 40150, 40360, 40855 | Y | N |  | Cost included in project 14TPIT0058A. | 2916 | 2758
10TPIT0063 | Geronimo(7604)-CMC Tap-McQueeney T-Line | Rebuild 5.5 miles of existing 69-kV T-line to 138-kV, 1192 ACSR between Geronimo and McQueeney substations on existing eight-of-way. |  | Geronimo | McQueeney | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2014-04-28 |  | 138 | 0 | 5.5 | 0 |  | Guadalupe | Guadalupe | Tier 4 | 2012-12-01 |  |  | 7604, 7606 | Y | N |  |  | 3211 | 3042
14TPIT0058E | Mont Belvieu Area Upgrades | Build new circuit out of JORDAN 138kV substation and reconnect portion of existing ENPROD - HACHER circuit to create new Ckt.59 JORDAN - RALYND. |  | JORDAN | RALYND | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-04-29 |  | 138 | 0.87 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2012-02-03 | 2012-03-05 |  | 40510, 40762, 40855 | Y | N |  | Cost included in project 14TPIT0058A. | 2917 | 2758
14TPIT0058J | Mont Belvieu Area Upgrades | Reconfigure existing Ckt.86 DUNCAN - BARHIL and Ckt.86 ENPROD - HACHER to create new Ckt.48 DUNCAN - ENPROD. |  | DUNCAN | ENPROD | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-04-30 |  | 138 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 3 | 2012-02-03 | 2012-03-05 |  | 40511, 40360, 40510 | Y | N |  | Cost included in project 14TPIT0058A. | 2922 | 2758
13TPIT0227 | Langston 138kV Substation | Construct service to new 138kV Langston customer-owned substation. Loop through Ckt.86 Brine to Mont Belvieu. |  | Langston | Brine/Mont Belvieu | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 55 | 2014-04-30 |  | 138 | 1.2 | 0 | 0 |  | Chambers |  | Tier 4 |  |  |  | 40775, 40000, 40220, 40255, 40300, 40764, 41700, 40012, 40500, 40900, 41113, 46100 | Y | N |  |  | 2865 | 2739
12TPIT0180 | Lon Hill to City of Robstown: Rebuild 69kV line | Rebuild Lon Hill - City of Robstown 69kV Line | Reformated project number to match other numbers | Lon Hill | City of Robstown | In-Service | 582 - 0735 | AEP TCC | Teresa Trotman 918-599-2664 | 3460 | 2014-04-30 |  | 69 | 0 | 4.6 | 0 |  | San Patricio | San Patricio | Tier 4 |  |  |  | 8448, 8884, 5630 | Y | N |  | 0 | 1819 | 1777
14TPIT3420 | Crosby to CONNER Ckt.86 Reconductor | Reconductor Ckt.86 Crosby to CONNER |  | Crosby | CONNER | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-04-30 |  | 138 | 0 | 5.9 | 0 |  | Harris | Chambers | Tier 4 |  |  |  | 40390, 40665 | Y | N |  | Reconductor with test conductor. | 3620 | 3420
12TPIT0184 | Lon Hill: Replace 138-69kV Autotransformers #1 and #2 | Upgrade Both 138-69kV Autotransformers at Lon Hill to 220MVA | Operational | Lon Hill |  | Planned | 580 - 0734 | AEP TCC | Teresa Trotman 918-599-2664 | 3463 | 2014-04-30 |  | 138 | 0 | 0 | 240 |  | San Patricio |  | Tier 4 |  |  |  | 8448, 8452 | Y | N |  | 0 | 1820 | 1778
11TPIT0114 | Alberta Switch-Doedyns 138kV Line | Rebuild 3.1 Miles of 138kV line from Alberta Switch to Doedyns Substation | Pending completion of Doedyns-Sioux 11TPIT0085 | Alberta Switch | Doedyns | In-Service | 07TPIT7777 | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-05-01 | 2014-05-30 | 138 | 0 | 3.1 | 0 |  | Hidalgo | Hidalgo | Tier 4 |  |  |  | 5753, 5759 | Y | N |  |  | 355 | 358
13TPIT0186 | Trinidad second 345/138 kV autotransformer |  | Construction Schedule Change | TRINIDAD SES | TRINIDAD SES | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6015-WAC | 2014-05-01 |  | 345 | 0 | 0 | 600 |  | Henderson | Henderson | Tier 4 |  |  |  | 3124, 3127 | Y | N |  |  | 3985 | 3739
13TPIT0174 | Piloncillo 138 kV Station: Install breaker ring bus | Construct 4 CB ring bus at new Piloncillo station on Asherton to North Laredo 138 kV line |  | Piloncillo |  | Under Construction | 600 - 0762 | AEP TCC | RICK McCRACKEN GAREED@AEP.COM 918-599-2664 | 3469 | 2014-05-02 |  | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 4 |  |  |  | 80481, 89631 | Y | N |  |  | 3567 | 3372
13TPIT0226 | New Switching station btw Gray & Alibates | Build new breaker and a half configuration substation for the interconnection of generation. | Upated project information and cost |  |  | Under Construction |  | CTT | Tim Cook 636-534-3250 |  | 2014-05-10 |  | 345 | 0 | 0 | 0 |  | Carson |  | Tier 4 |  |  |  | 79005, 79000, 79500 | Y |  |  |  | 3086 | 2911
14TPIT0134 | Ennis Creek 138 kV capacitors | Install shunt capacitors |  | Ennis Creek |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8188-WAC | 2014-05-15 |  | 138 | 0 | 0 | 0 | 0,73.6 | Scurry |  | Tier 4 |  |  |  | 1410 | Y | N |  |  | 3001 | 2828
14TPIT0132 | Spraberry 69kV capacitors | Install shunt capacitors |  | Spraberry |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8164-WAC | 2014-05-15 |  | 69 | 0 | 0 | 0 | 0,55.2 | Midland |  | Tier 4 |  |  |  | 1330 | Y | N |  |  | 3003 | 2830
14TPIT0133 | Texaco Harvey 69 kV capacitors | Install shunt capacitors |  | Texaco Harvey |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8163-WAC | 2014-05-15 |  | 69 | 0 | 0 | 0 | 0,36.8 | Midland |  | Tier 4 |  |  |  | 1221 | Y | N |  |  | 3004 | 2831
13TPIT0136 | Odessa North 138 kV Switching Station | Construction 138 kV switching station |  | Odessa North |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8050B-WAC | 2014-05-15 |  | 138 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  |  | Y | N |  |  | 3265 | 3096
14TPIT3344 | Katy Tap to Franz Ckt.09 | Upgrade 138kV Ckt.09 Katy tap to Franz to increase thermal ratings. |  | Katy | Franz | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 860 | 2014-05-15 |  | 138 | 0 | 4.1 | 0 |  | Waller | Harris | Tier 4 |  |  |  | 44230, 44261, 44422, 45770, 44262, 44421 | Y | N |  |  | 3532 | 3344
14TPIT0091 | Riley (Oklaunion) - Fisher Road 345 kV line relocation | Relocate 345 kV line |  | Oklaunion | Fisher Road | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R921-WAC | 2014-05-15 |  | 345 | 6.9 | 0 | 0 |  | Wilbarger | Wichita | Tier 4 |  |  |  | 1425, 6101 | Y | N |  |  | 3354 | 3183
3432 | Willow Valley Switch shunt reactor | Install shunt reactors on tertiary of 345/138 kV autotransformer |  | Willow Valley |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8193-WAC | 2014-05-15 |  | 345 | 0 | 0 | 0 | -75,0 | Borden |  | Tier 4 |  |  |  | 18537 | Y | N |  |  | 3632 | 3432
13TPIT0153 | Moss - Odessa Southwest - Odessa EHV 138 kV line | Reconductor existing 138 kV line |  | Moss | Odessa EHV | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8064-WAC | 2014-05-15 |  | 138 | 0 | 14.2 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1019, 1027, 1111, 1113 | Y | N |  |  | 2995 | 2822
14TPIT0083 | Electra 69 kV capacitors | Install capacitors |  | Electra |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R561-WAC | 2014-05-15 |  | 69 | 0 | 0 | 0 | 0,9.2 | Wichita |  | Tier 4 |  |  |  | 1538 | Y | N |  |  | 1965 | 1914
07TPIT0126 | Tri Corner - Seagoville Switch 345 kV line | Upgrade existing 345 kV line |  | Tri Corner | Seagoville Switch | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4044-WAC | 2014-05-15 |  | 345 | 0 | 9.4 | 0 |  | Dallas | Dallas | Tier 4 |  |  |  | 2432, 2433 | Y | N |  |  | 1823 | 1781
09TPIT0042 | Collin 345-138 kV autotransformer | Install second 345/138 kV autotransformer |  | Collin Switch |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M318-E | 2014-05-15 |  | 345 | 0 | 0 | 600 |  | Collin |  | Tier 4 |  |  |  | 902546, 2370, 29554, 2372, 29578 | Y | N | 2009-R15 |  | 1247 | 1244
13TPIT0199 | Caddo Mills HWY 66 Substation 69 kV Capacitors | Install shunt capacitors |  | Caddo Mills HWY 66 |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R513-E | 2014-05-15 |  | 69 | 0 | 0 | 0 | 0,18.4 | Hunt |  | Tier 4 |  |  |  | 1831, 1827, 1829 | Y | N |  |  | 3684 | 1972
3702 | Oklaunion: HVDC tie | Build a new HVDC tie to replace the old one between SPP and ERCOT at Oklaunion | Company Contact Update and IN-SERVICE | Oklaunion |  | In-Service | 425 - 0614 | AEP TNC | Tommy Vannoy 918-599-2664 | 3198 | 2014-05-15 |  | 345 | 0 | 0 | 0 | 0,135 | Wilbarger |  | Tier 4 |  |  |  | 6102 | Y | N |  |  | 3944 | 3702
14TPIT0103 | Moss Switching Station | Install 345 kV breakers |  | Moss |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8140-E | 2014-05-15 |  | 345 | 0 | 0 | 0 |  | Ector |  | Tier 4 |  |  |  |  | Y | N |  |  | 3291 | 3122
14TPIT0093 | Paris Switch shunt reactor | Install shunt reactor |  | Paris Switch |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R920-WAC | 2014-05-15 |  | 345 | 0 | 0 | 0 | -100,0 | Lamar |  | Tier 4 |  |  |  | 1692 | Y | N |  |  | 2348 | 2275
13TPIT0137 | Odessa North - Goldsmith Junction 138 kV line | Rebuild existing 69 kV line to create a double-circuit line with 69 kV and 138 kV circuits |  | Odessa North Switch | Goldsmith Junction | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8050C-WAC | 2014-05-15 |  | 138 | 13.3 | 0 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 11253, 1019, 1122, 1254, 1255, 11140, 1123, 1261, 11254 | Y | N |  |  | 2694 | 2578
08TPIT0109B | Payne - Collin Switching Station 138 kV line |  |  | EPCO | Collin Switching Station | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R519-E | 2014-05-15 |  | 138 | 0 | 17 | 0 |  | Grayson | Collin | Tier 3 |  |  |  | 1757, 2350, 2366, 12349, 12468, 2349, 2370 | Y | N | 2009-R12 |  | 3379 | 2174
07TPIT0017 | Handley - Hurst 138 kV line | Reconductor existing 138 kV line |  | Handley | Hurst | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M572-WAC | 2014-05-15 |  | 138 | 0 | 18.7 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1950, 1951, 2109, 2110, 2113, 2114, 2115, 2116 | Y | N |  | Interim rating increase was implemented in May 2012. | 3108 | 2939
14TPIT0009 | Odessa North - North Cowden 69 kV line | Upgrade existing line |  | Odessa North | North Cowden | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8008-E | 2014-05-15 |  | 69 | 0 | 12.4 | 0 |  | Ector | Ector | Tier 4 |  |  |  |  | N | N | 2009-R4 |  | 3357 | 3186
14TPIT0021 | Buttercup-Whitestone Upgrade | Upgrade the 2.3-mile Buttercup (7531)-Whitestone (7529) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). The Wavetrap will be replaced at Whitestone uprating Blockhouse to Whitestone line to (221MVA, 221MVA, 221MVA). |  | Buttercup Substation | Whitestone Substation | Planned |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2014-05-22 |  | 138 | 0 | 2.3 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 7527, 7529, 7531 | Y | N |  |  | 1002 | 1001
14TPIT0124 | Menger Creek Transmission Line Addition | Add 2.9 miles of 138-kV bundled 795 ACSR, 440 MVA, to an existing single circuit to establish a double circuit between Menger Creek Tap (7663) - Menger Creek substation (7665) |  | Menger Creek | Menger Creek Tap | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-05-23 |  | 138 | 2.9 | 0 | 0 |  | Kendall |  | Tier 4 |  |  |  | 5200, 7151, 7665 | Y | N |  |  | 3518 | 3335
14TPIT0048 | Clear Fork Substation (aka Maxwell) | Construct 69kV-12.5kV distribution substation Clear Fork (7195) on T-519 between Reedville and Lockhart. |  | Clear Fork | Reedville-Lockhart | Planned |  | BBEC | Thomas Ellis thomas.ellis@bluebonnet.coop |  | 2014-05-29 |  | 69 | 0 | 0 | 0 |  | Caldwell |  | Tier 4 |  |  |  |  | Y | N |  |  | 1000 | 999
14TPIT0043 | Tri-County - New 138kV Substation | Loop new 138kV substation into the existing Skyline to Wiederstein and Green Mountain to Parkway transmission lines. |  | Skyline-Green Mountain | Tri_County-Wiederstein Tri_County-Parkway | Planned | T-0191 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0620 | 2014-05-29 |  | 138 | 0.1 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5180, 5360, 5370, 5445, 7461, 7611 | Y | N |  | There are no transformers associated with this project | 959 | 958
3040 | WA Parish to Fort Bend Ckt.09 | Upgrade 138kV Ckt.09 Fort Bend to Reading to increase thermal ratings. |  | Fort Bend | Reading | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2014-05-29 |  | 138 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44280, 44570 | Y | N |  |  | 3894 | 3040
3040B | WA Parish to Fort Bend Ckt.09 | Upgrade 138kV Ckt.09 Reading to Crabb River Road to increase thermal ratings. |  | Reading | Crabb River Road | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2014-05-30 |  | 138 | 0 | 3.8 | 0 |  | Fort Bend | Fort Bend | Tier 4 |  |  |  | 44170, 44570 | Y | N |  | Cost included in project 14TPIT3040A. | 3895 | 3040
13TPIT0203 | Correction to in service date, bus & load | Old 13TPIT0203 (project ID:3132) with 1/1/14 in service date deleted. New 13TPIT0203 (project ID:3741) will replace and include bus, load and in service date corrections. Blossom PMCR (project ID:3742) to be used to remove Blossom from planning model until new in service date. | Still Constructing Station |  |  | Planned | 3132, 3742 | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE02916 | 2014-05-30 |  | 0 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 37400, 1687 | Y |  |  |  | 3987 | 3741
14TPIT0125 | Plum - Flatonia Transmission Line Upgrade | Upgrade the 19.62 mile Plum (7274) - Flatonia (7248) 138-kV transmission line to 795 ACSR, 220 MVA |  | Plum | Flatonia | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-05-30 |  | 138 | 0 | 19.6 | 0 |  | Fayette | Fayette | Tier 4 |  |  |  | 7248, 7274 | Y | N |  |  | 3127 | 2958
3677 | Replace Meadow Failed 500MVA Auto with 400MVA GBY A2 Auto | Replace failed 500MVA autotransformer A1 at Meadow with spare 400MVA transformer. | Delay in Project Schedule | Meadow |  | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-05-30 |  | 345 | 0 | 0 | -100 |  | Brazoria |  | Tier 4 |  |  |  | 43030, 43031, 49046 | Y | N |  |  | 3914 | 3677
3679A | Remove Brisco and Juliff from transmission service | Remove Brisco substation from CNP transmission service. | Delay in project schedule | Brisco |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 943/944 | 2014-05-30 |  | 69 | 0 | 0 | 0 |  | Fort Bend |  | Tier 4 |  |  |  | 44110, 44380, 47165 | Y | N |  |  | 3916 | 3679
15TPIT0021 | Replace structures | [6 empty] | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2014-05-31 |  | 0 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 38890, 42015 | Y |  |  |  | 4183 | 3587
14TPIT0111 | Conner 138kV Substation | Construct service to new 138kV CONNER customer-owned substation. Loop through Ckt.86 Crosby to Bender 4v33_Base Case JOR345, CNR, & LAN-Complete.idv |  | CONNER | Crosby/Bender | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 55 | 2014-05-31 |  | 138 | 1.8 | 0 | 0 |  | Chambers |  | Tier 4 |  |  |  | 40665, 40000, 40155, 40220, 40255, 40300, 40340, 40390, 40775, 40850, 40900, 41700, 45822, 46331, 40012, 40425, 40500, 40764, 41113, 41150, 45821, 46031, 46100 | Y | N |  |  | 2870 | 2743
3527 | Randado: Add 138 kV breaker terminal for SF interconnect | Construct a 138 kV breaker terminal at Randado for generation Interconnect | COMPLETED | RANDADO |  | In-Service |  | AEP TCC | BRENT HARIS GAREED@AEP.COM 918-599-2664 | TP2010005 | 2014-05-31 | 2014-03-18 | 138 | 0 | 0 | 0 |  | Jim Hogg |  | Tier 4 |  |  |  | 8699 | Y |  | NA | NA | 3734 | 3527
3962 | Fry Road Mobile 138kV Substation | Build temporary 138kV Fry Road mobile distribution substation. Tap from circuit 09 Zenith to Gertie. |  | Fry Road | Zenith/Gertie | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-05-31 |  | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 45813, 44910, 45801 | Y | N |  |  | 4283 | 3962
3679B | Remove Brisco and Juliff from transmission service | Remove Juliff substation from CNP transmission service. | Delay in project schedule | Juliff |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 943/944 | 2014-05-31 |  | 69 | 0 | 0 | 0 |  | Fort Bend |  | Tier 4 |  |  |  | 44380, 42041, 43260, 44362, 44400, 47150, 44361, 44552, 47165 | Y | N |  | Cost included in project 14TPIT3679A. | 3917 | 3679
3883 | GSEC_3883_Add_Rock-Hollow_Sub |  | NA |  |  | Under Construction | NA | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2014-06-01 |  | 138 | 0 | 0 | 0 |  | Reagan | Reagan | Tier 4 |  |  |  | 60352, 6559 | Y | N |  | Anticipated energization date of 6/1/2014 | 4173 | 3883
14TPIT0042A | Five Points to Broadview - 138 kV Transmission Line Rebuild | Rebuild 138 kV transmission line from Five Points to Broadview (Not all conductor replaced) |  | FIVE POINTS | BROADVIEW | In-Service |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0208 | 2014-06-01 |  | 138 | 0 | 9.4 | 0 |  | Bexar | Bexar | Tier 3 |  |  |  | 5040, 5345, 5419, 5150, 5490 | Y | N |  |  | 4025 | 956
14TPIT0070 | New 138kV line from LaPalma to Palo Alto | Construct new La Palma ¿ Palo Alto 138 kV line (~12 mi) and station upgrades | New Changed Dollars to include the station costs associated with the project (Approved by RPG, see comments for breakout) | LaPalma | Palo Alto | Planned |  | SLU |  |  | 2014-06-01 |  | 138 | 12 | 0 | 0 |  | Cameron | Cameron | Tier 1 | 2011-05-03 | 2011-12-19 | 2012-01-17 | 8314, 5965 | Y | N |  |  | 2456 | 2367
14TPIT0045 | Anderson to Cagnon - 138 kV Substation Equipment Upgrade | Upgrade terminals at Anderson and Cagnon to ensure at 2420 A rating and remove the existing MLSE on Anderson to Cagnon 138kV transmission line |  | Anderson | Cagnon | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0479 | 2014-06-01 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5003, 5054 | Y | N |  | There are no transformers associated with this project | 955 | 954
14TPIT0128 | Whitestone-Blockhouse | Replace under-rated limiting line terminal equipment at Whitestone to increase Whitestone (7529)-Blockhouse (7527) to the conductor's rating. |  | Whitestone | Blockhouse | Under Construction |  | PEC | Tony Perez jesus.perez@peci.com 830-868-5158 |  | 2014-06-02 |  | 138 | 0 | 0 | 0 |  | Williamson |  | Tier 4 |  |  |  | 7527, 7529 | Y | N |  |  | 3213 | 3044
14TPIT0059A | Bevo Station and Autotransformer | 69 kV bus and capacitor by June 2014. |  | BEVO |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-06-02 | 2014-06-01 | 69 | 0 | 0 |  | 0,9.6 | Dimmit |  | Tier 1 | 2012-04-01 | 2012-08-01 | 2012-09-01 | 5871, 5870, 5872 | Y | N |  | project cost in second phase | 3439 | 3264
14TPIT0047 | Denton 138 kV Loop Phase2 Project | Denton 138kV System Upgrades Phase2. Reliability projects necessary for the Denton area. Reconductoring 138kV loop line segments from North Denton to Jim Christal to West Denton to Fort Worth to Teasley, etc. |  | North Denton | Teasley | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2014-06-04 |  | 138 | 0 | 17.95 | 0 |  | Denton | Denton | Tier 4 |  |  |  | 916, 918, 919, 985, 986 | Y | N |  |  | 3790 | 3576
12TPIT0156 | Brundage Capacitor | Add 9.6 MVAR capacitor |  | Brundage |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-06-06 | 2014-02-15 | 69 | 0 | 0 | 0 | 0,9.6 | Dimmit |  | Tier 4 |  |  |  | 5870 | Y | N |  |  | 1405 | 1404
11TPIT0038 | COCS Northgate Substation |  |  |  |  | In-Service |  | COCS | Tony Mickalsky tmichalsky@cstx.gov 979-764-3438 |  | 2014-06-06 |  | 138 | 0 | 0 | 0 |  |  |  | Tier 4 |  |  |  | 32006, 32798, 32862 | Y |  |  |  | 4237 | 3935
13TPIT0114 | Silver to Silver Tap 1: Reterminate the 69 kV line into the | Reterminate Silver Tap 1 to Silver into Cedar Hill with 795 ACSR and add 7.2 Mvar capacitor bank at Silver | IN SERVICE,Project Title, and Project Description Update | Cedar Hill | Silver Tap 1 | In-Service | 557 - 0719 | AEP TNC | Eric Scott gareed@aep.com 918-599-2664 | 2559 | 2014-06-10 | 2014-06-10 | 69 | 0.02 | 0 | 0 | 0,7.2 | Coke | Coke | Tier 4 |  |  |  | 6000, 6431, 6423, 6430, 6428 | Y | N |  |  | 2752 | 2631
13TPIT0155 | Yucca: Add 10 MVA DRCS and add 69 kV capacitor bank | Add 3.6 Mvar capacitor bank at Barnhart SWTEC and add 10 MVA DRCS with 7.2 Mvar capacitor bank at Yucca | IN SERVICE and Project Title Update | Yucca |  | In-Service | 558 - 0721 | AEP TNC | Michael Tallon 918-599-2664 | 2563 | 2014-06-11 | 2014-06-11 | 69 | 0 | 0 | 0 | -10,17.2 | Crockett |  | Tier 4 |  |  |  | 6034, 60202, 6035, 6550 | Y | N | 0 | 0 | 1891 | 1847
14TPIT0066 | Jim Treece: Build 345 kV station | Interconnect Blue Summit Wind Farm at Jim Treece to connect Blue Summit to the Riley to Tesla 345 kV line | IN SERVICE and Project Title Update | Jim Treece |  | In-Service | 512 - 0724 | ETT | Dave Goetz 918-599-2664 | 2515 | 2014-06-13 | 2014-06-13 | 345 | 0 | 0 | 0 |  | Wilbarger |  | Tier 4 |  |  |  | 61001, 61004, 6050, 6060, 6101, 60501 | Y | N |  |  | 1882 | 1838
13TPIT0152 | Loving - Elmar 138 kV line | Rebuild existing 138 kV line | Construction schedule change | Loving | Elmar | Under Construction | R8066-E | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 |  | 2014-06-15 |  | 138 | 0 | 12.6 | 0 |  | Winkler | Reeves | Tier 3 |  |  |  | 1092, 1093 | Y | N |  |  | 3961 | 3717
14TPIT0136 | Bakke Substation conversion | Convert Bakke Substation to 138 kV operation | Construction schedule change | Bakke Tap | Bakke | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8169-WAC | 2014-06-15 |  | 138 | 0 | 3 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1154, 1279, 1280, 1277 | Y | N |  |  | 2999 | 2826
14TPIT0104 | Mason 138 kV capacitors | Install shunt capacitors | Construction schedule change | Mason |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8085-WAC | 2014-06-15 |  | 138 | 0 | 0 | 0 | 0,52.4 | Reeves |  | Tier 4 |  |  |  | 1094 | Y | N |  |  | 2989 | 2816
13TPIT0058 | Circuit 941 Summit - Williamson Reconductor | Reconductor the 3.54 miles circuit from single 795 ACSR to single 795 ACSS Drake conductor. |  | Summit Substation | Williamson Substation | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 | PLAN_117_079 | 2014-06-15 |  | 138 | 0 | 3.54 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9279, 9295 | Y | N |  |  | 1023 | 1022
14TPIT0135 | Midland Farms Substation conversion | Convert Midland Farms Substation to 138 kV operation | Construction taking longer than projected | Midland Farms Tap | Midland Farms | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8168-WAC | 2014-06-15 |  | 138 | 0.1 | 0 | 0 |  | Andrews | Andrews | Tier 4 |  |  |  | 1266, 1269, 1264, 1282 | Y | N |  |  | 3006 | 2833
14TPIT0004 | Cushman-Highway 123 | Construct a new 6.2 mile single 795 ACSR 138 kV transmission line (220 MVA) from the new Highway 123 substation (7221) located near the intersection of St Highway 123 and the GVEC Hickory Forest (7225)-New Berlin (7612) 138 kV (T529) transmission line. |  | Highway 123 | Cushman | Under Construction |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-06-18 |  | 138 | 6.2 | 0 | 0 |  | Guadalupe |  | Tier 2 | 2009-02-06 | 2009-06-01 |  | 7221, 7226, 7225, 7228, 7612 | Y | N |  | Coordinate with GVEC | 1001 | 1000
14TPIT0046 | Hill Country to La Sierra - 138 kV Substation Equipment Upgr | Upgrade termainls at Hill Country and La Sierrra to ensure a 2420 A rating and remove the existing MLSE on Hill Country to La Sierra 138kV transmission line |  | Hill Country | La Sierra | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0485 | 2014-06-20 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5209, 5257 | Y | N |  | There are no transformers associated with this project | 965 | 964
13TPIT0123 | Tordillo Station and Autotransformer | Build new Tordillo station with 138-69 kV 150 MVA autotransformer close to Fashing station with a short 69 kV line Fashing. | Project was renamed from Fashing Autotransformer and modifed due to property constraints. | Tordillo |  | In-Service | 13TPIT0130 | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-06-29 | 2014-07-30 | 138 | 0 | 0 | 150 |  | Atascosa |  | Tier 3 | 2011-12-12 | 2012-04-01 |  | 5716, 5715, 5717 | Y | N |  |  | 2675 | 2559
14TPIT0040 | Springwoods 138kV Substation | Build new 138kV Springwoods distribution substation. Loop through Ckt.66 Rayford to Westfield. |  | Springwoods | Rayford-Louetta | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 875 | 2014-06-30 | 2014-05-28 | 138 | 6.2 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 46270, 40900, 46051, 46261, 45972 | Y | N |  |  | 2204 | 2132
14TPIT0110 | MCCABE 138kV Substation | Construct service to new 138kV MCCABE customer-owned substation. Loop through Ckt. 96 Bayou to Bimont. |  | MCCABE | Bayou/Bimont | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-06-30 |  | 138 | 0.2 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 42350, 41205, 41615, 42160, 40200, 41520 | Y | N |  |  | 2869 | 2742
13TPIT0130 | San Miguel to Fashing Conversion | Convert 69 kV line to 138 kV line. The line was originally built for 138 kV operation. 138 kV circuit will terminate at Tordillo | Likely to be sped up with new load forecast | San Miguel | Fashing | In-Service | 13TPIT0123 | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-06-30 | 2014-07-30 | 138 | 0 | 23.05 | 0 |  | Atascosa | Atascosa | Tier 3 | 2011-12-12 | 2012-04-01 |  | 5715, 5717, 5702, 5706, 5716 | Y | N |  |  | 2677 | 2561
12TPIT0182 | Crystal City - Turtle Creek: Reconductor 69kV Line | Reconductor Crystal City - Turtle Creek 69kV Line | Reformated project number to match other numbers, changed ISD, and Dollars. PM Updated | Crystal City | Turtle Creek | Under Construction | 591 - 0761 | AEP TCC | Rick McCracken Gareed@aep.com 918-599-2664 | 3468 | 2014-06-30 |  | 69 | 0 | 3.3 | 0 |  | Zavala | Zavala | Tier 4 |  |  |  | 8242, 8243 | Y | N | NA | 0 | 1944 | 1895
07TPIT0077 | Big Foot to Devine: Rebuild 69 kV Line | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69-138 kV autotransformer at Lytle |  | Big Foot | Devine | Under Construction | 028 - 0028 | AEP TCC | Terry Weeks 918-599-2664 | 1777 | 2014-06-30 |  | 69 | 0 | 6.13 | 0 |  | Frio | Medina | Tier 4 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 8223, 8218 | Y | N |  |  | 1255 | 1252
14TPIT0139 | WALKER 138kV Substation | Construct service to new 138kV WALKER customer-owned substation. Loop through Ckt.85 QUANUM to Cedar Bayou. |  | WALKER | QUANUM/ Cedar Bayou | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 55 | 2014-06-30 | 2014-05-28 | 138 | 0.4 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 41440, 40010, 40070, 41330, 41500, 41611 | Y | N |  |  | 3147 | 2978
14TPIT0105 | 69E LINE INSTALL |  |  | Wink | Pecos | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 |  | 2014-07-01 |  | 69 | 0 | 32.8 | 0 |  | Reeves | Winkler | Tier 4 |  |  |  | 37920, 38090, 38150, 38180, 38230 | Y |  |  |  | 3677 | 3471
13TPIT0123B | Reconnect 69 lines from Fashing at Tordillo | Moves the Fashing lines from Pleasanton and Coy City to Tordillo |  | Tordillo |  | In-Service | 13TPIT0123 | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-07-01 | 2014-08-01 | 69 | 0.5 | 0 | 0 |  | Atascosa |  | Tier 3 | 2011-12-16 | 2012-04-25 |  | 5714, 5715, 5716, 5720 | Y | N |  |  | 3118 | 2949
14TPIT0107 | Bond Road: Add 69 kV capacitor banks | Construct new Bond Road station along the Sonora to Uvalde 69 kV line and add two 7.2 Mvar capacitor banks | IN SERVICE and Project Title Update | Bond Road |  | In-Service | 587 - 0768 | AEP TNC | Rick McCracken gareed@aep.com 918-599-2664 | 2804 | 2014-07-03 | 2014-07-03 | 69 | 0 | 0 | 0 | 0,14.4 | Sutton |  | Tier 4 |  |  |  | 6570, 6513, 8239 | Y | N |  |  | 2927 | 2761
3678 | Barrilla Junction: Add 138 kV terminal | Interconnect Barrilla Solar farm at Barrilla Junction 138 kV station | IN SERVICE and Project Title Update | Barrilla Junction |  | In-Service | 649 - 0819 | AEP TNC | Brent Harris 918-599-2664 | 1814 | 2014-07-29 | 2014-07-29 | 138 | 0 | 0 | 0 |  | Pecos |  | Tier 4 |  |  |  | 6653 | Y | N |  |  | 3915 | 3678
15TPIT0043F | Fort Bend Area Upgrades | Adding Temporary Configuration for FtBend - Richmond Irrigation |  | FtBend | Richmond | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 937 | 2014-07-30 |  | 69 | 0 | 0 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2012-09-14 | 2012-10-29 |  | 44290, 44580, 44610 | Y | N |  | Cost included in project 15TPIT0043D. | 4565 | 4208
3862 | Colorado T1 Transformer upgrade to 138 kV | Replace Colorado T-1 Transformer for 138 kV, add circuit switcher, 138 kV switch and upgrade low side bus | ERCOT approval through RPG review process was granted March 27, 2012 | Colorado |  | In-Service | 14TPIT0129 and 13TPIT0150 | SBEC | Don Roberts droberts@sbec.org | WO#12-5331 | 2014-07-30 |  | 138 | 0 | 0 | 0 |  | Colorado | Colorado | Tier 4 |  |  |  | 7636, 7639 | Y | N |  | Upgrade of the Colorado T-1 transformer will continue until July 31, 2014 | 4150 | 3862
12TPIT0079 | Grapevine Junction - Coppell 138 kV line | Rebuild 138 kV line |  | Grapevine Junction | Coppell | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5001A-WAC | 2014-08-01 |  | 138 | 0 | 4.4 | 0 |  | Dallas | Tarrant | Tier 4 |  |  |  | 2014, 2015, 2025 | Y | N | 2007-R4 | Interim rating increase for Coppell - Grapevine Junction section was implemented in May 2012. | 3104 | 2929
3884 | GSEC_3884_Add_Walker_Sub |  | NA |  |  | Under Construction | NA | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2014-08-01 |  | 138 | 0 | 0 | 0 |  | Taylor | Taylor | Tier 4 |  |  |  | 60354, 60355 | Y | N |  | Anticipated energization date of 7/1/2014 | 4174 | 3884
06TPIT0043A | Sherry - Liggett 138 kV line and Liggett - International Air |  | Construction schedule change | Watson | GM | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5042-WA | 2014-08-01 |  | 138 | 0 | 3.3 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 2128, 2133, 2137, 2140, 2141 | Y | N |  | Sherry - GM section was completed in 2009. | 2777 | 2653
3685 | Hargrove: Build 138 kV station | Construct new Hargrove station along the Big Lake to Twin Buttes 138 kV line | IN SERVICE and Project Title Update | Hargrove |  | Planned | 652 - 0821 | AEP TNC | Eric Scott 918-599-2664 | 1816 | 2014-08-11 | 2014-08-11 | 138 | 0 | 0 | 0 |  | Irion |  | Tier 4 |  |  |  | 6559, 6648, 6535, 76011 | Y | N |  |  | 3926 | 3685
14TPIT0097 | Colorado - Nada 138 kV Transmission Line Conversion | Convert the 20 mile Colorado (7636) - Nada (5536) 69-kV transmission line to 138-kV, 220 MVA. | ERCOT approval through RPG review process was granted March 27, 2012 | Colorado | Nada | In-Service | 13TPIT0150 (STEC) | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-08-12 | 2014-08-15 | 138 | 0 | 20 | 0 |  | Colorado | Colorado | Tier 3 | 2012-02-01 | 2012-03-27 |  | 77636, 78103 | Y | N |  | Coordinate with STEC | 2775 | 2651
3723 | Benedum Substation Addition | Construct a new 138-kV substation, Benedum (71213), on the LCRA Midkiff (1210) to Upton (1212) 138-kV transmission line. |  | Benedum | Midkiff / Upton | In-Service |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-08-29 | 2014-08-29 | 138 | 0 | 0 | 0 |  | Upton |  | Tier 4 |  |  |  | 71213, 1210, 1212 | Y | N |  |  | 3967 | 3723
3694 | AEP_Add_MAYBERRY | Distribution Project DR13X0003 |  | FRONTERA | SLU TAYLOR ROAD | Planned |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2014-08-31 |  | 138 | 0 | 0 | 0 |  | Hidalgo |  | Tier 4 |  |  |  | 8109, 8391, 8980 | Y |  |  |  | 3937 | 3694
13TPIT0119B | Vanderbilt to Ricebird 138 kV circuit | New 138 kV line on existing structures |  | ETP | Vanderbilt | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-09-01 | 2014-08-27 | 138 | 26.5 | 0 | 0 |  | Jackson | Wharton | Tier 2 | 2011-10-07 | 2012-01-26 |  | 5523, 5584 | Y | N |  | project costs were included with 13tpit0119a | 2673 | 2558
12TPIT0140 | South Batesville breaker addition | Adds breakers to South Batesville to allow closing of normally open South Batesville to Frio Town. Creates 3- terminal switching station |  | South Batesville |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-09-01 | 2014-09-26 | 69 | 0 | 0 | 0 |  | Zavala |  | Tier 4 |  |  |  | 5832, 5848 | Y | N |  |  | 1553 | 1537
3329 | Garfield Auto2 back in service |  |  | Garfield | Garfield | Planned |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2014-09-01 |  | 138 | 0 | 0 | 480 |  |  |  | Tier 4 |  |  |  | 9071, 9048 | Y |  |  |  | 3510 | 3329
3879 | GSEC_3879_Add_Busby_Sub |  |  |  |  | Under Construction | NA | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2014-09-01 |  | 138 | 0 | 0 | 0 |  | Irion | Irion | Tier 4 |  |  |  | 60356, 6648 | Y | N |  | Anticipated energization date of 8-1-2014. | 4169 | 3879
14TPIT0106 | SW Vernon to Vernon Main: Rebuild 69 kV line | SW Vernon to Vernon Main: Rebuild 69 kV line with 959.6 ACSS/TW | IN SERVICE | SW Vernon | Vernon Main | In-Service | 315 - 0470 | ETT | Dave Goetz 918-599-2664 | 3154 | 2014-09-04 | 2014-09-04 | 69 | 0 | 4.6 | 0 |  | Wilbarger | Wilbarger | Tier 4 |  |  |  | 6062, 6063, 6079, 6058, 6061, 6064 | Y | Y |  |  | 3954 | 2755
3686 | Vinson: Build 138 kV station | Construct new Vinson station along the South Abilene to Putnam 138 kV line | IN SERVICE and Project Title Update | Vinson |  | Planned | 653 - 0822 | AEP TNC | Eric Scott 918-599-2664 | 1817 | 2014-09-10 | 2014-09-10 | 138 | 0 | 0 | 0 |  | Taylor |  | Tier 4 |  |  |  | 60355, 6260, 6313 | Y | N |  |  | 3927 | 3686
13TPIT0112 | North Andrews 138 kV capacitors | Install shunt capacitors | Construction schedule change | North Andrews |  | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8157-E | 2014-09-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Andrews |  | Tier 4 |  |  |  | 1159 | Y | N |  |  | 3355 | 3184
3759 |  | Substation for new Windthorst wind generation | New sub |  |  | Planned |  | BEPC | Dwight Beckman dbeckman@brazoselectric.com 254-750-6373 |  | 2014-09-15 |  | 69 | 0 | 0 | 0 |  | Archer |  | Tier 4 |  |  |  | 33776, 776, 1605 | Y |  |  |  | 4004 | 3759
11TPIT0108 | Penascal: Add 345 kV EPS Metering for Phase 3 | Penascal Wind Phase 3 (Baffin Wind, LLC.) | Updated Project Title and Schedule | Penascal |  | Under Construction | 489 - 0690 | ETT | Glen Reed gareed@aep.com 918-599-2664 | 3370 | 2014-09-30 |  | 345 | 0 | 0.4 | 0 |  | Kenedy |  | Tier 4 |  |  |  | 80071, 80171 | Y | N |  |  | 3275 | 3106
3987 | Lorentz: EF 90 Temporary Tap | Install a Temporary 138kV Station Skid | New | Champlin |  | Planned | 674 - 0843 | AEP TCC | John Pulay gareed@aep.com 918-599-2664 | 3534 | 2014-09-30 | 2014-09-30 | 138 | 0 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 8090, 8476, 8479 | Y | N |  |  | 4312 | 3987
14TPIT0130 | Triangle Park Substation | Install (3) Breaker ring to allow loop-in of 138 kV line (Dansby to Jack Creek) and 138 kV line to industrial customer. |  | Triangle Park | Triangle Park | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2014-10-01 |  | 138 | 0 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32854 | Y |  |  |  | 3305 | 3136
15TPIT0027 | Millican Substation Upgrade | Install (3) Breaker ring to support (2) 138kV lines and (1) 138-69 auto-transformer |  | Millican Substation | Millican Substation | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2014-10-01 |  | 138 | 0 | 0 | 0 |  | Brazos |  | Tier 4 |  |  |  | 32855, 32898, 32889, 32895, 32856 | Y | N |  |  | 1834 | 1791
15TPIT0026 | Wellborn to Millican Upgrade | ReBuild-Reconductor (3.6) miles of 69kV line converting to 138 kV as part of 138 kV BEC Roans Prairie Project |  | Wellborn Susbstation | Millican Substation | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2014-10-01 |  | 138 | 0 | 3.6 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 32856, 32895 | Y | N |  |  | 1833 | 1790
3906 | Dessau-Sprinkle: Ckt2 Cut-In | Dessau-Sprinkle Circuit 1011 Cut-In to Sprinkle Sub |  | Dessau | Sprinkle | Under Construction |  | AEN | Biju Mathew biju.mathew@austinenergy.com 512-322-6737 |  | 2014-10-01 |  | 138 | 0 | 6.23 | 0 |  | Travis | Travis | Tier 4 |  |  |  | 9184, 9193, 9271 | Y |  |  |  | 4202 | 3906
3765 | Bessel 138 kV Tap Station | Temporary custormer interconenction | Updated Transmission Status AND estimates | BESSEL |  | In-Service | 671-0840 | AEP TCC | DAVE GOETZ GAREED@AEP.COM 918-599-2664 | 3532 | 2014-10-01 | 2014-09-29 | 138 |  |  |  |  | Nueces |  | Tier 4 |  |  |  | 80601, 8452, 8514 | Y | N | NA |  | 4010 | 3765
13TPIT0148A | Cotulla 138 kV bus load and auto | First phase moves load from 69 to 138 kV in February 15 |  | Cotulla |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-10-02 | 2015-02-01 | 138 | 0 | 0 | 0 |  | La Salle |  | Tier 1 | 2012-04-16 | 2012-08-30 | 2012-09-18 | 8520 | Y | N |  | project costs in second phase | 3649 | 3449
14TPIT0031A | Project to add new Auto #2 and moving existing #3 to new pos | Move existing autotransformer from bus 5055 to bus 5054 |  |  |  | Planned | T-0176 | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | S-0588 | 2014-10-09 |  | 345 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5052, 5054, 5055, 5430, 5056, 5057, 5059 | Y | N |  |  | 2861 | 2736
14TPIT0073 | Kokernut Substation | Build a new 138x69-26.18 kV 18-24-30 MVA substation on the GVEC Gonzales-GVEC Shiner 69 kV transmission line |  | Kokernut | Gonzales / Shiner | In-Service |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2014-10-22 | 2014-10-31 | 69 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  | 7591, 7590, 7592 | Y | N |  |  | 2223 | 2151
3695 | Tynan: Add new Distribution station | Distribution Project DP13X0037 |  | BEEVILLE | MATHIS | Planned |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2014-10-31 |  | 69 | 0 | 0 | 0 |  | Bee |  | Tier 4 |  |  |  | 8107, 8198, 8407 | Y |  |  |  | 3938 | 3695
4015 | Bates-Garza:tap for WF connection | Construct a 138 kV temporary tap on Bates to Garza line for the Generation Interconnect | Change Transmission status, ISD | BATES | GARZA | In-Service | 669 - 0838 | AEP TCC | William (Bill) Clark gareed@aep.com 918-599-2664 | 3530 | 2014-10-31 | 2014-12-09 | 138 |  |  |  |  | Starr |  | Tier 4 |  |  |  | 8835, 8392, 8399 | Y | N |  |  | 4360 | 4015
13TPIT0193 | Tomball Reactor | Install 50MVAR reactor at Tomball substation. |  | Tomball |  | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-10-31 | 2014-11-13 | 138 | 0 | 0 | 0 | -50,0 | Harris |  | Tier 4 |  |  |  | 46510 | Y | N |  |  | 2378 | 2302
3659 | New Midstream 138 kV station | New load serving station with a short line to AEP Bessel |  | Midstream |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-10-31 | 2014-10-31 | 138 | 0.4 | 0 | 0 |  | Nueces |  | Tier 4 |  |  |  | 5643, 80601 | Y | N |  |  | 3893 | 3659
14TPIT0123 | Dimmit Substation Addition | Construct a new 138-kV substation, Dimmit (78281), on the LCRA Asherton to Rosita Creek 138-kV transmission line. |  | Dimmit | Asherton / Rosita Ck | In-Service |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-11-03 | 2014-10-31 | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 4 |  |  |  | 78281, 8274, 8283 | Y | N |  |  | 3203 | 3034
3274 | Nacogdoches to Skyline MLSE Upgrade | Upgrade terminals at Skyline and Nacogdoches to ensure a rating of 2386 A (minimum). |  | Skyline | Nacogdoches | Planned | S-0731b | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2014-11-13 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5315, 5369 | Y | N |  | There are no transformers associated with this project | 3450 | 3274
3697 | Neas: Build 138 kV station | Construct new Neas station along the Ft. Phantom to South Abilene 138 kV line | IN SERVICE and Cost Update | Neas |  | In-Service | 654 - 0823 | AEP TNC | Eric Scott 918-599-2664 | 1818 | 2014-11-14 | 2014-11-14 | 138 | 0 | 0 | 0 |  | Jones |  | Tier 4 |  |  |  | 60366, 6222, 6292 | Y | N |  |  | 3940 | 3697
07TPIT0116 | Handley - Duval 69 kV line | Upgrade existing 69 kV line |  | Handley | Duval | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5116-E | 2014-11-15 |  | 69 | 0 | 10.8 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1952, 2158 | Y | N |  |  | 4753 | 2655
14TPIT0086 | Allen Sw - Parker Maxwell Creek - Ben Davis 138 kV line | Reconductor existing 138 kV line |  | Allen Switch | Ben Davis Switch | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M4102-E | 2014-11-15 |  | 138 | 0 | 9.4 | 0 |  | Collin | Collin | Tier 4 |  |  |  | 968, 2477, 2509, 12509 | Y | N |  |  | 2351 | 2278
14TPIT0138 | Roanoke Switch - Coppell Switch 138 kV Line Phase 1 | Rebuild existing double-circuit Roanoke Switch - Southlake line section |  | Roanoke Switch | Southlake | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5001B-WAC | 2014-11-15 |  | 138 | 0 | 7.4 | 0 |  | Tarrant | Tarrant | Tier 4 |  |  |  | 1852, 2018, 2020 | Y | N |  | An interim rating increase for the Roanoke Switch - Roanoke West line section was implemented in July 2012. | 2689 | 2573
06TPIT0043B | Sherry - Liggett 138 kV line and Liggett - International Air | Rebuild existing International Airport - Liggett line section |  | International Airport | Liggett | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | M5042-WA | 2014-11-15 |  | 138 | 0 | 5.2 | 0 |  | Tarrant | Dallas | Tier 4 |  |  |  | 1922, 1924, 2124, 2125 | Y | N |  | Sherry - GM section was completed in 2009. | 4210 | 2653
4130 | SLU_Luther_addition |  |  | N/A | N/A | Planned | N/A | SLU | Brad Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2014-12-01 |  | 138 | 0 | 0 | 0 |  | Howard | Howard | Tier 4 |  |  |  | 79559, 79600, 79603 | Y | N | N/A |  | 4475 | 4130
14TPIT0081 | Bowie Capacitor Bank | Install 15 MVAR at Bowie substation |  | Bowie | Bowie | Planned |  | BEPC | Kenneth Dye kdye@brazoselectric.com 254-750-6353 | 12012 | 2014-12-01 |  | 138 | 0 | 0 | 0 | 0,15 | Montague |  | Tier 4 |  |  |  | 620 | Y | N |  |  | 2727 | 2609
3668 | New Kittie West substation | Add new station for AEP load on 69 kV |  | Kittie West |  | In-Service |  | STEC | Doug Evans devans@stec.org 361-485-6459 |  | 2014-12-01 | 2014-12-01 | 69 | 0 | 0 | 0 |  | Live Oak |  | Tier 4 |  |  |  | 5683, 5685, 5690 | Y | N |  |  | 3905 | 3668
3757B | Line rebuild and XMFR upgrade OLSEN. | Olsen Auto replace/upgrade. |  | 37460 | 37470 | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07314 and NTE07414 | 2014-12-01 | 2014-12-01 | 138 | 0 | 0 | 167 |  | Bosque | Bosque | Tier 4 |  |  |  | 37470, 37460 | Y |  |  |  | 4503 | 3757
3757A | Line rebuild and XMFR upgrade OLSEN. | Rebuild Lake Whitney - Olsen 69 KV with 795 ACSS |  | 37420 | 37470 | Planned |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | NTE07314 and NTE07414 | 2014-12-01 | 2014-12-01 | 69 | 0 | 13.75 | 0 |  | Bosque | Bosque | Tier 4 |  |  |  | 37420, 37470 | Y |  |  |  | 4502 | 3757
4117 | GSEC_4117_Add_Ketchum_Mountain_Sub | [5 empty] | NA | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2014-12-01 |  | 138 | 0 | 0 | 0 |  | Irion | Irion | Tier 4 |  |  |  | 60379, 60374 | Y | N |  | Anticipated energization date of 11/1/2014 | 4463 | 4117
4128 | SLU_ArprtRd_addition |  |  | N/A | N/A | Planned | N/A | SLU | Brad Schwarz bschwarz@huntpower.com 512-289-7425 |  | 2014-12-01 |  | 138 | 0 | 0 | 0 |  | Mitchell | Mitchell | Tier 4 |  |  |  | 79557, 11342 | Y | N | N/A |  | 4473 | 4128
12TPIT0062A | Butler Road - New Substation | High side (138 kV) energization. | Project moved forward and under construction. |  |  | Under Construction |  | TNMP | Robert Lona Robert.Lona@tnmp.com 281-581-4732 | STE04512 | 2014-12-05 |  | 138 | 0 | 0 | 0 |  | Galveston | Galveston | Tier 4 |  |  |  | 38930, 38920, 38950 | Y |  |  |  | 4511 | 1191
14TPIT0074 | Thompson Creek to Snook Transmission Line | Build 6 miles of 1033ACSR transmission line (operated at 138 kV) to Snook substation. | The Thompson Creek to Koppe Bridge Line is now broken into two segments with different completion dates. | Thompson Creek | Snook Substation | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2014-12-12 |  | 138 | 2.4 | 3.6 | 0 |  | Brazos | Burleson | Tier 4 |  |  |  | 32857, 32863 | Y | N |  |  | 2050 | 1999
3890 | Whiting: Build new 138 kV station | Construct new Whiting station along the Hamilton Road to Sonora 138 kV line | NEW | Whiting |  | Planned | 679 - 0848 | AEP TCC | Eric Scott 918-599-2664 | 2598 | 2014-12-12 |  | 138 | 0 | 0 | 0 |  | Val Verde |  | Tier 4 |  |  |  | 8261, 8257, 8259, 6515 | Y | N |  |  | 4184 | 3890
14TPIT0052 | Stanton East - Buffalo (SU) - Midland East 138 kV Line | Rebuild existing line |  | Midland East | Stanton East | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8025-WAC | 2014-12-15 |  | 138 | 0 | 27.2 | 0 |  | Martin | Midland | Tier 4 |  |  |  | 1023, 1326, 79549 | Y | N |  |  | 3005 | 2832
13TPIT0152 | Elmar - Mason 138 kV line | Rebuild existing 138 kV line |  | Elmar | Mason | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8066-E | 2014-12-15 |  | 138 | 0 | 11.8 | 0 |  | Winkler | Reeves | Tier 3 | 2012-05-15 | 2012-06-15 |  | 1093, 1094 | Y | N |  | Wink - Loving complete in 11/2013, Loving - Elmar complete in 12/2013 and Elmar - Mason complete in 5/2014 | 3158 | 2989
14TPIT0084 | Buzzard Draw 138 kV Switching Station | Install 138 kV circuit breakers |  | Buzzard Draw |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8034-E | 2014-12-15 |  | 138 | 0 | 0 | 0 |  | Dawson |  | Tier 4 |  |  |  |  | Y | N |  |  | 3292 | 3123
14TPIT0085 | Lamesa Switching Station | Install 138 kV circuit breakers |  | Lamesa |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8033-E | 2014-12-15 |  | 138 | 0 | 0 | 0 |  | Howard |  | Tier 4 |  |  |  |  | Y | N |  |  | 3294 | 3125
15TPIT0086 | Mockingbird 138 kV capacitors | Install shunt capacitors |  | Mockingbird |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8153-WAC | 2014-12-15 |  | 138 | 0 | 0 | 0 | 0,55.2 | Ector |  | Tier 4 |  |  |  | 1182 | Y | N |  |  | 3334 | 3163
15TPIT0075 | Midway 69 kV capacitors | Install shunt capacitors |  | Midway |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8145-WAC | 2014-12-15 |  | 69 | 0 | 0 | 0 | 0,27.6 | Ector |  | Tier 4 |  |  |  | 1253 | Y | N |  |  | 3446 | 3270
13TPIT0094 | Lamesa - Buzzard Draw 138kV line | Add second circuit to existing line |  | Lamesa | Buzzard Draw | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8032-E | 2014-12-15 |  | 138 | 21.5 | 0 | 0 |  | Dawson | Howard | Tier 2 | 2008-10-01 | 2011-01-01 |  | 1163, 1355 | Y | N |  |  | 2682 | 2566
14TPIT0053 | Moss - Westover 138 kV line | Reconductor existing line |  | Moss | Westover | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8016-E | 2014-12-15 |  | 138 | 0 | 3.4 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1019, 1129 | Y | N |  |  | 2806 | 2682
14TPIT0090 | Monticello shunt reactors | Install shunt reactors |  | Monticello SES |  | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R919-WAC | 2014-12-15 |  | 345 | 0 | 0 | 0 | -100,0 | Titus |  | Tier 4 |  |  |  | 1695 | Y | N |  |  | 2349 | 2276
14TPIT0118 | Permian Basin - Wink 138 kV line | Rebuild existing 138 kV line |  | Permian Basin | Wink | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8105-E | 2014-12-15 |  | 138 | 0 | 16.5 | 0 |  | Ward | Winkler | Tier 4 |  |  |  | 1010, 1074 | Y | N |  |  | 2998 | 2825
14TPIT0137 | Odessa EHV - Odessa 138 kV Line | Reconductor existing 138 kV line |  | Odessa EHV | Odessa | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8143-E | 2014-12-15 |  | 138 | 0 | 2.3 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1027, 1126 | Y | N |  |  | 3002 | 2829
4197 | Pumpjack: Build 138 kV station | Construct 138 kV POD box bay for customer interconnection | IN SERVICE and Cost Update | Pumpjack |  | In-Service | 686 - 0856 | AEP TNC | Eric Scott 918-599-2664 | 2603 | 2014-12-15 | 2014-12-15 | 138 | 0 | 0 | 0 |  | Irion |  | Tier 4 |  |  |  | 60374, 6559, 6648 | Y | N |  |  | 4553 | 4197
4199 | Hoefs Road: Install a 69 kV skid station | Construct a 69 kV skid station on the Barrilla Junction to Verhalen line | Project Title, Project Description and Cost Update and IN SERVICE | Hoefs Road |  | In-Service | 690 - 0860 | AEP TNC | Brent Harris 918-599-2664 | 2607 | 2014-12-16 | 2014-12-16 | 69 | 0 | 0 | 0 |  | Reeves |  | Tier 4 |  |  |  | 6654, 6649, 6653 | Y | N |  |  | 4555 | 4199
15TPIT0018 | Kerrville Stadium to Raymond F. Barker | Upgrade the 10.1-mile Kerrville Stadium (7136) - Kerrville Travis (7162) - Kerrville Legion (7160) - Raymond F. Barker (7159) 69 kV transmission lines to 795 ACSR, 138 kV (235 MVA) and OPGW. |  | Kerrville Stadium | Raymond F Barker | In-Service |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-12-16 | 2014-11-16 | 138 | 0 | 10.1 | 0 |  | Kerr | Kerr | Tier 4 |  |  |  | 7136, 7159, 7160, 7162, 77160, 77162, 7138, 7158 | Y | N |  | Coordinate with KPUB | 1006 | 1005
14TPIT0122 | Bevo Station Addition | Construct a new 138-kV substation, Bevo (78280), which will cut into the LCRA TSC Asherton (8283) to Escondido (8260) 138-kV transmission line. |  | Bevo | Asherton / Escondido | In-Service | 14TPIT0059 (STEC) | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2014-12-19 | 2014-12-19 | 138 | 0 | 0 | 0 |  | Dimmit |  | Tier 4 |  |  |  | 78280, 8283, 78281 | Y | N |  |  | 2418 | 2341
3675 | Foxtail: Build 345 kV temporary tap | Interconnect Green Pastures Wind Farm at Foxtail to connect Green Pastures and Vertigo to the Oklaunion to Mulberry Creek 345 kV line | IN SERVICE and Cost Update | Foxtail |  | In-Service | 650 - 0818 | AEP TNC | Dave Goetz 918-599-2664 | 1812 | 2014-12-19 | 2014-12-19 | 345 | 0 | 0 | 0 |  | Baylor |  | Tier 4 |  |  |  | 6076, 6100, 6235 | Y | N |  |  | 3912 | 3675
3947 | Illinois #4: Replace 138/69 kV autotransformer | Replace the Illinois #4 autotransformer | Company Contact and Cost Update and IN SERVICE | Illinois #4 |  | In-Service | 685 - 0855 | ETT | Brent Harris 918-599-2664 | 1852 | 2014-12-19 | 2014-12-19 | 138 | 0 | 0 | 90 |  | Crockett |  | Tier 4 |  |  |  | 6565, 6564, 6563 | Y | N |  |  | 4265 | 3947
14TPIT0075 | Millican to BEC HWY 6Line | Build(6) miles of new 1033 ACSR energized at 138 kV to planned BEC HWY 6 substation as part of Dobbin Project |  | Millican Substation | BEC HWY 6 Substation | Planned |  | BRYN | James Tanneberger 979-821-5763 |  | 2014-12-23 |  | 138 | 6 | 0 | 0 |  | Brazos | Brazos | Tier 4 |  |  |  | 6, 32856 | Y | N |  |  | 2367 | 2292
15TPIT0043A | Fort Bend Area Upgrades | Convert FOSTER substation from 69kv service to 138kv tap off of Ckt.25 Flewellen - Peters |  | FOSTER | Peters/Flewellen | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 937 | 2014-12-27 | 2014-10-23 | 138 | 0 | 1.3 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2012-09-14 | 2012-10-29 |  | 44250, 44255, 44100, 44230, 44240, 44640, 44231, 44610, 46220 | Y | N |  | Cost included in project 15TPIT0043D. | 4566 | 4208
3693 | Holcomb: Add new Distribution station | Distribution Project DP13X0014 |  | NORTH LAREDO SWITCHING STATION | REVEILLE | Planned |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2014-12-31 |  | 138 | 0 | 0 | 0 |  | La Salle |  | Tier 4 |  |  |  | 8108, 8619, 8909 | Y |  |  |  | 3936 | 3693
3732 | Cedar Bayou to Jordan Ckt.99 | Upgrade equipment at Cedar Bayou to increase Ckt.99 thermal ratings. |  | Cedar Bayou | Jordan | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-12-31 | 2014-05-30 | 345 | 0 | 0 | 0 |  | Chambers | Chambers | Tier 4 |  |  |  | 40000, 40850 | Y | N |  |  | 3977 | 3732
14TPIT0076 | Fry Road 138kV Substation | Expand existing 138kV Fry Road Mobile substation to become permanent 138kV Fry Road distribution substation. Double tap off Ckt.09 Zenith - Gertie tap and Ckt.76 Zenith - Gertie tap. |  | Fry Road | Zenith/Gertie | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 612 | 2014-12-31 | 2014-12-17 | 138 | 0.1 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 45811, 45812, 45813, 44910, 45610, 45801, 45802, 46302 | Y | N |  |  | 4293 | 2347
3990 | Gila: Re-termination of Morris Street-Nueces Bay | Re-terminate Morris Street-Nueces Bay 138 kV line into the existing ETT Gila GIS station. |  | Gila | Morris Street | Under Construction |  | AEP TNC | Michael Glueck mglueck@aep.com 918-599-2042 |  | 2014-12-31 | 2014-12-14 | 138 | 0.28 | 0 | 0 |  | Nueces | Nueces | Tier 4 |  |  |  | 8441, 8474, 80260 | Y | N |  |  | 4316 | 3990
14TPIT3389 | Dunlavy to Hyde Park Ckt 32 Upgrade | Upgrade substation equipment at Dunlavy to increase Ckt.32 thermal ratings |  | Dunlavy | Hyde Park | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-12-31 | 2014-12-18 | 69 | 0 | 0 | 0 |  | Harris | Harris | Tier 4 |  |  |  | 47580, 47690 | Y | N |  |  | 3587 | 3389
14TPIT0042B | Five Points to Broadview - 138 kV Transmission Line Rebuild | Rebuild 138 kV transmission line from Five Points to Broadview (All conductor replaced) |  | Five Points | Broadview | Planned |  | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 | T-0208 | 2014-12-31 |  | 138 | 0 | 9.4 | 0 |  | Bexar | Bexar | Tier 3 |  |  |  | 5040, 5150 | Y | N |  | There are no transformers associated with this project | 957 | 956
14TPIT0077 | PH Robinson Autotransformer A1 Upgrade | Replace existing 400MVA PH Robinson autotransformer A1 with 800MVA autotransformer. |  | PH Robinson |  | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2014-12-31 | 2014-12-16 | 345 | 0 | 0 | 400 |  | Galveston |  | Tier 4 |  |  |  | 42000, 42015, 49026 | Y | N |  |  | 2543 | 2438
4526 | Increase capacity of line |  |  | Collin | Frisco (Brazos) | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 |  | 2015-01-01 |  | 138 | 0 | 1.7 | 0 |  | Collin | Denton |  |  |  |  | 681, 2370 | Y | N |  |  | 4924 | 4526
4238 | Hutto Switching Station - Round Rock 138 kV Line | Upgrade operating temperature of existing 138 kV line |  | Hutto | Round Rock | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 |  | 2015-01-10 |  | 138 | 0 | 9.1 | 0 |  | Williamson | Williamson | Tier 4 |  |  |  | 3666, 3668, 3670 | Y | N |  |  | 4611 | 4238
3933 | Aruba 138 kV POI | Convert Aruba POI to 138 kV operation |  | Spraberry Tap | Aruba | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8239 | 2015-01-13 |  | 138 | 6.8 | 0.5 | 0 |  | Midland | Midland | Tier 4 |  |  |  | 1220, 1221, 1222, 1337, 1328 | Y | N |  |  | 4235 | 3933
3882 | GSEC_3882_Add_Horton_Sub |  | NA |  |  | Under Construction | NA | GOLDENSPREAD | Chris Koenig ckoenig@gsec.coop 806-349-5201 |  | 2015-01-15 |  | 138 | 0 | 0 | 0 |  | Jones | Jones | Tier 4 |  |  |  | 60353, 60366 | Y | N |  | Anticipated energization date of 03/2015 | 4172 | 3882
4244 | Odessa North Switch - Odessa Basin Switch 69 kV Line | Upgrade existing line |  | Odessa North Switch | Odessa Basin Switch | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R8223 | 2015-01-15 |  | 69 | 0 | 9.4 | 0 |  | Ector | Ector | Tier 4 |  |  |  | 1123, 1254 | Y | N |  |  | 4618 | 4244
3938A | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.26 Angleton to STRATT to increase thermal ratings. | Delay in Project Schedule | Angleton | STRATT | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-01-28 |  | 138 | 0 | 13.8 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42110, 43300 | Y | N |  |  | 4249 | 3938
3938B | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.26 STRATT to SINTEK to increase thermal ratings. | Delay in Project Schedule | STRATT | SINTEK | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-01-29 |  | 138 | 0 | 6.4 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43240, 43300 | Y | N |  |  | 4250 | 3938
15TPIT0043D | Fort Bend Area Upgrades | Convert 69kv Rosenberg substation to 138kv and reconfigure existing circuits to create new Ckt.60 Orchard - Rosenberg - Fort Bend. |  | Rosenberg | Orchard/Fort Bend | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 937 | 2015-01-30 |  | 138 | 0 | 1.5 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2012-09-14 | 2012-10-29 |  | 44610, 44611, 44010, 44070, 44171, 44230, 44250, 44280, 44290, 44300, 44540, 44580, 44341, 46220 | Y | N |  |  | 4567 | 4208
3938C | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.82 Angleton to Richwood to increase thermal ratings. | Delay in Project Schedule | Angleton | Richwood | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-01-30 |  | 138 | 0 | 14.2 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 42110, 43150 | Y | N |  | Cost Included in TPIT Project 3938A | 4251 | 3938
3580 | Cottulla STEC tap into AEP Line | Cotttulla STEC Substation tap into existing AEP Dilley SS to Reveille 138kV Line. |  | Jardin | Cotulla | Planned | 631 - 0800, 3719 | AEP TCC | Glen Reed 918-599-2664 | 3510 | 2015-01-30 |  | 138 | 0 | 0 | 0 |  | La Salle | La Salle | Tier 4 |  |  |  | 8520, 8610, 8611 | Y | N |  |  | 3794 | 3580
15TPIT0043E | Fort Bend Area Upgrades | Remove 69kv facilities at Flewellen substation and convert existing circuit to create new 138kV Ckt.60 Flewellen - Fort Bend. |  | Flewellen | Fort Bend | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 937 | 2015-01-31 |  | 138 | 0 | 9.3 | 0 |  | Fort Bend | Fort Bend | Tier 3 | 2012-09-14 | 2012-10-29 |  | 44240, 49013, 44250, 44230 | Y | N |  | Cost included in project 15TPIT0043D. | 4568 | 4208
16TPIT0051 | Athens - Forest Grove 138 kV line | Upgrade existing line |  | Athens | Forest Grove | Under Construction |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R6018-E | 2015-01-31 |  | 138 | 0 | 16.9 | 0 |  | Henderson | Henderson | Tier 4 |  |  |  | 3131, 3238, 3247, 3248 | Y | N |  |  | 4140 | 3111
3938D | Angleton Area Ckt.26 & 82 Upgrades | Upgrade 138kV Ckt.82 Richwood to Cavern to increase thermal ratings. | Delay in Project Schedule | Richwood | Cavern | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 1055 | 2015-01-31 |  | 138 | 0 | 5.4 | 0 |  | Brazoria |  | Tier 4 |  |  |  | 43150, 43330 | Y | N |  | Cost Included in TPIT Project 3938A | 4252 | 3938
14TPIT3346 | Clinton Conversion | Convert all Clinton load to 138kV. Convert Clinton 138kV from tap to loop service. | Delay in project schedule | Clinton | Ninth/Anbush | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-01-31 | 2015-01-06 | 138 | 0 | 0 | 0 |  | Harris |  | Tier 4 |  |  |  | 40350, 40351, 40352, 40235, 41160, 47540 | Y | N |  |  | 3534 | 3346
14TPIT3257 | Smithers to Bellaire Ckt.98 | Upgrade 138kV Ckt.98 Smithers to Bellaire to increase thermal ratings. |  | Smithers | Bellaire | Planned |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 |  | 2015-01-31 |  | 345 | 0 | 25.4 | 0 |  | Fort Bend | Harris | Tier 4 |  |  |  | 44650, 47000 | Y | N |  |  | 3431 | 3257

## CancelledTPIT020115NoCost
FEBRUARY BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS AS OF 2/1/2015
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional) | Phase Number | MOD Project Number
12TPIT0190 | Boots: Build 138 kV station | Interconnect White Camp Solar Farm at Boots to connect White Camp to the Spur to Sun 138 kV line | Project Title and Schedule Update | Boots |  | Under Construction | 507 - 0718 | AEP TNC | Eric Scott 918-599-2664 | 2502 | 2015-05-31 |  | 138 | 0 | 0 | 0 |  | Kent |  | Tier 4 |  |  |  | 6179, 720, 6150 | N | N |  |  | 1849 | 1806
3506 | Sinton to Skidmore: Rebuild 69kV Line | Rebuild Sinton to Skidmore 69kV Line for future 138 kV operation | CHANGES | SINTON | SKIDMORE | Under Construction | 579-0737 | AEP TCC | FRANK PRITZLAFF gareed@aep.com 918-599-2664 | TP2012071 | 2015-05-31 |  | 69 |  | 10.5 | 0 |  | San Patricio | Bee | Tier 3 | 2012-08-31 | 2012-12-27 | 2013-04-05 | 8405, 8413 | N | N | NA | NA | 3713 | 3506
3575 | Raymondville #1 to Raymondville #2: Open 69 kV Line | Segment the Harlingen Switching Station to Raymondville #2 69 kV throughpath by opening the line between Raymondville #1 and Raymondville #2 | Cancel Project (Line is Open in Ops Model) | Raymondville #1 | Raymondville #2 | Planned |  | AEP TCC | Glen Reed gareed@aep.com 918-599-2664 |  | 2015-06-30 |  | 69 | 0 | 0 | 0 |  | Willacy | Willacy | Tier 4 |  |  |  | 8300, 8325, 8700 | N | N |  | RTP: 2012-R11 | 3789 | 3575
15TPIT0063 | Gillett Substation | Construct the new Gillett Substation (78582) on the existing LCRA TSC Nixon AEP (78580) - Milton (78583)138-kV transmission line. |  | Gillett | Milton / Nixon AEP | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2015-12-30 |  | 138 | 0 | 0 | 0 |  | Gonzales |  | Tier 4 |  |  |  |  | N | N |  |  | 3408 | 3235
3912 | Whitsett (Campbellton) 69kV Substation: STEC Interconnect | Whitsett (Campbellton) 69kV Substation: STEC Interconnect | NEW | PLEASANTON | THREE RIVERS | Planned | 638 - 0807 | AEP TCC | GLEN REED 918-599-2664 | 3514 | 2016-01-30 |  | 69 | 0 | 0 | 0 |  | Atascosa |  | Tier 4 |  |  |  | 8137, 8406, 8600 | N | N |  |  | 4212 | 3912
14TPIT0096 | Nevada-Olinger 138 kV line upgrade | Nevada-Olinger 138 kV line upgrade | On Hold For Funding | A new switch at new Nevada | A switch at Olinger | Planned |  | GARLAND | Danh Huynh dhuynh@garlandpower-light.org 972-205-3826 |  | 2016-06-01 |  | 138 | 0 | 9.5 | 0 |  | Dallas |  | Tier 4 |  |  |  | 811, 818 | N | N |  | This project is a new line for new load serving at Nevada | 2619 | 2514
12TPIT0007 | FM-725 - New Substation | Build a new 138-26.18 kV, 40 MVA substation on the GVEC McQueeney(7606) - Schumansville(7609) 138 kV transmission line | Cancelled | FM 725 | McQueeney-Schumansville | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-10-31 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7607, 7606, 7609 | N | N |  |  | 2222 | 2150
3878 | Schumannsville T3 Addition | Add T3, 40 MVA 138-26.18 kV power transformer, CSW, low side, panels, etc |  | Schmannsville |  | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org |  | 2016-10-31 |  | 138 | 0 | 0 | 0 |  | Guadalupe |  | Tier 4 |  |  |  | 7609 | N | N |  |  | 4168 | 3878
3275 | JT Deely to Converse MLSE Upgrade | Upgrade terminal at JT Deely to ensure a rating of 2386 A (minimum). | This project is now covered in project ID 3276 | JT Deely | Converse | Planned | S-0759a | CPS | Basilio Rocha bdrocha@cpsenergy.com 210-353-4933 |  | 2018-05-30 |  | 138 | 0 | 0 | 0 |  | Bexar | Bexar | Tier 4 |  |  |  | 5098, 5110 | N | N |  | There are no transformers associated with this project | 3451 | 3275
13TPIT0107 | Bobville Switching Station | Construct 345-138 kV switching station in CNP's Roans Prairie to Kuykendahl line |  | Dobbin | Dobbin | Planned | 13TPIT0107 15TPIT0022 16TPIT0016 | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713-207-2192 | 11045 | 2018-06-02 |  | 345 | 0 | 0 | 700 |  | Montgomery |  | Tier 4 | 2010-10-04 | 2010-12-20 | 2011-05-05 | 40640, 40600, 45972, 40630, 3 | N | Y |  |  | 1159 | 1156
4474 | Kendall to Kerrville Stadium Transmission Line Upgrade | Upgrade 16.68-mile Kendall (7150) to Kerrville Stadium (7138) 138-kV transmission line to bundle Drake (440 MVA). |  | Kendall | Kerrville Stadium | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2019-05-31 |  | 138 | 0 | 16.68 | 0 |  | Kendall | Kerr | Tier 1 | 2014-06-29 |  |  |  | N | N |  |  | 4860 | 4474
4476 | Kendall to Comfort Transmission Line Upgrade | Upgrade the 1.09-mile Kendall (7152) - Comfort (7155) 138-kV transmission line to bundle 1590 Lapwing conductor (669 MVA). Part of CPS-Tie Project. |  | Kendall | Comfort | Planned |  | LCRATSC | Charles Dewitt Charles.Dewitt@LCRA.org 512-578-4199 |  | 2019-05-31 |  | 138 | 0 | 1.09 | 0 |  | Kendall | Kendall | Tier 1 | 2014-06-29 |  |  |  | N | N |  |  | 4862 | 4476
06TPIT0143 | Temple Switch - Temple SE 138 kV line | Upgrade existing 138 kV line |  | Temple Switch | Temple SE | Conceptual |  | ONCOR | Michael Juricek michael.juricek@oncor.com 214-743-6671 | R448-E | 2024-05-15 |  | 138 | 0 | 4.4 | 0 |  | Bell | Bell | Tier 4 |  |  |  | 3415, 3612 | N | N |  |  | 1346 | 1342

## RTPProjects
Project Number | Project Name | Transmission Owner | ERCOT Proposed in-service year | TSP MOD in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2014-NC2 | Eastland Tap (1622)-Leon Switch (1625) 69-kV line upgrade | Oncor | 2015 | 2016-12-15 | Planned | 4268
2014-NC3 | Highlands TNP (37050)-West TNP (37060) 138-kV terminal equipment upgrade | TNMP | 2017
2014-NC4 | Trinidad (3128)-Powell (3467) 69-kV line upgrade | Oncor | 2019 | 2016-12-15 | Planned | 4273
2014-NC5 | Killeen Switch (3423)-Belton (3610) 138-kV circuit upgrade | Oncor | 2017 |  |  |  | Under Study
2014-NC7 | Bosque Switch (252) – Olsen (37460) 138-kV line terminal equipment upgrade | TNMP/Brazos Electric Power Co Op | 2015
2014-NC8 | Olsen (37460-37470) 138/69-kV autotransformer upgrade | TNMP | 2015
2014-NC9 | Firewheel (821) -Wylie Switch (833) 138-kV line upgrade | Garland | 2019 | 2017-12-31 | Planned | 3775
2014-NC10 | Northwest Carrollton (2362)-Lake Pointe TNP (37010) 138-kV line upgrade | Oncor / TNMP | 2019 |  |  |  | Under Study
2014-NC11 | Fox (478)-Sodasprings (484) 69-kV line upgrade | Brazos Electric Power Co Op | 2019
2014-NC12 | Trumbull (221-222) 138/69-kV autotransformer upgrade | Brazos Electric Power Co Op | 2017
2014-NC13 | Trinidad (3123)-Watermill (2427) 345-kV line upgrade | Oncor | 2019 | 5/15/2018; 5/15/2018 | Planned; Planned | 07TPIT0140; 4301
2014-NC14 | Lake Creek (3402)-Tradinghouse (3405)-Sam Switch (68090) 345-kV line upgrade | Oncor / Lone Star | 2019 | 5/15/2017; 12/15/2017 | Planned; Planned | 4304; 4303
2014-NC15 | Big Brown (3380)-Navarro (68091) 345-kV double circuit line upgrade | Oncor | 2019 | 2016-05-15 | Planned | 4299
2014-NC16 | Cedar Crest Switch (2493-2495) 138-kV bus tie upgrade | Oncor | 2017 |  |  |  | Under Study
2014-NC17 | Norwood Switch (2410-2404) 345/138-kV autotransformer #1 upgrade | Oncor | 2019 | 2015-05-15 | Planned | 11TPIT0097
2014-NC18 | Prairie Creek Switch (2762, 2763)-Parkdale (2445, 2442) 138-kV double circuit line upgrade | Oncor | 2019 | 2019-05-15 | Planned | 4285
2014-NC19 | Mountain Creek SES (2412)-Norwood Switch (2407) 138-kV line upgrade | Oncor | 2015 | 2016-05-15 | Planned | 14TPIT0012
2014-NC20 | Fisher Road Switch (1426)-Wind Creek (17007) 138-kV terminal equipment upgrade | Oncor | 2015 |  |  |  | Under Study
2014-NC21 | Fisher Road Switch (1425-1426) 345/138-kV autotransformer addition | Oncor | 2015 | 2016-05-16 | Planned | 17TPIT0032
2014-NC22 | Olsen TNP (37470)-Lake Whitney TNP (37420) 69-kV line upgrade | TNMP | 2019
2014-NC23 | Coryell County TNP (37530)-Sycamore TNP (37520) 69-kV line upgrade | TNMP | 2017
2014-NC24 | Walnut Springs TNP (37680) 69-kV bus capacitor bank upgrade | TNMP | 2020
2014-NC25 | Industrial Blvd (2976)-East Levee Switch (2482) 138-kV line upgrade | Oncor | 2019 |  |  |  | Under Study
2014-NC26 | Sargent Rd (2940, 2947)-Industrial Blvd (2974, 2975) 138-kV double circuit line upgrade | Oncor | 2017 | 2017-05-15 | Planned | 4330
2014-NC27 | Liggett Switch (1922, 1924)-Hackberry (2388) 138-kV double circuit line upgrade | Oncor | 2019 |  |  |  | Under Study
2014-NC28 | Reagan St (2819)-East Levee Switch (2482) 138-kV line upgrade | Oncor | 2015 | 2016-05-15 | Planned | 16TPIT0061
2014-NC29 | Hicks Switch (2081-2082) 345/138-kV autotransformer addition | Oncor | 2017 | 2017-05-14 | Planned | 16TPIT0018
2014-NC30 | NorthHaven Switch (2659)- Alpha Road (2597) 138-kV terminal equipment upgrade | Oncor | 2015 | 2016-05-15 | Planned | 16TPIT0050
2014-NC31 | Rockwall South (2711) –Rockwall East (2710) 138-kV line upgrade | Oncor | 2017 | 2016-05-15 | Planned | 17TPIT0019
2014-NC32 | Cedar Hill Switch (2422)-Sorcey Road (3050) 138-kV line upgrade | Oncor | 2015 | 2018-05-15 | Planned | 4355
2014-NC33 | Desoto Switch (2424)-Sterrett (2317) 138-kV line upgrade | Oncor | 2015 | 2017-05-15 | Planned | 4254
2014-NC34 | Everman (1883)-Mansfield (2208) 138-kV line upgrade | Oncor | 2015 | 2019-05-15 | Planned | 10TPIT0019
2014-NC35 | Renner Switch (2353)- Plano Coit Road (2521)-Plano Tennyson (2523) 138-kV line upgrade | Oncor | 2019 |  |  |  | Under Study
2014-NC36 | Collins Switch (2372-2370) 345/138-kV autotransformer #2 reactor addition | Oncor | 2017 | 2016-05-15 | Planned | 4354
2014-NC37 | Everman-Wedgwood 138-kV double circuit line upgrade | Oncor | 2015 | 2016-05-15 | Planned | 4251
2014-NC38 | Schroeder Road (2636, 2637)- Dallas Texas Instruments (2633, 2607) 138-kV double circuit line upgrade | Oncor | 2015 |  |  |  | Under Study
2014-NC39 | Bosque Switch (252) – Rogers Hill (249)-Elm Mott (3407) 138-kV line upgrade | Oncor/Brazos Electric Power Co Op | 2017 | 2020-05-15 | Planned | 4356
2014-NC40 | Ranger Gulf (1627)-Thurber TNP (37850) 69-kV terminal equipment upgrade | TNMP | 2015
2014-NC41 | Lewisville Switch (646-645, 33646-33645) 345/138-kV autotransformers 1 and 2 CMP | Brazos Electric Power Co Op | 2015
2014-NC42 | Royse Switch (2483-2460) 345/138-kV autotransformer CMP | Oncor | 2019 |  |  |  | Under Study
2014-NC43 | Renner TPL 345/138-kV autotransformer upgrade and substation reconfiguration | Oncor | 2015 | 12/15/2015; 5/15/2016 | Planned; Planned | 4347; 13TPIT0113
2014-NC44 | Ben Davis-Murphy 138-kV terminal equipment upgrade | TMPA/Oncor | 2019 | 2019-06-01 | Planned | 4438
2014-NC45 | Cedar Hill Switch (2422)-Dalworth (2474) 138-kV line upgrade | Oncor | 2017 | 2020-05-15 | Planned | 14TPIT0057
2014-NC46 | Roanoke Switch (1848, 1850) 138-kV series reactor additions | Oncor | 2019 |  |  |  | Under Study
2014-NC47 | Series reactors on Liggett 345/138-kV autotransformers #1 and #2 | Oncor | 2017 |  |  |  | Under Study
2014-NC48 | Trinidad (3127)-Montfort Switch (3454) 138-kV line upgrade | Oncor | 2015 |  |  |  | Under Study
2014-E1 | Stryker Creek (3110)-Nacogdoches (3303) 138-kV line upgrade | Oncor | 2015 | 5/15/2016; 5/15/2017 | Planned; Planned | 16TPIT0065; 4257
2014-E2 | Jewett 345/138-kV additional autotransformer | Oncor | 2015 |  |  |  | Under Study
2014-E3 | Tyler Grande ( 3143)-Tyler GE ( 3213) 138-kV line upgrade (a), Elkton ( 3106)-Tyler West ( 3139) 138-kV line upgrade (b), Tyler West ( 3139)-Tyler Northwest ( 3141) 138-kV line upgrade (c), Troup ( 3147)-Walnut Grove ( 3156) 138-kV line upgrade (d), and Elkton ( 3106)-Athens ( 3238) 138-kV line upgrade (e) | Oncor | 2015 | 5/15/2015; 12/15/2015; 5/15/2016; 5/15/2016; 5/15/2017 | Planned; Planned; Planned; Planned; Planned | 14TPIT0015; 08TPIT0153; 06TPIT0047; 17TPIT0029; 4263
2014-C1 | Dickinson (38850)-League City (38920) 138-kV line upgrade | TNMP | 2019
2014-C2 | Dickinson (38850)-Freeway Park (38820) 138-kV line terminal equipment upgrade | TNMP | 2019
2014-C3 | South Shore (38890)-Hidden Lakes (38900) 138-kV line upgrade | TNMP | 2019
2014-C4 | Loop Roans Prairie-King 345-kV line into Rothwood (46290) | Centerpoint Energy | 2017 | 2015-05-31 | Planned | 3886
2014-C5 | Reconfigure Hitchcock (42800)-West Galveston (43400) and loop Hitchcock (42800)-West Galveston (43401) into La Marque (42861) | Centerpoint Energy | 2019 | 2016-05-31 | Planned | 4187
2014-C6 | Power factor improvement at Southwyck | Centerpoint Energy | 2019 |  |  |  | There is no topology change needed for this project as the power factor improvement is handled on the distribution side and the same is reflected in the current set of cases with Southwyck load at unity PF on distribution side.
2014-C7 | Switched shunt addition at Aldine (45640) | Centerpoint Energy | 2019 |  |  |  | The shunt addition is needed by summer of 2020; TP is still evaluating alternatives however, this project can be available (tentatively) by May 2019.
2014-C8 | Hasting (39010)-Friendswood (38980) 138-kV line terminal equipment upgrade | TNMP | 2015
2014-C9 | Danevang (5548)-Clemville (5549) 69-kV line upgrade | STEC | 2019
2014-C10 | Jordan 345/138-kV additional autotransformer | Centerpoint Energy | 2015 | 2016-12-31 | Planned | 3825
2014-C11 | Rothwood 345/138-kV additional autotransformer | Centerpoint Energy | 2015 | 2016-05-30 | Planned | 4421
2014-C12 | Clodine (44140)-Barker (44052) 138-kV line upgrade (a), Britmore (44120)-Sauer (44621, 44622) 138-kV double-circuit line upgrade (b), Bellaire (47010)-San Felipe (47382) 138-kV line upgrade (c), and San Felipe (47382)-Eureka (45750) 138-kV line upgrade (d) | Centerpoint Energy | 2015 |  |  |  | A mitigation plan has been developed to address the needs in the near term. TP is still evaluating alternatives however, this project can be available (tentatively) by May 2017.
2014-C13 | Replace PH Robinson 345/138-kV autotransformer A2, move PH Robinson autotransformer A2 to Meadow, and upgrade Friendswood (38980)-Seminole (38990) 138-kV line | Centerpoint Energy/TNMP | 2015 | 2016-12-31 | Planned | 4168
2014-FW1 | (a) Arena Tap (1153) -Andrew County South (1157) 138-kV line upgrade (b) Arena Tap (1153)-Andrews Tap (1155) 138-kV line upgrade | Oncor | 2017 | 2017-05-15 | Planned | 4267
2014-FW2 | Big Lake (6535)-Stiles (79614) new 138kV line Pemkiff tie project (79612, 79614, 1210) | Oncor/Sharyland | 2019 | 2015-05-15 | Planned | 4296
2014-FW3 | Crane Tap 2 (6609)-Crane Gulf Tap (6603)-Crane Gulf 1 (6608) 69-kV line Upgrades | American Electric Power | 2019
2014-FW4 | Flat Top TNP (38070)-Barilla Tap (38092) 138kV tie 1. Tap existing Barilla (6655)-Musquiz (6673) 138-kV line 2. New 138-kV line from the tap to Flat Top (90008) 3. New 138/69-kV transformer at Flat Top TNP (38070) 4. Upgrade Barilla Draw Tap TNP (38060)-Flat Top TNP (38070) | American Electric Power/TNMP | 2015
2014-FW5 | Holt (1142) -Emma Tap (1262) 69-kV line upgrade | Oncor | 2017 | 2017-05-15 | Planned | 14TPIT0008
2014-FW6 | McDonald (1333)-Spraberry (1330) 138-kV line 1. Upgrade McDonald Road 138-kV switching station (1333) 2. Install McDonald Road Sw Station (1333)-Garden City East (1218) 138-kV line on new double circuit structures and operate both 69-kV and 138-kV 3. Upgrade Spraberry 138-kV Switching Station (1330) 4. Install Spraberry Switching Station (1330)-Garden City East (1218) 138-kV line on new double circuit structures and operate both 69-kV and 138-kV | Oncor | 2015 | 5/15/2015; 5/15/2015; 12/15/2015; 12/15/2015 | Planned; Planned; Planned; Planned | 3924; 3932; 3925; 3934
2014-FW7 | (a) Close NO Shell Powell Tap (6540) -Powell Field (6545) Open NC Powell Field (6545) -Powell Field Tap (6548) Open Close NO Illinois (6565)-Pandale (6567) (b) Upgrade Shell Powell Tap (6540)-Powell Field (6545) | American Electric Power | 2015 | 2018-05-31 | Planned | 3848
2014-FW8 | Wink (1075)-Odessa Basin SS (1254) 69-kV line upgrade | Oncor | 2015 | 2016-12-15 | Planned | 4245
2014-FW9 | Midland East (1023)-Stanton East (1326) 138-kV line upgrade | Oncor | 2015 | 2014-12-15 | Planned | 14TPIT0052
2014-FW10 | (a) Mason (1094)-Sand Bend POI (1083) 138-kV line upgrade (b) Mason (1094)-Culberson (1097) 138-kV line upgrade 138-kV line upgrade | Oncor | 2019 | 5/15/2015; 5/15/2016 | Planned; Planned | 16TPIT0033; 4367
2014-FW11 | Odessa 345/138-kV autotransformers upgrade (1027) | Oncor | 2015 |  |  |  | Under Study
2014-FW12 | Texaco Tap (1179)-Midconw (1183) 138-kV line upgrade | Oncor | 2020 |  |  |  | Under Study
2014-FW13 | Add a 30 Mvar capacitor bank at Mason (1094) | Oncor | 2017 |  |  |  | Under Study
2014-FW14 | Add a 10 Mvar capacitor bank at Hargrove (6648) | AEP/TNC | 2019
2014-FW15 | Add a 12 Mvar capacitor bank at Exxon Means (1166) | Oncor | 2017 |  |  |  | Under Study
2014-FW16 | Add a 30 Mvar capacitor bank at Big Lake (6535) | AEP/TNC | 2017
2014-W1 | Bluff Creek (1309) -China Grove (1318) terminal equipment upgrade | Oncor | 2019 | 2015-05-15 | Planned | 4101
2014-W2 | Add a second 345/138-kV autotransformer at Twin Buttes (76009) | American Electric Power/LCRA TSC | 2015 | 2016-11-22 | Planned | 3965
2014-W3 | Campwood (8633)-Montell (8230)-Uvalde (8231) 69-kV line upgrade | American Electric Power | 2015 | 2018-05-31 | Planned | 4488
2014-W4 | Ferguson (7126)-Sandy Creek (7127)-Pittsburg (7120) 138-kV line upgrade | LCRA TSC | 2017 | 2015-05-11 | Planned | 3968
2014-W5 | Dermott (11306)-Ennis Creek (1410) 138-kV line upgrade | Oncor | 2015 | 2015-05-15 | Planned | 3875
2014-W6 | Morgan Creek (1032)-Cosden (1333) 138-kV line upgrade | Oncor | 2017 | 2015-12-15 | Planned | 3874
2014-W8 | Add 40 Mvar inductor at Horse Hollow (170245) | NEXTera Energy Resources | 2020
2014-SC1 | CPS/LCRA TSC tie project with new Bracken substation and additional Zorn to Marion line | CPS/LCRA TSC | 2017 | 2019-05-31 | Planned | 4473
2014-SC2 | Hutto Switch (3666)-Round Rock Northeast (3670)-Round Rock (3668) 138-kV line upgrade to 717 MVA | Oncor | 2019 | 2015-01-10 | Planned | 4238
2014-SC3 | Tap the 138kV LCRA TSC line between Shiner and Moulton and add a 138/69kV auto at the GVEC Moulton substation | LCRA TSC/GVEC | 2019 | 2019-07-01 | Planned Not in Case | 4606
2014-SC4 | Zorn (7180)-York (7227)-Seguin (7228) 138-kV line upgrade | LCRA TSC | 2019 | 2016-05-05 | Planned | 3966
2014-SC5 | Lockhart auto and Lockhart (7216)-Seawillow (7559)-Luling (7224) 138kV line upgrade | LCRA TSC | 2015 | 2017-05-31 | Planned | 3963
2014-SC6 | Marion (7178)-Cibolo (7608) second circuit addition | GVEC | 2017 | 2017-05-31 | Planned | 17TPIT0008
2014-SC7 | CPS reconfiguration of 345-kV lines between Skyline, Marion, Elm Creek and Hill Country | CPS | 2017 | 2017-06-01 | Planned | 4081
2014-SC8 | Merida (5310)-Westside (5490) 138-kV line upgrade | CPS | 2019 | 2019-06-01 | Planned | 4083
2014-SC9 | Decker Power Plant (9188)-McNeil (9076) 138-kV line upgrade | AEN | 2020 | 2015-02-15 | Planned | 3905
2014-SC10 | Wirtz (7104)-Flat Rock (7111)-Paleface (7477) 138-kV line upgrade | LCRA TSC | 2020 | 2019-05-31 | Planned | 4465
2014-SC11 | Clear Springs 345/138-kV auto addition | LCRA TSC | 2017 | 2016-05-31 | Planned | 4462
2014-SC12 | Close Kendall bus tie between 7150 and 7152 | LCRA TSC | 2017 | 2016-05-31 | Planned | 4463
2014-SC13 | Hutto Switch (3666)-Pflugerville (3665) 138-kV line upgrade | Oncor | 2017 |  |  |  | Under Study
2014-SC14 | Medical Center (5300)-Hamwolf (5187) 138-kV line upgrade | CPS | 2019
2014-SC15 | Loop the Gilleland (7340) to Clearsprings (7050) 345-kV line into Dunlap (9044) and upgrade the double circuit from Sandow Switch (13429) to Austrop (7040) | LCRA TSC/AEN/Oncor | 2020 | 5/31/2020; 5/31/2020 | Planned; Planned | 4477; 4479
2014-S1 | George West 138/69-kV Auto (5688-5686) upgrade to at least 102 MVA | STEC | 2015 | 2018-06-01 | Planned | 3817
2014-S2 | Calallen (5626)-Robstown (5634) 69-kV line upgrade to at least 109 MVA | STEC | 2019 | 2018-06-01 | Planned | 3818
2014-S3 | San Miguel Tap (5693)-N. Calliham (5698) 69-kV line upgrade to at least 109 MVA | STEC | 2017 | 2017-06-01 | Planned | 3819
2014-S4 | Pearsall (5895)-Paloduro (5866) 138-kV line upgrade to at least 326 MVA | STEC | 2019 | 2018-06-01 | Planned | 3821
2014-S5 | Fowlerton 345/138-kV auto addition | STEC | 2017 | 2017-02-01 | Planned | 3894
2014-S6 | Lobo 345/138-kV auto addition and close San Diego tie between American Electric Power and STEC (8890-5654) | American Electric Power/STEC | 2015 | 2016-06-30 | Planned | 3903
2014-S7 | Bevo (5871)-Carrizo (8244) 69-kV line addition | American Electric Power/STEC | 2015
2014-S8 | Pleasanton 138/69-kV transformer upgrade to at least 102 MVA | American Electric Power | 2015 | 2016-06-30 | Planned | 3898
2014-S9 | Cross Valley Project tap at South McAllen | American Electric Power | 2017
2014-S10 | Escondido (8260) to West Batesville (8236), build 138-kV line | American Electric Power | 2015 | 2019-03-31 | Planned Not in Case | 10TPIT0028
2014-S11 | Stewart 138/69-kV transformer upgrade, Stewart (8951)-Rio Rico (8751) and La Palma (8310)-Rangerville (8748) 69-kV line upgrades | American Electric Power | 2017 | 2017-05-31 | Planned | 3900
2014-S12 | Stewart Road (8951) to Weslaco Unit (8348) 138kV line upgrade to at least 233 MVA. | American Electric Power | 2017 | 2016-12-31 | Planned | 3998
2014-S13 | Escondido (8260) to Eagle Pass (8270) 138kV line upgrade | American Electric Power | 2015 | 2017-05-31 | Planned | 4489
2014-S14 | Koch Up River 138/69-kV transformer upgrade | American Electric Power | 2019 | 2017-05-31 | Planned | 4487
2014-S15 | Harlingen Switch (8327)-Oleander (80022) 138-kV line upgrade | American Electric Power | 2017
2014-S16 | Rio Hondo (8319)-East Rio Hondo (5764) 138-kV line upgrade | STEC | 2019
2014-S17 | San Miguel Switchyard 345/138-kV auto addition | STEC | 2017

## TransmissionOwnerProjContac
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Bob Healey; Veronica Billings | bhealey@aep.com; vbillings@aep.com | Bob Healey: 918 599 2249; Veronica Billings: 918 599 2945 | Glen Reed; David Kidd; Brad Myers; Mabel See; Mike Forcum; Doug Lee; Daniel Lyons; Bob Lager; Mina Turner; Lisa Kelso; Carole Myser | gareed@aep.com; dekidd@aep.com; blmyers@aep.com; msee@aep.com; mlforcum@aep.com; dnlyons@aep.com; dlee@aep.com; rjlager@aep.com; myturner@aep.com; lokelso@aep.com; camyser@aep.com | David Kidd: 918 599 2637 Glen Reed: 918 599 2664 Brad Myers: 918 599 2690
AUSTIN ENERGY | Primary & Secondary | Reza Ebrahimian | Reza.Ebrahimian@austinenergy.com; | Reza: (512) 322-6740 | Armke, James; Hunt, Dandy; Ron Krautz; Brion Ryan | James.Armke@austinenergy.com; dandy.hunt@austinenergy.com; ron.krautz@austinenergy.com; Ryan, Brion <Brion.Ryan@austinenergy.com> | James:512 322 6705 Biju:512 322 6381 Reza:512 322 6740 Dandy:512 322 6748 Ron:512 322 6835 Brion: 512-322-6879
Bandera Electric | Primary | David Baker | d.baker@banderaelectric.com | David: 830-796-6084
BPUB | Primary | Ramon Sanz | rsanz@brownsville-pub.com; | Ramon: 956 983 6203 | James McCann | jmccann@brownsville-pub.com; | James: 956 983 6204
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Dwight Beckman | dbeckman@brazoselectric.com | Dwight: 254 750 6373 | David Albers | dalbers@brazoselectric.com | David: 254 750 6358
BTU | Primary & Secondary | James Tanneberger | jtanneberger@btutilities.com | James: 979 821 5763 | Shawndra Green | sgreen@btutilities.com | Shawndra: 979 821 5744
CNP | Primary & Secondary | Wayne Kemper | wayne.kemper@centerpointenergy.com | Wayne: 713 207 2192 | David Mercado; Yingying Huang; Cody Mann | david.mercado@centerpointenergy.com; yingying.huang@centerpointenergy.com; cody.mann@centerpointenergy.com | David Mercado: 713-207-2125 Yingying Huang: 713-207-2831 Cody Mann: 713-207-3149
COCS | Primary | Tony Michalsky | tmichalsky@cstx.gov; | Tony: 979 764 3438 | Timothy Crabb; Stacy Engelmann | tcrabb@cstx.gov; sengelmann@cstx.gov; | Timothy Crabb 979 764 3439 Stacy Engelmann 979 764 3681
CPS | Primary & Secondary | Basileo Rocha, Sunil Dhakal | bdrocha@cpsenergy.com; SDhakal@cpsenergy.com | Basileo: 210 353 4933 Sunil: 210 353 2008 | Kenneth Bowen Trieu Vo | kbowen@cpsenergy.com; tvo@cpsenergy.com; | Kenneth: 210 353 4142 Trieu: 210 353 2127
CTT (Cross Texas Transmission) | Primary & Secondary | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310 | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310
DENTON | Primary & Secondary | Chuck Sears | Chuck.Sears@cityofdenton.com; | Chuck: 940 349 7111 | Brent Heath | brent.heath@cityofdenton.com; | Brent: 940 349 7180
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@gpltexas.org | Danh: 972 205 3826 | Grubbs, David; Juan Santos | Dgrubbs@gpltexas.org; Jsantos@gpltexas.org | David: 972 205 2664 Juan: 972-205-2603
Golden Spread EC | Primary & Secondary | Chris Koenig | ckoenig@gsec.coop | Chris: 806 349 5201 | Shane McMinn, Mark Reinart | smcminn@gsec.coop; mreinart@gsec.coop | Shane: 806 379 7766 Mark: 806 349 6562
LCRA TSC; PEC; SBEC; GVEC; City of Georgetown; BBEC,CTEC, NBU | Primary & Secondary | Charles DeWitt | Charles.dewitt@lcra.org | Charlie: 512-578-4199 | Sergio Garza, Cris Urena, Ken Chui | sergio.garza@lcra.org; cris.urena@lcra.org; ken.chui@lcra.org | Sergio: 512 578 4149 Cris: 512 578 4525 Ken: 512 578 4510
Lone Star | Primary & Secondary | Don Le | don.le@lonestar-transmission.com | Don - 512-236-3144 | Matt Gomes | Matthew.Gomes@LONESTAR-TRANSMISSION.COM | Matt - 512-236-3133
Oncor | Primary & Secondary | Mike Juricek | Michael.Juricek@oncor.com; | Mike: 214 743 6671 | Paul Bell | paul.bell@oncor.com | Paul: 214-743-6676
Sharyland Utilities | Primary & Secondary | Mark Caskey | mcaskey@sharyland.com | Mark: 214 978 8243 | Michael Glass, Dwight Yarbrough, Miguel Alvarado | mglass@sharyland.com; dyarbrough@sharyland.com; malvarado@sharyland.com | Michael: (956) 687-5600, Dwight: (432) 684-0321, Miguel: (214) 855-6103
STEC | Primary & Secondary | Doug Evans | devans@stec.org | Doug: 361 485 6459 | Paul Person Loretta Gallaga | pperson@stec.org; lgallaga@stec.org; | Paul: 361 485 6151 Loretta: 956 377 7120
TMPA | Primary & Secondary | Ahmad Saboor | asaboor@texasmpa.org | Ahmad: 936 873 1104 | Frank Owens | fowens@texasmpa.org; | Frank: 936 873 1120
TNMP | Primary & Secondary | Robert Lona | Robert.Lona@tnmp.com | Robert: 281-581-4732 | Anthony, Hudson Ballay, Dustin Cloninger, Ross | Anthony.Hudson@tnmp.com; Dustin.Ballay@tnmp.com; Ross.Cloninger@tnmp.com; | Anthony: 281 581 4712 Dustin:281 581 4730 Ross:281 581 4733
Wind Energy Texas Transmission (WETT) | Primary | Julius Horvath | julius.horvath@windenergyoftexas.com | Julius: 512 436 9585; cell: 512 496 9186 | Christina Minchew | christina.Minchew@windenergyoftexas.com | Christina: 512-436-9469