## ImprovementCostSummary09012011
PRIVILEGED AND CONFIDENTIAL, DO NOT release outside of ERCOT Staff or Transmission Providers organization. Contains critical cost information that can affect bids for projects.
| Project Cost | [5 empty] | Circuit Miles |  |  |  |  | XFMR MVA
| Project Cost | [5 empty] | XFMR MVA
| 345 | 138 | 69 | total |  |  | 345 | 138 | 69 | total
2009 | 172284112 | 452787046.68 | 98206585 | 723277743.68 |  | 2009 | 2467 | 1462 | 0 | 3929
2010 | 527016732 | 393661394.52 | 79708160 | 1000386286.52 |  | 2010 | 5957 | 758 | 0 | 6715 |  | For ROS and BOD reports
2011 | 541190049 | 334023463 | 224713388 | 1099926900 | 2823590930.2 | 2011 | 4622 | 983 | 0 | 5605 | 16249
2012 | 771281619 | 536640382 | 224618691 | 1532540692 |  | 2012 | 5972 | 249 | 75 | 6296 |  | ·All Projects (in engineering, routing, licensing and construction) (sum of F13, E16) |  |  |  | 9763938898
2013 | 5375978365 | 254970224 | 59710078 | 5690658667 |  | 2013 | 6650 | 353 | 0 | 7003
2014 | 235890630 | 246978968 | 46152736 | 529022334 |  | 2014 | 1200 | 187 | 0 | 1387 |  | ·Transmission Projects Energized in 2010 (E15) |  |  |  | 694815095
2015 | 259952933 | 104285063 | 34878886 | 399116882 |  | 2015 | 700 | 150 | 0 | 850
2016 | 372404000 | 66411591 | 34345531 | 473161122 |  | 2016 | 1800 | 0 | 0 | 1800
2017+ | 394546044 | 308960450 | 30820902 | 734327396 | 9358827093 | 2017+ | 4929 | 607 | 60 | 5596 | 22932
2011COM | 349204398 | 234843429 | 110767268 | 694815095 |  | 2011COM | 3422 | 451 | 0 | 3873
2011PLAN | 191985651 | 99180034 | 113946120 | 405111805 |  | 2011PLAN | 1200 | 532 | 0 | 1732
2009-2017+ | 8650544484 | 2698718582.2 | 833154957 | 12182418023.2 |  | 2009-2017+ | 34297 | 4749 | 135 | 39181
2009-2011 | 1240490893 | 1180471904.2 | 402628133 | 2823590930.2 |  | 2009-2011 | 13046 | 3203 | 0 | 16249
2012-2017+ | 7410053591 | 1518246678 | 430526824 | 9358827093 |  | 2012-2017+ | 21251 | 1546 | 135 | 22932
| Circuit Miles New | [5 empty] | Circuit Miles Rebuilt, Reconductored or Upgraded |  |  |  |  | TOTAL
| 345 | 138 | 69 | total |  |  | 345 | 138 | 69 | total |  | 345 | 138 | 69 | total
2009 | 107.1 | 52.8 | 1 | 160.9 |  | 2009 | 0.5 | 350.15 | 119.3 | 469.95 |  | 107.6 | 402.95 | 120.3 | 630.85
2010 | 380.5 | 108.1 | 27.5 | 516.1 |  | 2010 | 115.5 | 284.92 | 52.55 | 452.97 |  | 496 | 393.02 | 80.05 | 969.07
2011 | 624.4 | 61.2 | 0 | 686.1 | 1363.1 | 2011 | 12.9 | 282.1 | 171.9 | 608.4 | 1531.32 | 637.3 | 343.3 | 171.9 | 1294.5
2012 | 551.1 | 144.7 | 63.1 | 758.9 |  | 2012 | 16.4 | 417.9 | 179.4 | 613.7 |  | 567.5 | 562.6 | 242.5 | 1372.6
2013 | 3728.7 | 69.1 | 0 | 3797.8 |  | 2013 | 165.2 | 216.5 | 54.5 | 436.2 |  | 3893.9 | 285.6 | 54.5 | 4234
2014 | 13.5 | 31.6 | 0 | 45.1 |  | 2014 | 122.9 | 212.6 | 50.8 | 386.3 |  | 136.4 | 244.2 | 50.8 | 431.4
2015 | 144.5 | 38 | 0 | 182.5 |  | 2015 | 37.2 | 56.8 | 51.5 | 145.5 |  | 181.7 | 94.8 | 51.5 | 328
2016 | 204 | 48 | 7.7 | 259.7 |  | 2016 | 0 | 11.2 | 13.9 | 25.1 |  | 204 | 59.2 | 21.6 | 284.8
2017+ | 172.9 | 96.4 | 11 | 280.3 | 5324.3 | 2017+ | 71.1 | 167.6 | 38.2 | 276.9 | 1883.7 | 244 | 264 | 49.2 | 557.2
2011COM | 297 | 56.4 | 0 | 353.4 |  | 2011COM | 12.9 | 229.7 | 171.9 | 414.5 |  | 309.9 | 286.1 | 171.9 | 767.9
2011PLAN | 327.4 | 4.8 | 0.5 | 332.7 |  | 2011PLAN | 0 | 52.4 | 141.5 | 193.9 |  | 327.4 | 57.2 | 142 | 526.6
2009-2017+ | 5926.7 | 649.9 | 110.3 | 6687.4 |  | 2009-2017+ | 541.7 | 1999.77 | 732.05 | 3415.02 |  | 6468.4 | 2649.67 | 842.35 | 10102.42
2009-2011 | 1112 | 222.1 | 28.5 | 1363.1 |  | 2009-2011 | 128.9 | 917.17 | 343.75 | 1531.32 |  | 1240.9 | 1139.27 | 372.25 | 2894.42
2012-2017+ | 4814.7 | 427.8 | 81.8 | 5324.3 |  | 2012-2017+ | 412.8 | 1082.6 | 388.3 | 1883.7 |  | 5227.5 | 1510.4 | 470.1 | 7208

## FutureTPIT09012011NoCost
SEPTEMBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS As Of 09/01/2011
Projects (New/Old) | Service Date Changes | ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional)
Old Project | No Change | 11TPIT0163 | Tres Palacious 69 kV Substation | Construct new 69 kV load serving substation in the line between N Clemville and Saltdome. |  |  |  | Under Construction |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-09-01 |  | 69 | 0 | 0 | 0 | 0 | MATAGORDA |  | Tier 4 |  |  |  | 5553 | Y | N
Old Project | Change in Service Date. Changed from 8/1/2011 to 9/1/2011 | 11TPIT0092 | Handley SES capacitors | Install 138 kV capacitors | Construction delays |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5159-WAC | 2011-09-01 |  | 138 | 0 | 0 | 0 | 110.4 | TARRANT |  | Tier 4 |  |  |  | 1951 | Y | N
Old Project | Change in Service Date. Changed from 8/12/2011 to 9/12/2011 | 09TPIT0176 | Bertram-Andice | Close the normally open Bertram (7520)-Andice(7521) 69 kV transmission line. | Material and contractor delays | Bertram | Andice | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-09-12 |  | 69 | 0 | 0 | 0 | 0 | BURNET | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | Change in Service Date. Changed from 8/5/2011 to 9/15/2011 | 11TPIT0136 | Bissett to Aspermont | Rebuild Bissett to Aspermont 69 kV line with 795 ACSR | construction delay due to high temps | Bissett | Aspermont | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10030 | 2011-09-15 |  | 69 | 0 | 21.35 | 0 | 0 | STONEWALL | STONEWALL | Tier 4 |  |  |  | 753, 755, 6156 | Y | N
Old Project | No Change | 11TPIT0143 | Comstock to Rough Canyon, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | Transmission Status Update | Comstock | Rough Canyon | Under Construction | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2439 | 2011-09-30 |  | 69 | 0 | 21.6 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 10TPIT0026 | Mueller 138kV substation | Establish new 138kV Mueller substation with a 30MVA transformer and two underground feeders. The substation will cut into existing Ckt 938 (Kingsbery to Wheless Lane). |  | Mueller Substation | Mueller Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_2793 3240_117_4793 3230_117_4229 | 2011-10-01 |  | 138 | 1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9342 | Y | N
Old Project | Change in Service Date. Changed from 8/1/2011 to 10/1/2011 | 10TPIT0022 | Ckt 918 Oak Hill to Brodie Lane Reconductor | Reconductor the last span of the Ckt 918 going into Oak Hill sub with bundled 795 ACSR Drake capable of 2000 Amperes | Delay | Oak Hill Substation | Brodie Lane Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P080 | 2011-10-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9169, 9247 | Y | N
Old Project | Change in Service Date. Changed from 12/1/2011 to 10/1/2011 | 11TPIT0168 | Elroy | Add Elroy station (7209) to LCRA TSC's Colton (7208) to Wolf Lane (7212) 138 kV transmission line. |  | Elroy | Colton/Wolf Lane | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-10-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 11TPIT0171 | Hutto Switch shunt reactors | Install shunt reactors on the tertiary of the 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R755-WAC | 2011-10-01 |  | 138 | 0 | 0 | 0 | -75 | WILLIAMSON |  | Tier 4 |  |  |  | 3666 | Y | N
Old Project | Change in Service Date. Changed from 10/14/2011 to 10/7/2011 | 11TPIT0131 | Hearne Auto | Replace 60 MVA, 138/69 kV auto with 100 MVA auto |  | Hearne |  | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10067 | 2011-10-07 |  | 138 | 0 | 0 | 100 | 0 | ROBERTSON |  | Tier 4 |  |  |  | 35, 36 | Y | N
Old Project | No Change | 10TPIT0078 | Granbury to Glen Rose Rebuild | Rebuild Granbury to Geln Rose with 959ACSS |  | Granbury | Glen Rose | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 07017 | 2011-10-10 |  | 69 | 0 | 14.2 | 0 | 0 | HOOD | SOMERVELL | Tier 4 |  |  |  | 315307 | Y | N
Old Project | Change in Service Date. Changed from 9/5/2011 to 10/30/2011 | 11TPIT0165 | Wirtz (7107) - Johnson City (7516) | Rebuild Johnson City 69kV bus to single bus, replacing switches (512 and 542) with breakers (22150 and 22160). Move T-313 from Wirtz breaker (1430) to Wirtz breaker (1690). Close loop Wirtz (1690)-Johnson City(22150)-Mountain Top (1990). | Construction Delays | Wirtz | Johnson City | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-10-30 |  | 69 | 0 | 0 | 0 | 0 | BURNET | Blanco | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | Change in Service Date. Changed from 7/1/2011 to 10/30/2011 | 11TPIT0156 | Bandera Sub 138kv switches | Upgrade 138kv switches and bus |  | Bandera Sub | Bandera Sub | Under Construction |  | Bandera Electric | David Baker 830-796-6084 | 182768 | 2011-10-30 |  | 138 | 0 | 0 | 0 | 0 | Bandera |  | Tier 4 | N/A | N/A | N/A |  | N | N |  | Necessary to utilize full rating of the 2-795 circuit
Old Project | Change in Service Date. Changed from 7/1/2011 to 10/30/2011 | 11TPIT0157 | Verde Creek Sub 138kv switches | Upgrade 138kv switches |  | Verde Creek Sub | Verde Creek Sub | Under Construction |  | Bandera Electric | David Baker 830-796-6084 | 182769 | 2011-10-30 |  | 138 | 0 | 0 | 0 | 0 | Kerr |  | Tier 4 | N/A | N/A | N/A |  | N | N |  | Necessary to utilize full rating of the 2-795 circuit
Old Project | No Change | 11TPIT0106 | Pelican 138 kV: Build 4 Breaker ring Bus | Pelican 138 kV Switching Station for ultimate interconnect of Papalote Creek and Cotton Windfarms |  |  |  | Under Construction | 486 - 0688 | AEP/ETT/TCC | Tommy Vannoy 918-599-2653 | 3361 | 2011-10-31 |  | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 11TPIT0153 | Colorado City 69 kV terminal equipment | Upgrade terminal equipment on line to Morgan Creek |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8026-WAC, R8026B-WAC, R8026C-WAC & R8026D-WAC | 2011-11-01 |  | 69 | 0 | 0 | 0 | 0 | MITCHELL | MITCHELL | Tier 4 |  |  |  | 1378, 1033 | Y | N
Old Project | No Change | 11TPIT0130 | Webberville Solar Project | A new 30MW solar plant operated at 138kV level and tapped into an existing Austrop to Decker Ckt 921. |  | Webberville Solar Plant | Webberville Tap | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P311 | 2011-11-01 |  | 138 | 0.91 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9030, 9185, 9289 | Y | N
Old Project | Change in Service Date. Changed from 1/1/2012 to 11/1/2011 | 12TPIT0032 | Fort Mason to Pitsburg | Rebuild and convert the capacity of the existing transmission line (approximately 31 miles) between the LCRA TSC Fort Mason (76390) and Pitsburg (7120) stations. The new transmission line will consist of 1x795 ACSR Drake conductor to provide a thermal rating of 220 MVA. |  | Fort Mason | Pitsburg | Under construction |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-11-01 |  | 138 | 0 | 31 | 0 | 0 | MASON | LLANO | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | Change in Service Date. Changed from 11/18/2011 to 11/17/2011 | 10TPIT0064 | Parkway(7611) - Schertz(7610) Transmission Line | Replace existing 795 "Drake" circuit with 680T19 ACCR composite conductor |  | Parkway | Schertz | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-11-17 |  | 138 | 2.8 | 0 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 |  |  |  | See Project Title | Y | N
Old Project | No Change | 11TPIT0138 | Deer Park Area Reconfigurations | Reconfigure Ckt. 84 SOUTH - WABURN and Ckt. 96 CONIAL - Morgan's Point to create new Ckt. 96 SOUTH - Morgan's Point and Ckt. 84 WABURN - CONIAL. |  |  |  | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-11-30 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 43250, 41670, 40370, 41100, 40442, 40443, 42241 | Y | N |  | No autotransformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | No Change | 08TPIT0133 | Rocksprings Station: Install 69 KV Ring Bus | Rocksprings : Install 5-69 KV Breaker Ring Bus and 3.6 MVAR Cap Bank |  | Rocksprings |  | Under Constuction | 377 - 0552 | AEP/ETT | Eric Scott 918-599-2653 | 3019 | 2011-12-01 |  | 69 | 0 | 0 | 0 | 3.6 | EDWARDS |  | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 11TPIT0154 | Montell: Construct 69 kV Substation Including Motor Operated Switches with Interrupters | Add new 69 kV Montell Substation for STEC distribution interconnection | Removed "From an To" info because this is a Station |  |  | Under Constuction | 498 - 0703 | AEP/TCC | Kenneth 'Rich' Haley 918-599-2653 | 3419 | 2011-12-01 |  | 69 | 0 | 0 | 0 | 0.0 | UVALDE |  | Tier 4 |  |  |  | 8230 | N | N
Old Project | No Change | 11TPIT0060 | Lamesa - Ackerly Vealmoor 69 kV line | Rebuild existing 69 kV line |  | Lamesa | Ackerly Vealmoor | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8005-WAC | 2011-12-01 |  | 69 | 0 | 21.5 | 0 | 0 | DAWSON | HOWARD | Tier 4 |  |  | 2009-07-21 | 1164, 1364, 1362, 1363, 1356 | Y | N | 2009-R3 | ERCOT BOD approved this project as part of the RMR exit strategy for Permian Basin generation. Ackerly Vealmoor - Sparenburg section was completed in 5/2011, and Sparenburg - Lamesa section will be completed in 12/2011.
Old Project | Change in Service Date. Changed from 9/1/2011 to 12/1/2011 | 11TPIT0089 | Cottonwood Road 69 kV Switch | Construct new switching station | Construction delays |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R588-WAC | 2011-12-01 |  | 69 | 0 | 0 | 0 | 0 | ARCHER |  | Tier 4 |  |  |  | 1605 | Y | N
Old Project | No Change | 10TPIT0024 | Stoney Ridge 138kV substation (original title is Linda Vista substation) | Establish new 138kV Stoney Ridge substation and install (2) 30MVA transformers. The substation will cut into Ckt 962 (Garfield to Onion Ck). |  | Stoney Ridge Substation | Stoney Ridge Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_2894 3230_117_4894 | 2011-12-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9237 | Y | N
Old Project | No Change | 11TPIT0158 | Mason Creek Sub 138kv breakers | Add 138kv breakers |  | Mason Creek Sub | Mason Creek Sub | Planned |  | Bandera Electric | David Baker 830-796-6084 | 201491 | 2011-12-01 |  | 138 | 0 | 0 | 0 | 0 | Bandera |  | Tier 4 | N/A | N/A | N/A |  | N | N |  | System reliability & Maintenance
Old Project | No Change | 11TPIT0155 | Pearsall Capacitor Bank | Install 60 MVAR Capacitor and a new 138 kV circuit breaker at the Pearsall Substation. Replace Existing Substation Equipment at Pearsall to remove MLSE on the Leon Creek to Pearsall and the Medina Base to Pearsall 138kV transmission lines. | [5 empty] | CPS | S: Juan Salinas | S-0605 | 2011-12-01 |  | 138 | 0 | 0 | 0 | 60 | BEXAR | BEXAR | Tier 4 |  |  |  | 5335 5260 5305 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 6/1/2011 to 12/1/2011 | 09TPIT0214 | Alberta Switch 138kV Substation | Build new 138kV Switching Station |  |  |  | Under Construction | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-12-01 |  | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759 | Y | N
Old Project | No Change | 10TPIT0090 | Copperas Cove - Killeen Clark Road Tap - Killeen Fort Hood West 138 kV line upgrade | Upgrade existing 138 kV line |  | Copperas Cove | Killeen Fort Hood West | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R717-WAC | 2011-12-01 |  | 138 | 0 | 5 | 0 | 0 | CORYELL | BELL | Tier 4 |  |  |  | 3630, 3620, 3629 | Y | N
Old Project | No Change | 11TPIT0169 | Graham 138 kV terminal equipment | Upgrade terminal equipment on 345/138 kV autotransformer |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R904A-E | 2011-12-01 |  | 138 | 0 | 0 | 382 | 0 | YOUNG |  | Tier 4 |  |  |  | 1601 | Y | N
Old Project | Change in Service Date. Changed from 3/1/2012 to 12/1/2011 | 12TPIT0117 | Temple Switch shunt reactors | Install shunt reactors 345/138 kV autotransformer tertiary | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R756-E | 2011-12-01 |  | 138 | 0 | 0 | 0 | -37.5 | BELL |  | Tier 4 |  |  |  | 3415 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2012 to 12/1/2011 | 12TPIT0119 | Forney - Hubbard 138 kV line | Replace terminal equipment | Change in construction schedule | Forney | Hubbard | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4040A | 2011-12-01 |  | 138 | 0 | 0 | 0 | 0 | KAUFMAN | DALLAS | Tier 4 |  |  |  | 2934, 2438, 2402 | Y | N
Old Project | No Change | 10TPIT0037 | Bell County East - TNP One 345 kV line and Bell County East Switching Station (Oncor Electric Delivery part of project) | Install 345 kV switching station and construct a double-circuit 345 kV line |  | Bell County East | TNP One | Under Construction | R704A, R705 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R494-WAC | 2011-12-01 |  | 345 | 82.6 | 0 | 0 | 0 | ROBERTSON | BELL | Tier 1 | 2006-11-30 |  | 2007-07-01 | 39950, 3687 | Y | N |  | Bell County East Switching Station was completed in 5/2011.
Old Project | No Change | 10TPIT0103 | Bowman Switch terminal equipment | Replace terminal equipment on line to Fisher Road. |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C032-WA | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422, 1425 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 10TPIT0104 | Bowman Switch terminal equipment | Replace terminal equipment on line to Graham. |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C070-WA | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422, 1430 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0061 | Bowman - Riley (Oklaunion) 345 kV line (Oncor Electric Delivery portion) | Construct double-circuit 345 kV line |  | Bowman | Riley | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C073-E | 2011-12-01 |  | 345 | 85.2 | 0 | 0 | 0 | WILBARGER | ARCHER | CREZ |  |  |  | 1422, 6101 | Y | N | 2007- E7e | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0062 | Sweetwater East - Central Bluff 345 kV line | Construct double-circuit 345 kV line |  | Sweetwater East | Central Bluff | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C058-E | 2011-12-01 |  | 345 | 71.6 | 0 | 0 | 0 | NOLAN | NOLAN | CREZ |  |  |  | 11420, 11406 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0063 | Central Bluff Switch | Construct 345 kV switching station with 345/138 kV autotransformer |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C074-E | 2011-12-01 |  | 345 | 0 | 0 | 1200 | -150 | NOLAN |  | CREZ |  |  |  | 11406 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0064 | Central Bluff - Bluff Creek 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Central Bluff | Bluff Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C075-E | 2011-12-01 |  | 345 | 19 | 0 | 0 | 0 | NOLAN | TAYLOR | CREZ |  |  |  | 11406, 60040 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0070 | Dermott Switch (Central B) - Scurry County South Switch (Central A) 345 kV line | Construct double-circuit 345 kV line |  | Dermott Switch | Scurry County South Switch | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1009-E | 2011-12-01 |  | 345 | 65.4 | 0 | 0 | 0 | SCURRY | SCURRY | CREZ |  |  |  | 11305, 11318 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0098 | Bowman Switch | Rebuild switching station |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C009-E | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER |  | CREZ |  |  |  | 1422 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0099 | Temple Switch circuit breaker | Install 345 kV circuit breaker on line to Salado Switch. |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R739-WAC | 2011-12-01 |  | 345 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 3414 | Y | N
Old Project | Change in Service Date. Changed from 10/7/2011 to 12/7/2011 | 12TPIT0089 | Knox to Knox | Rebuild Knox to Knox 69 kV line with 795 ACSR |  | Knox | Knox | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10032 | 2011-12-07 |  | 69 | 0 | 3.67 | 0 | 0 | HASKELL | KNOX | Tier 4 |  |  |  | 765, 6114 | Y | N
Old Project | No Change | 10TPIT0039 | East Bell County - TNP One 345 kV Line Project | Expansion of 345 kV Switchyard at TNP One associated with East Bell County TNP One 345 kV Line Project |  | TNP One | TNP One | Under Construction | 10TPIT0037 | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2011-12-11 |  | 345 | 0 | 0 | 0 | 0 | ROBERTSON | ROBERTSON | Tier 4 | 2006-11-30 | 2007-01-02 |  | 39950 | Y | N | See Oncor Electric Delivery Entry for this project, 10TPIT0037
Old Project | No Change | 11TPIT0115 | Reagor Springs to Purdon Rebuild | Rebuild existing Reagor Springs to Purdon 69 kV line to serve new load at Emmett. |  | Reagor Springs | Purdon | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10020 | 2011-12-14 |  | 69 | 0 | 28.55 | 0 | 0 | ELLIS | NAVARRO | Tier 4 |  |  |  | 204, 210, 193, 194, 198 | Y | N |  | Load-serving project, necessitated by a large load addition at Emmett.
Old Project | No Change | 09TPIT0060 | Buda-Turnersville | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Turnersville (7500) to the conductor's rating. |  | Buda | Turnersville | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-12-16 |  | 138 | 0 | 0 | 0 | 0 | HAYS | HAYS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 10TPIT0073 | Buda-Rutherford | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Rutherford (7509) to the conductor's rating. |  | Buda | Rutherford | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-12-16 |  | 138 | 0 | 0 | 0 | 0 | HAYS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 10TPIT0074 | Buttercup-Whitestone | Replace under-rated limiting line terminal equipment at Buttercup and Whitestone to increase Buttercup (7531)-Whitestone (7529) to the conductor's rating. | Moved schedule up to coincide with Buda projects | Buttercup | Whitestone | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-12-16 |  | 138 | 0 | 0 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 11TPIT0104 | Move Hearn Rd to the Lon Hill to Upriver 69 kV line | Lon Hill to Upriver 69 kV Hairpin into Hearn Road and Upgrade Lon Hill to Hearn Road section |  | Lon Hill & Upriver | Hearn Road | Under Construction | 399 - 0709 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3279 | 2011-12-30 |  | 69 | 0.5 | 0.5 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N
Old Project | No Change | 11TPIT0144 | Rough Canyon to Hamilton Road, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line |  | Rough Canyon | Hamilton Road | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2440 | 2011-12-31 |  | 69 | 0 | 12.4 | 0 | 0 | VALVERDE | VALVERDE | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0070 | Ballinger to Winters, Rebuild 69 kV line | Re-Build Portions of the Ballinger to Abilene South 69 kV line with 795 ACSR | Transmission Status Update | Ballinger | Winters | Under Construction | 499 - 0705 | AEP/ETT | Teresa Trotman 918-599-2653 | 2460 | 2011-12-31 |  | 69 | 0 | 16.7 | 0 | 0 | TAYLOR | TAYLOR | Tier 1 | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y | N
New Project | New Project | 11TPIT0175 | Rocksprings - PEC Rocksprings: Constrcut 69 kV line | Rocksprings : Install 5-69 KV Breaker Ring Bus and 3.6 MVAR Cap Bank | NEW | Rocksprings | PEC Rocksprings | Under Construction | 377-0552 | AEP/ETT | Eric Scott 918-599-2653 | 3203 | 2011-12-31 |  | 69 | 0 | 0 | 0 | 0 | EDWARDS | EDWARDS | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 11TPIT0103 | Remove Hearn Rd from Lon Hill to Sinton 69 kV Line | Lon Hill to Upriver 69 kV Hairpin into Hearn Road and Upgrade Lon Hill to Hearn Road section |  | Lon Hill | Sinton | Under Construction | 399 - 0709 | AEP/TCC | Michael Glueck 918-599-2653 | 3279 | 2011-12-31 |  | 69 | 0 | 0.25 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N
New Project | New Project | 11TPIT0174 | Nall to Briarcrest Upgrade | Upgrade 0.82 miles of conductor from 2/0 ACSR to 795 ACSR and replace transmission poles as needed. |  | Nall Lane Substation | Briarcrest Substation | planned |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2011-12-31 |  | 69 | 0 | 0.82 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 12TPIT0069 | Barney Davis to Alazan 138 kV line rebuild | Barney Davis to Nelson Sharpe 138 kV line rebuild 1st circuit on a double circuit capable structure |  | Barney Davis | Alazan | Under Construction | 400 - 0647 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3332 | 2011-12-31 |  | 138 | 0 | 12.24 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N
Old Project | No Change | 11TPIT0086 | Bruni 138kV Station: Install breaker | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm | Removed "From an To" info because this is a Station |  |  | Under Constuction | 398 - 0587 | AEP/TCC | Tommy Vannoy 918-599-2653 | 3354 | 2011-12-31 |  | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 10TPIT0122 | Formosa: Interconnect New Generation at Formosa Substation | Upgrade generator disturbance monitoring, metering, and communications at the Formosa 138 kV substation. Add generator monitoring, protection, and communications at the Formosa CFB Plant. | PM updated and removed "From an To" info because this is a Station |  |  | Planned | 437 - 0645 | AEP/TCC | Dave Goetz 918-599-2653 | 3333 | 2011-12-31 |  | 138 | 0 | 0 | 0 | 0 | CALHOUN | CALHOUN | Tier 4 |  |  |  |  | Y | N |  | Project schedule date delayed based on customer's input.
Old Project | No Change | 09TPIT0103 | Alamito Creek, add 2nd 138/69 kV auto | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a NaS Battery at Gonzales | Removed "From an To" info because this is a Station |  |  | Under Construction | 358 - 0532 | AEP/TNC | Jim Eriksen 918-599-2653 | 1178 | 2011-12-31 |  | 138 | 0 | 0 | 50 | 0 | PRESIDIO |  | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y | N
Old Project | No Change | 11TPIT0110a | Alberta Switch-Valverde | Rebuild 4.05 Miles of 138kV line from Alberta Switch to Valverde Substation to AEP Weslaco Switch | Project Speedup due to delay with Alberta Switch-Doedyns | Alberta Switch | Valverde | Planned | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-12-31 |  | 138 | 0 | 4.05 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8769-8354 | Y | N |  | Divided Project into two projects. Associated with Valverde to AEP Weslaco Switch
Old Project | Change in Service Date. Changed from 5/31/2012 to 12/31/2011 | 12TPIT0076 | Oklaunion, Expand 345 kV switch station for the addition of the new Oklaunion to Riley circuit #2 | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 | Schedule, Cost & Status Update and Removed "From an To" info because this is a Station |  |  | Under Construction | 501 - 0708 | AEP/ETT | Paul Hassink 918-599-2653 | 2452 | 2011-12-31 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 5/31/2012 to 12/31/2011 | 11TPIT0052 | Riley, Build a new Riley to Oklaunion 345 kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule, Cost & Status Update | Riley | Oklaunion | Under Construction | 467 - 0668 | AEP/ETT | Paul Hassink 918-599-2653 | 2351 | 2011-12-31 |  | 345 | 3.55 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 11TPTI0173 | Substation CIP Security Project | Install physical and cyber security measures at each of TMPA's critical substations |  | Gibbons Creek, Shelby, Interchange | Gibbons Creek, Shelby, Interchange | Planned |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T11004 | 2011-12-31 |  | 345 | 0 | 0 | 0 | 0 | Grimes, Hunt |  | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 8/1/2011 to 1/1/2012 | 09TPIT0031 | Circuit 972 (McNeil to Howard Lane) Reconductor | Reconductor the last span of the Ckt 972 (McNeil to Howard Lane) going into McNeil substation with bundled 795 ACSR Drake conductor. | Delay | McNeil Substation | Howard Lane Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P085 | 2012-01-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9217 | Y | N
Old Project | Change in Service Date. Changed from 12/1/2011 to 1/1/2012 | 11TPIT0164 | McNeil 138kV Bus Upgrade | Upgrade the pin cap and bus support insulators for fault duty requirements. A minor topology change will be made within the station. | Delay | McNeil Substation | McNeil Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P290 | 2012-01-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9076, 9077, 9079 | N | N
Old Project | No Change | 12TPIT0105 | Elroy 138kV Unit Transformer | Establish one 30MVA unit transformer at the LCRA owned 138kV Elroy substation |  | Elroy Substation | Elroy Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_2943 3230_117_4943 | 2012-01-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9198 | Y | N |  | Will add to the base case in this TPIT updates.
Old Project | No Change | 12TPIT0091 | Garvey Road 345 kV Switching Station | Construct new switching station |  |  |  | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R905-E | 2012-01-01 |  | 345 | 0 | 0 | 0 | 0 | ARCHER | ARCHER | Tier 4 |  |  |  | 1702 | Y | N
Old Project | Change in Service Date. Changed from 11/21/2011 to 1/13/2012 | 11TPIT0133 | Bowie to Montague Rebuild | Rebuild Bowie to Montague 69kV line with 959 ACSS |  | Bowie | Montague | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10015 | 2012-01-13 |  | 69 | 0 | 11 | 0 | 0 | MONTAGUE | MONTAGUE | Tier 4 |  |  |  | 621, 632, 633 | Y | N
Old Project | No Change | 09TPIT0054 | LA Heights - 138kV Breaker Installations | Install line breakers between LA Heights bus A & B. | Delayed due to Budget Constraints |  |  |  | T-0156 | CPS | PM: Bruce Raney | S-0308 | 2012-02-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5285 5286 | Y | No |  | This is a line terminal addition, there are no additional tranformer capacity or transmission circuit miles associated with this project
Old Project | No Change | 12TPIT0098 | Bruni relay upgrade | Additional relays will be installed to allow the autotransformer to be normally closed. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-02-01 |  | 138 | 0 | 0 | 0 | 0 | WEBB |  | Tier 4 |  |  |  | 5887, 5888 | Y | N
Old Project | No Change | 07TPIT0042 | 2nd Lewisville Auto | Install (2nd) 345/138 kV autotransformer at Lewisville station |  | Lewisville |  | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 02032 | 2012-02-17 |  | 345 | 0 | 0 | 700 | 0 | DENTON |  | Tier 3 |  |  |  | 646, 645 | Y | N | 2009-R17
Old Project | No Change | 10TPIT0045 | Mauermann Rd - New 138kV Substation | Loop new 138kV substation into the existing VH Braunig to Toyota line | Delayed due to resource allocation | VH Braunig | Toyota | Planned | T-0087 | CPS | PM: Hector Torres | S-0399 | 2012-02-22 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5297 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 5/23/2012 to 2/24/2012 | 10TPIT0012 | Barclay to Silver City Rebuild | Rebuild existing Barclay to Silver City 69kv line |  | Barclay | Silver City | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 05009 | 2012-02-24 |  | 69 | 0 | 17 | 0 | 0 | FALLS | MILAM | Tier 4 |  |  |  | 69,65 | Y | N
Old Project | No Change | 11TPIT0167 | Lyssy: Construct 138 kV Facilities | Construct and own 138 kV transmission through-path facilities at the STEC Lyssy substation. | PM updated. Added dollars. | Kenedy Switch Station | Pleasanton | Planned | 497 - 0702 | AEP/TCC/ STEC | Kenneth Haley 918-599-2653 | 3413 | 2012-02-25 |  | 138 | 0 | 0 | 0 | 0 | KARNES |  | Tier 1 |  |  |  | 8193 | Y | N
Old Project | No Change | 12TPIT0092 | OXY USA Collie Field 69kV Tap | This project will tap TNMP's Worsham to IH20 69kV line to serve the new Oxy Collie Filed station |  | Worhsam | IH20 | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | NTE07410 | 2012-02-28 |  | 69 | 3.077 | 0 | 0 | 0 | Ward | Reeves | Tier 4 |  |  |  | 38020, 38040, 38041, 38042 | Y | N
Old Project | No Change | 10TPIT0088 | Ft. Lancaster to Illinois #4, Convert 69 KV to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line |  | Ft. Lancaster | Illinois #4 | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2363 | 2012-02-28 |  | 138 | 0 | 17.21 | 0 | 0 | PECOS | CROCKETT | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 10TPIT0089 | Illinois #4 to Hamilton Rd., Convert 69 kV to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line |  | Illinois #4 | Hamilton Road | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2364 | 2012-02-28 |  | 138 | 0 | 97.63 | 0 | 0 | CROCKETT | VALVERDE | CREZ Modified |  |  |  |  | Y | Y
Old Project | No Change | 12TPIT0034 | Illinois #4, Build new three breaker ring bus & add 138/69 kV auto | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | Removed "From an To" info because this is a Station |  |  | Under Construction | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2365 | 2012-02-28 |  | 138 | 0 | 0 | 37 | 0 | CROCKETT |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0064 | Rough Canyon, Convert station to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | Removed "From an To" info because this is a Station |  |  | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2433 | 2012-02-28 |  | 138 | 0 | 0 | 0 | 0 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0065 | Comstock, Convert station to 138 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | Removed "From an To" info because this is a Station |  |  | Planned | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2401 | 2012-02-28 |  | 138 | 0 | 0 | 0 | 0 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0086 | Hamilton Road, expand station | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | Removed "From an To" info because this is a Station |  |  | Under Construction | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2368 | 2012-02-28 |  | 138 | 0 | 0 | 0 | 0 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 11TPIT0041 | Gila 138kV: Construct new 138 kV, 6 breaker Ring Bus | Expand Nueces Bay 138 kV system for interconnection of 700 MW of new generation |  |  |  | Planned | 399 - 0650 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3242 | 2012-02-28 |  | 138 | 0 | 0 | 0 | 57.6 | NUECES |  | Tier 1 | 2009-03-16 | 2009-10-09 | 2009-12-01 |  | Y | N
Old Project | No Change | 08TPIT0092 | North Victoria to Victoria: Reconductor 69 kV Line | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | North Victoria | Victoria Power Plant | Planned | 389 - 0566 | AEP/TCC | Dave Goetz 918-599-2653 | 15 | 2012-03-01 |  | 69 | 0 | 3.1 | 0 | 0 | VICTORIA | VICTORIA | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 07TPIT0251 | Victoria Power Plant: Install 1-28.8 MVAR 69 kV Cap Bank | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | Victoria Power Plant |  | Planned | 389 - 0667 | AEP/TCC | Dave Goetz 918-599-2653 | 2243 | 2012-03-01 |  | 69 | 0 | 0 | 0 | 28.8 | VICTORIA |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0063 | Rebuild Heights-Lamarque 69kV line | This project will rebuild the 69 kV path from Heights to LaMarque. This includes lines 69-H1, 69-H2, and 69-J. Total length of line is approximately 2.8 miles. This project also will add to the system hardening efforts taken after Hurricane Ike in September of 2008. |  | Heights | LaMarque | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07610 | 2012-03-01 |  | 69 | 0 | 2.8 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38770, 39280, 39310, 39340 | N | N
Old Project | No Change | 12TPIT0107 | AMD to Pedernales New Circuit | Combine Circuit 1014 (Burleson to Pedernales) and Circuit 1017 (AMD to Burleson) into a single 138kV circuit bypassing Burleson substation. |  | AMD Substation | Pedernales Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | NEW | 2012-03-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9151, 9118 | Y | N |  | Will add to the base case in this TPIT updates.
Old Project | Change in Service Date. Changed from 2/28/2012 to 3/1/2012 | 11TPIT0129 | Pilot Grove - New Substation | Construct a new 138-26.18KV, 40 MVA x two, redundant backup substation |  | Pilot Grove | Sweet Home/Yoakum | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-03-01 |  | 138 | 0 | 0 | 0 | 0 | LAVACA |  | Tier 4 |  |  |  | See Project Title | Y | N
Old Project | No Change | 12TPIT0122 | Killeen Switch Shunt Reactors | Install shunt reactors on the tertiary of the 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R757-E | 2012-03-01 |  | 138 | 0 | 0 | 0 | -75.0 | BELL |  | Tier 4 |  |  |  | 3423 | Y | N
Old Project | No Change | 10TPIT0048 | Koppe Bridge Substation | Install (4) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  | Koppe Bridge | Koppe Bridge | under construction | 10TPIT0049 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2012-03-28 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32860 | Y | N
Old Project | No Change | 11TPIT0111 | Thompson Creek to Koppe Bridge Transmission Line | Build 17 miles of 1033ACSR transmission line operated at 138 kV; jump over the existing Atkins-Snook transmission line, bypass Snook substation and continue to Koppe Bridge substation. Eventually, the line will be looped into Snook substation and the 69 kV line form Atkins to Snook will be removed. | We have decided to bypass Snook substation for now. Priority has been given to heating up Koppe Bridge substation. | Thompson Creek | Koppe Bridge | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2012-03-28 |  | 138 | 17 | 0 | 0 | 0 | BRAZOS | BURLESON | Tier 4 |  |  |  | 32863 32860 | Y | N
Old Project | Change in Service Date. Changed from 11/30/2011 to 3/31/2012 | 11TPIT0072a | Garrott - Midtown - Polk Ckt. 90 | Upgrade 138 kV underground Ckt. 90 Garrott to Midtown by building additional underground cable parallel to existing cable. | Delay in project schedule | Garrott | Midtown | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-03-31 |  | 138 | 0 | 1.47 | 0 | 0 | HARRIS | HARRIS | Tier 3 | 2009-07-01 | 2009-07-01 | N/A | 47660, 47705 | Y | N |  | No transformer capacity to be added.
Old Project | Change in Service Date. Changed from 11/30/2011 to 3/31/2012 | 11TPIT0072b | Garrott - Midtown - Polk Ckt. 90 | Upgrade 138 kV underground Ckt. 90 Midtown to Polk by building additional underground cable parallel to existing cable. | Delay in project schedule | Midtown | Polk | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-03-31 |  | 138 | 0 | 1.04 | 0 | 0 | HARRIS | HARRIS | Tier 3 | 2009-07-01 | 2009-07-01 | N/A | 47705, 47730 | Y | N | See project 11TPIT0072a for total project cost estimate | No transformer capacity to be added.
Old Project | Change in Service Date. Changed from 5/1/2012 to 4/1/2012 | 08TPIT0034 | McNeil to Summit Reconductor | The proposal of adding the 2nd ckt from McNeil to Summit in not feasible due to right of way issues. New proposal calls for the upgrading of the original circuit to 3000Amp. | Speedup | McNeil Substation | Summit Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P351 PLAN_117_P372 PLAN_117_P373 | 2012-04-01 |  | 138 | 2 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9279 | Y | N
Old Project | No Change | 11TPIT0042 | Gila to Highway 9 138kV, Re-connect existing Highway 9 to Nueces Bay into Gila, | Expand Nueces Bay 138 kV system for interconnection of 700 MW of new generation |  | Highway 9 | Gila | Planned | 399 - 0649 | AEP/TCC | Michael Glueck 918-599-2653 | 3255 | 2012-04-12 |  | 138 | 0 | 3.29 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-17 | 2009-10-09 | 2009-12-01 |  | Y | N
Old Project | Change in Service Date. Changed from 12/3/2012 to 4/13/2012 | 08TPIT0097 | Rhome to Roanoke Rebuild | Rebuild existing Rhome to Roanoke |  | Rhome | Roanoke | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 06062 | 2012-04-13 |  | 138 | 0 | 16.6 | 0 | 0 | WISE | DENTON | Tier 4 |  |  |  | 602-640 640-1866-1852 | Y | N |  | 602-640 completed 4/13/2012 1852-1866 completed 4/9/2012
Old Project | No Change | 09TPIT0132 | Bonnie Brae Substation Constrcution | Construct new 50MVA, 69kV to 13.2kV substation adjacent to DME's 69kV Hickory to North Lakes transmission line 1/4 mile south of US 380 | On schedule |  |  | Under Construction | 07TPIT0097 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602099 | 2012-04-28 |  | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 905 | Y | N
New Project | New Project | 12TPIT0137 | New Barksdale: Construct new 69 kV Substation including box bay structure interconnection | Add new 69 kV New Barksdale Substation for PEC distribution interconnection | NEW |  |  | Under Construction | 469 - 0671 | AEP/ETT | Eric Scott 918-599-2653 | 3343 | 2012-04-30 |  | 69 | 0 | 0 | 0 | 0 | EDWARDS | EDWARDS | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0103 | Las Pulgas: Construct 138 kV Tap Station for a WF Interconnect | Construct a 138 kV tap substation, cut the Raymondville to Rio Hondo 138 kV line into the tap station | Removed "From an To" info because this is a Station |  |  | Under Construction | 490 - 0691 | AEP/TCC | Teresa Trotman 918-599-2653 | 3371 | 2012-04-30 |  | 138 | 0 | 0 | 0 | 0 | WILLACY |  | Tier 4 |  |  |  | 80309 | Y | N
Old Project | No Change | 12TPIT0116 | Scarsdale 138kV Substation | Build new 138kV Scarsdale customer-owned substation. Loop through Ckt.92 PH Robinson to Garden Villas. |  | Scarscale | El Dorado/ South Houston | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-04-30 |  | 138 | 0.9 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 43610, 42652, 43173 | Y | N
Old Project | Change in Service Date. Changed from 7/15/2012 to 5/1/2012 | 12TPIT0114 | Lost Creek - New Substation | Construct a new 69/138-4.16-KV, 12/16/20 MVA x two, redundant backup substation | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-05-01 |  | 69 | 0 | 0 | 0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 12TPIT0018 | Bonham Switch 69 kV capacitors | Install 69 kV capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R556-E | 2012-05-01 |  | 69 | 0 | 0 | 0 | 18.4 | FANNIN |  | Tier 4 |  |  |  | 1761 | Y | N
Old Project | No Change | 12TPIT0120 | Seymour 69 kV capacitors | Install 69 kV capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R599-E | 2012-05-01 |  | 69 | 0 | 0 | 0 | 9.2 | BAYLOR |  | Tier 4 |  |  |  | 1532 | Y | N
Old Project | No Change | 06TPIT0112 | Lakeway second circuit from LCRA tap to the substation. | Construct 0.88 mile long 138kV circuit from Lakeway substation to the LCRA tap between Marshall Ford and Bee Creek substation. |  | Lakeway Substation | Lakeway Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_4255 | 2012-05-01 |  | 138 | 0.88 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 7349, 9235 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2012 to 5/1/2012 | 12TPIT0110 | Hollmig | Cut in the new Hollmig (7145) substation on the LCRA TSC Fredericksburg-Kendall 138 kV transmission line |  | Hollmig | Fredricksburg/Kendall | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-05-01 |  | 138 | 0 | 0 | 0 | 0 | GILLESPIE |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 11TPIT0085 | Doedyns-Sioux 138kV Line | Build New 138kV Line from Doedyns-Sioux Substations | Delays due to Right of Way process | Doedyns | Sioux | Planned | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 789640 | 2012-05-01 |  | 138 | 5.5 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-01 | 2005-04-20 |  | 8753-8792 | Y | N
Old Project | No Change | 11TPIT0110b | Valverde-AEP Weslaco Switch | Rebuild 4.5 Miles of 138kV line from Alberta Switch to Valverde Substation to AEP Weslaco Switch | Project Speedup due to delay with Alberta Switch-Doedyns | Weslaco Switch | Valverde | Planned | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-05-01 |  | 138 | 0 | 4.5 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8769-8354 | Y | N |  | Divided Project into two projects. Associated with Alberta Switch to Valverde
Old Project | No Change | 10TPIT0148 | Las Pulgas Tap - Renamed from Willacy Tap Switch 138kV | Install a normally open 138kV connection to the AEP Raymondville #2 to AEP North Rio Hondo Line at the future AEP Las Pulgas substation. | Project being revisited due to pending AEP generation interconnection agreement. |  |  | Planned | 12TPIT0103 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-05-01 |  | 138 | 0 | 0 | 0 | 0 | WILLACY | WILLACY | Tier 4 |  |  |  | 80309 | N | N
Old Project | No Change | 12TPIT0096 | Pearsall auto upgrade | Upgrade the 50 MVA138/69 kV autotransformer. |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-05-01 |  | 138 | 0 | 0 | 200 | 0 | FRIO |  | Tier 4 |  |  |  | 5893, 5895 | Y | N
Old Project | No Change | 07TPIT0017 | Handley - Hurst 138 kV line | Upgrade existing 138 kV line |  | Handley | Hurst | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M572-E | 2012-05-01 |  | 138 | 0 | 18.7 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 2110, 2109, 1951 | Y | N
Old Project | No Change | 08TPIT0107 | Leon - Flat Creek 138 kV line | Rebuild existing 138 kV line |  | Leon | Flat Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R520A-E | 2012-05-01 |  | 138 | 0 | 19.5 | 0 | 0 | EASTLAND | ERATH | Tier 4 |  |  |  | 1624, 1640 | Y | N
Old Project | No Change | 09TPIT0120 | Sun Switch - Golden - Sacroc 138 kV line | Rebuild 138 kV line |  | Sun Switch | Sacroc | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R807-E | 2012-05-01 |  | 138 | 0 | 12.8 | 0 | 0 | SCURRY | SCURRY | Tier 4 |  |  |  | 1064, 1067, 1311 | Y | N
Old Project | No Change | 10TPIT0018 | Austin Ranch - Colony 138 kV line | Upgrade existing 138 kV line |  | Austin Ranch | Colony | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3004-E | 2012-05-01 |  | 138 | 0 | 4.6 | 0 | 0 | DENTON | COLLIN | Tier 4 |  |  |  | 2518, 2378, 12518 | Y | N | 2009-R16
Old Project | No Change | 10TPIT0032 | Arco (TMPA) - Krugerville 138 kV line | Rebuild existing 138 kV line |  | Arco (TMPA) | Krugerville | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5129-E | 2012-05-01 |  | 138 | 0 | 5.6 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | 2010-06-15 | 1994, 1993 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2012 | 11TPIT0031 | Celina SE 138 kV capacitors | Install 138 kV capacitors | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3066-E | 2012-05-01 |  | 138 | 0 | 0 | 0 | 36.8 | COLLIN |  | Tier 4 |  |  |  | 2350 | Y | N
Old Project | No Change | 12TPIT0118 | Elkton - Tyler Bullard Rd - S Tyler 138 kV line | Upgrade existing 138 kV line |  | Elkton | S Tyler | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6008-E | 2012-05-01 |  | 138 | 0 | 4.59 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3106, 3219,3218 | Y | N
Old Project | No Change | 12TPIT0121 | Oran 138/69 kV autotransformer | Install second 138/69 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R598-E | 2012-05-01 |  | 138 | 0 | 0 | 50 | 0 | PALO PINTO |  | Tier 4 |  |  |  | 1571, 1572 | Y | N
Old Project | No Change | 16TPIT0002 | Barton Switch 138 kV series reactor | Install 9-ohm series reactor on line to Oran |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R565 | 2012-05-01 |  | 138 | 0 | 0 | 0 | 0 | Jack | Palo Pinto | Tier 4 |  |  |  | 1599, 1571 | N | N | 2007- E7d
Old Project | No Change | 10TPIT0041 | Temple Switch - Salado Switch 345 kV line | Upgrade existing 345 kV line |  | Temple Switch | Salado Switch | Conceptual | R494 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R705-E | 2012-05-01 |  | 345 | 0 | 15.2 | 0 | 0 | BELL | BELL | Tier 1 | 2006-11-01 |  | 2007-07-01 | 3414, 3699 | Y | N
Old Project | No Change | 10TPIT0109 | Burwick Switching Station | Construct new switching station to connect a new wind farm |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R583-WA | 2012-05-01 |  | 345 | 0 | 0 | 0 | 0 | JACK |  | Tier 4 |  |  |  | 1456 | Y | N
Old Project | No Change | 11TPIT0096 | Elm Mott Switch circuit breaker | Install 345 kV circuit breaker on line to Tradinghouse |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R737-E | 2012-05-01 |  | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3406 | Y | N
Old Project | No Change | 12TPIT0067 | Anna Switch 345/138 kV autotransformer replacement | Replace #1 autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3085-E | 2012-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2373, 2374 | Y | N
Old Project | No Change | 12TPIT0106 | Southeast Nacogdoches 345/138 kV autotransformer | Replace existing 345/138 kV autotransformer with larger autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6007-E | 2012-05-01 |  | 345 | 0 | 0 | 600 | 0 | NACOGDOCHES |  | Tier 2 | 2010-11-01 | 2010-12-01 |  | 3119, 3120 | Y | N
Old Project | Change in Service Date. Changed from 3/12/2012 to 5/14/2012 | 10TPIT0011 | Olney to Lake Kemp Switch Rebuild | Rebuild exisitng Olney to Lake Kemp Switch 69kv line |  | Olney | Lake Kemp Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 05007 | 2012-05-14 |  | 69 | 0 | 29 | 0 | 0 | YOUNG | BAYLOR | Tier 3 |  |  |  | 788781784782 | Y | N
Old Project | Change in Service Date. Changed from 12/21/2011 to 5/16/2012 | 11TPIT0101 | Reno to Rhome Rebuild | Rebuld existing Reno to Rhome 138 kV Line |  | Reno | Rhome | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 09010 | 2012-05-16 |  | 138 | 0 | 13.85 | 0 | 0 | PARKER | WISE | Tier 4 |  |  |  | 541, 572, 576 | Y | N
Old Project | No Change | 10TPIT0051 | Alamito Creek to Gonzales, Replace existing 69kV line with new 69kV line | Replace Alamito Creek to Gonzales line with 795 ACSR |  | Alamito Creek | Gonzales | Under Construction | 438 - 0701 | AEP/ETT | Jim Eriksen 918-599-2653 | 2170 | 2012-05-31 |  | 69 | 60 | 0 | 0 | 0 | PRESIDIO | PRESIDIO | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y | N
Old Project | No Change | 10TPIT0084 | Magruder: Add 1-14.4 MVAR 69 kV Cap Bank | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. | Removed "From an To" info because this is a Station |  |  | Planned | 389 - 0667 | AEP/ETT | Dave Goetz 918-599-2653 | 3374 | 2012-05-31 |  | 69 | 0 | 0 | 0 | 14.4 | VICTORIA |  | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 12TPIT0126 | Cap Bank at Pyote | Install 10MVAR 69kV Cap Bank at Pyote |  | Pyote | Pyote | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE072AB | 2012-05-31 |  | 69 | 0 | 0 | 0 | 10 | Ward | WARD | Tier 4 |  |  |  | 38000 | Y | N
Old Project | No Change | 12TPIT0047 | Zenith - Kluge and Zenith - Addicks: Reconfigure and Upgrade Circuits 09, 21, & 76. | Reconfigure circuits to form Zenith to Gertie tap to Cy Fair tap to Kluge Ckt. 09, Zenith to Gertie tap to Satsuma tap to Addicks Ckt. 76, and Camron to Cy Fair tap to Kluge Ckt. 21. Upgrade Circuits 09 & 76 to increase thermal ratings. |  |  |  | Under Construction | 12TPIT0046 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 |  | 138 | 0 | 6.1 | 0 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 45952, 45712, 45801, 45802, 46302 | Y | N |  | Part of the 2012 Northwest Houston Reliability Project
Old Project | Change in Service Date. Changed from 5/1/2012 to 5/31/2012 | 13TPIT0068 | Reconfigure Helotes to Bandera - 138kV Circuit | Reconfigure Helotes - Bandera to Helotes - Grissom 138 kV circuit |  | Helotes | Grissom | Planned |  | CPS | PM: Bruce Raney | T-0203 | 2012-05-31 |  | 138 | 0.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 |  |  |  | 5200 5020 5185 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 4/30/2012 to 5/31/2012 | 12TPIT0113 | Mont - New Substation | Construct a new 138-26.18KV, 30 MVA on LCRA Hallettsville to Sweet Home 138 Transmission line |  | Mont | Hallestville/Sweet Home | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-05-31 |  | 138 | 0 | 0 | 0 | 0 | LAVACA |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 5/30/2013 to 5/31/2012 | 14TPIT0018 | Upgrade North Alvin-Hastings | This project will rebuild North Alvin to Hastings transmission line |  | North Alvin | Hastings | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07113 | 2012-05-31 |  | 138 | 0 | 1.93 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 39010, 39015 | Y | N
Old Project | Change in Service Date. Changed from 5/31/2013 to 5/31/2012 | 13TPIT0080 | LEW Cyrus One TI 25KV Station | Build a new 25kV station on the TNMP owned land on FM 3040. The projected load is expected to reach 82MW, Lakepointe Sub will not able to support that load, but a temporary redundant system is possible form Lakepointe, Sub. |  | Lewisville TI | Lewisville TI | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE02210 | 2012-05-31 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 12TPIT0046 | Zenith 138kV | Expand Zenith substation with addition of 345/138kV 800MVA Autotransformer. Build a new 138kV double circuit line from Zenith to Gertie corner. |  | ZENITH | Gertie | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-05-31 |  | 345 | 10 | 0 | 800 | 0 | HARRIS | HARRIS | Tier 2 | 2009-02-06 | 2009-09-01 | N/A | 44900, 44910, 45801, 45802 | Y | N |  | Part of the 2012 Northwest Houston Reliability Project
Old Project | Change in Service Date. Changed from 11/1/2011 to 6/1/2012 | 11TPIT0162 | Cordele 68 kV Substation | Construct new 69 kV load serving substation in the line between Edna and Ganado Switch |  |  |  | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-06-01 |  | 69 | 0 | 0 | 0 | 0 | JACKSON |  | Tier 4 |  |  |  | 5524 | Y | N
New Project | New Project | 12TPIT0127 | Barstow Oncor POI | Create Tap for Oncor's new Barstow station |  | Barstow | Barstow | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE087AA | 2012-06-01 |  | 69 | 0 | 0 | 0 | 0 | Ward | Ward | Tier 4 |  |  |  | 38090, 38150, 38180 | Y | N
Old Project | No Change | 09TPIT0032 | Williamson 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Williamson substation. |  | Williamson Substation | Williamson Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P063 | 2012-06-01 |  | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9295 | Y | N
New Project | New Project | 12TPIT0134 | St Jo to Capps Corner | Intall additional poles and modify existing structures to raise normal operating temperature to 75° C |  | St Jo | Capps Corner | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11035 | 2012-06-01 |  | 138 | 0 | 8.6 | 0 | 0 | MONTAGUE | MONTAGUE | Tier 1 |  |  |  | 750, 754 | Y | N
Old Project | No Change | 12TPIT0093 | Switch Station Transformer Addition | Add 40 MVA Power Transformer. |  | 138 kV Switch S10009A | 138 kV Switch S1209A | Planned |  | COCS | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32000 | Y | N
Old Project | No Change | 12TPIT0125 | Cagnon to Westside - 138 kV Substation Equipment Upgrade | Replace Existing Substation Equipment at Westside to remove MLSE on the Cagnon to Westside 138kV transmission line | [5 empty] | CPS | Blake Williams | S-0524 | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5490 5419 5310 5150 5054 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0054 | SWRI to Westside - 138 kV Substation Equipment Upgrade | Replace Existing Substation Equipment at Westside to remove MLSE on the SWRI to Westside 138kV transmission line | [5 empty] | CPS | Blake Williams |  | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5419 5490 | Y | No |  | There are no transmission line additions associated with this project There are no transformers associated with this project
Old Project | No Change | 11TPIT0024 | TCC - 138kV Line Reroutes | The following 138kV lines will be rerouted: Cagnon - AMDTP - AMD becomes Cagnon - AMD Cagnon - AMDTP - Pinn becomes Cagnon - Pinn Pinn - SWRI becomes Pinn - Westside Construct a new 138kV line from TCC - SWRI Cagnon - AMD line upgrade to 1590AAC |  |  |  |  | S-0384 | CPS | T: Kevin Phillips | T-0106 | 2012-06-01 |  | 138 | 5.8 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 |  |  |  | 5423 5419 5345 5002 5004 5490 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0072 | Ferguson to Wirtz | Upgrade the 4.0 mile Ferguson (7126) -Wirtz (7104) 138kV transmission lines to 1433.6 ACSS/TW (2000 Amps) |  | Ferguson | Wirtz | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-06-01 |  | 138 | 0 | 4 | 0 | 0 | BURNET | LLANO | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
New Project | New Project | 13TPIT0101 | Winchester Terminal Equipment Upgrade | Upgrade three switches and jumpers to 2000 A at the Winchester Substation (7306). |  | Winchester | Winchester | Planned |  | LCRA TSC | Brad Woods brad.woods@lcra.org 512 369 4104 |  | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | FAYETTE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 12TPIT0097 | Cross substation | Construct new 138 kV load serving substation in San Miguel to Pearsall line. |  |  |  | Conceptual |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | ATASCOSA |  | Tier 4 |  |  |  | 5707 | Y | N
Old Project | No Change | 11TPIT0065 | Ector County North Switch (West B) - Moss 138 kV line | Construct 138 kV line with one circuit in place. |  | Ector County North Switch | Moss | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C043-E | 2012-06-01 |  | 138 | 20.5 | 0 | 0 | 0 | ECTOR | ECTOR | CREZ |  |  |  | 11140, 1019 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0066 | Ector County North Switch (West B) | Construct 138 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C016-E | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR |  | CREZ |  |  |  | 11140 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 11TPIT0100 | Moss Switch | Install 138 kV circuit breakers |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C005-E | 2012-06-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR |  | CREZ |  |  |  | 1019 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0044 | Hill Country - Install Fourth 345/138 kV Autotransformer | Install 600 MVA autotransformer at Hill Country | [5 empty] | CPS | Blake Williams |  | 2012-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5211 5210 | Y | No |  | There is no transmission line additions associated with this project
Old Project | No Change | 12TPIT0124 | Skyline to Marion - 345 kV Substation Equipment Upgrade | Replace Metering CT at Skyline and ensure a 1800 A rating and remove the existing MLSE on Skyline to Marion 345kV transmission line | [5 empty] | CPS | Blake Williams | S-0467 | 2012-06-01 |  | 345 | 0 | 0 | 0 | 0 | BEXAR | GUADALUPE | Tier 4 |  |  |  | 5371 7044 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 1/1/2012 to 6/1/2012 | 12TPIT0024 | Kendall Autotransformer Replacement | Replace the existing 345/138 kV 336 MVA autotransformer with an 800 MVA autotransformer at the Kendall Substation (7152). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-06-01 |  | 345 | 0 | 0 | 800 | 0 | KENDALL |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | CREZ Default project assigned to LCRA TSC
Old Project | No Change | 11TPIT0047 | Twin Buttes - Brown 345 kV line (Oncor Electric Delivery section) | Add second 345 kV circuit |  | Twin Buttes | Brown | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C038-E | 2012-06-01 |  | 345 | 0.2 | 0 | 0 | 0 | BROWN | BROWN | CREZ |  |  |  | 76009 | Y | N | 2007-E7f | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 12TPIT0043 | Bluff Creek - Brown 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Bluff Creek | Brown | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C076-E | 2012-06-01 |  | 345 | 86.6 | 0 | 0 | 0 | TAYLOR | BROWN | CREZ |  |  |  | 60040, 1444 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 12TPIT0045 | Brown Switch | Construct 345 kV switching station with shunt reactors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C022-E | 2012-06-01 |  | 345 | 0 | 0 | 0 | -250 | BROWN |  | CREZ |  |  |  | 1444 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0014 | Decatur Capacitor Bank | Install 15mvar capacitor bank at Decatur |  | Decatur |  | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08053 | 2012-06-15 |  | 138 | 0 | 0 | 0 | 15 | WISE |  | Tier 4 |  |  |  | 583 | Y | N
Old Project | Change in Service Date. Changed from 6/16/2012 to 6/20/2012 | 11TPIT0016 | GPLTemp-Shiloh 69kV line and Shiloh 138kV substation rebuild and install a 138 kV/69 kV autotransformer (75 MVA) | Line upgrade and substation rebuild with installing a 138 kV/69 kV autotransformer (75 MVA) at Shiloh substation | FUNDED |  |  | Under construction |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-06-20 |  | 69 | 0 | 2 | 75 | 0 | DALLAS |  | Tier 4 |  |  |  | 808, 830, 854 | Y | N |  | This project is a line upgrade and substation rebuild and install a 138 kV/69 kV-75MVA autotransformer for serving Plastipak and Shiloh loads
Old Project | Change in Service Date. Changed from 12/15/2012 to 6/29/2012 | 12TPIT0083 | Firewheel-Lookout 138 kV line | Line upgrade | On Hold For Funding | Switch 8512 at Firewheel | A new switch at new Lookout | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-06-29 |  | 138 | 0 | 1.3 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 821, 828 | Y | N |  | This project is a line reconductor for solving overload
Old Project | Change in Service Date. Changed from 12/15/2012 to 6/29/2012 | 12TPIT0084 | Lookout 138 kV new substation | New load serving | On Hold For Funding |  |  | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-06-29 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 828 | Y | N |  | This project is a line reconductor for solving overload
Old Project | Change in Service Date. Changed from 12/15/2012 to 6/29/2012 | 12TPIT0085 | Apollo-Lookout 138 kV line | Line upgrade | On Hold For Funding | Switch 8622 at Apollo | A new switch at new Lookout | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-06-29 |  | 138 | 0 | 2.8 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 802, 828 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 11TPIT0057 | Matador to Paducah Clare, Rebuild 69 kV line | Rebuild 69 kV line from Matador to Paducah Clare to Paducah City as 69/138 kV double circuit capable with 795 ACSS |  | Matador | Paducah Clare | Under Construction | 454 - 0652 | AEP/ETT | Joe Gilbert 918-599-2653 | 2328 | 2012-06-30 |  | 69 | 0 | 31.2 | 0 | 0 | MOTLEY | COTTLE | Tier 3 | 2010-05-01 | 2010-06-01 | N/A |  | Y | N
Old Project | No Change | 11TPIT0058 | Paducah Clare to Paducah City, Rebuild 69 kV line | Rebuild 69 kV line from Matador to Paducah Clare to Paducah City as 69/138 kV double circuit capable with 795 ACSS |  | Paducah Clare | Paducah City | Planned | 454 - 0652 | AEP/ETT | Joe Gilbert 918-599-2653 | 2378 | 2012-06-30 |  | 69 | 0 | 0.68 | 0 | 0 | COTTLE | COTTLE | Tier 4 | 2010-05-03 |  |  |  | Y | N
Old Project | No Change | 05TPIT0079 | Port Aransas: add 3 breaker 69 kv bus and 1-14.4 MVAR 69 kV cap bank | Add 3 breaker 69 kV ring bus on high side and install 1-14.4 MVAR capacitor bank at Port Aransas substation |  |  |  | Under Construction | 029 - 0123 | AEP/TCC/ETT/LCRA | Michael Glueck 918-599-2653 | 1136 | 2012-06-30 |  | 69 | 0 | 0 | 0 | 14.4 | ARANSAS |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 12/31/2011 to 6/30/2012 | 11TPIT0140 | Convert Kirby Substation into a double tap substation | Reconfigure Kirby substation. Kirby will loop through Ckt.37 (existing) and tap from Ckt.90 HOC to Garrott (new). | Delay in project schedule | Kirby | HO Clarke/ Garrott | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-06-30 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47320, 47321, 47322 | Y | N |  | No autotransformer capacity to be added.
Old Project | No Change | 12TPIT0095a | South Lane - West Columbia Ckts. 04 & 60 | Upgrade 138kV Ckt.60 South Lane - TXGULF to increase thermal ratings. |  | South Lane | TXGULF | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-06-30 |  | 138 | 0 | 10.52 | 0 | 0 | WHARTON | WHARTON | Tier 3 | 2011-02-02 | 2011-02-24 | N/A | 43190, 43012, 43340 | Y | N |  | Project is part of the 2011 ERCOT 5-Year Plan.
Old Project | No Change | 12TPIT0095b | South Lane - West Columbia Ckts. 04 & 60 | Upgrade 138kV Ckt.04 TXGULF - West Columbia to increase thermal ratings. |  | TXGULF | West Columbia | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-06-30 |  | 138 | 0 | 27.53 | 0 | 0 | WHARTON | BRAZORIA | Tier 3 | 2011-02-02 | 2011-02-24 | N/A | 43340, 43011, 43120, 43380 | Y | N | See project 12TPIT0095a for total project cost estimate | Project is part of the 2011 ERCOT 5-Year Plan.
New Project | New Project | 12TPIT0131 | DEPOT 138kV Substation | Construct service to new 138kV DEPOT customer-owned substation. Loop through Ckt.84 Channelview - Jacintoport |  | DEPOT | Channelview/EPOTH | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-06-30 |  | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40410 | Y | N
Old Project | No Change | 13TPIT0078 | Kendall Autotransformer Addition | Replace the existing 345-138 kV 478MVA autotransformer with an 672 MVA autotransformer at the Kendall substation (7150). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-07-01 |  | 345 | 0 | 0 | 672 | 0 | KENDALL |  | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | CREZ Default project assigned to LCRA TSC
Old Project | No Change | 12TPIT0044 | Central Bluff - Brown 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Central Bluff | Brown | Under Construction |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C075-E & C076-E | 2012-07-01 |  | 345 | 96.1 | 0 | 0 | 0 | NOLAN | BROWN | CREZ |  |  |  | 11406, 11425, 1444 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | Change in Service Date. Changed from 7/12/2012 to 7/11/2012 | 11TPIT0081 | Plastipak-Shiloh 138 kV line | Line upgrade | FUNDED | Switch 7512 at Plastipak | Switch 8702 at Shiloh | Under construction |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-07-11 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 808, 830 | Y | N |  | This project is a line upgrade for serving new load at Plastipak
Old Project | No Change | 13TPIT0013 | Perry to Midway Rebuild | Rebuild Perry to Midway with 959ACSS |  | Perry | Midway | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08050 | 2012-07-23 |  | 69 | 0 | 12.4 | 0 | 0 | FALLS | FALLS | Tier 4 |  |  |  | 92185 | Y | N
Old Project | Change in Service Date. Changed from 5/31/2012 to 7/27/2012 | 12TPIT0073 | Nordheim West - New Substation | Construct a new 69/138-26.18-KV, 12/16/20 MVA substation | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-07-27 |  | 69 | 0 | 0 | 0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | Y | N
Old Project | Change in Service Date. Changed from 7/1/2012 to 7/31/2012 | 12TPIT0082 | Hotwells - New 138kV Substation | Loop new 138kV substation into existing 138kV Ball Park to Deely line |  | Hotwells | Ball Park/Deely | Planned | T-0168 | CPS | PM: Hector Torres | S-0615 | 2012-07-31 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5227 5255 5110 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 5/1/2012 to 8/1/2012 | 12TPIT0111 | Kimbro (7337) | Cut in the new Kimbro (7337) substation on the LCRA TSC Gilleland Creek (7336) - Elgin (3650) 138kV transmission line. |  | Kimbro | Gilleland Creek/Elgin | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-08-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0066 | E C Mornhinweg | Construct a new 138 kV 795 ACSR transmission line between the GPI switching station (7459) and the new E C Mornhinweg substation (7463). |  | GPI | EC Mornhinweg | Planned |  | NBU | Greg Baumbach (830) 629-8441 gbaumbach@nbutexas.com |  | 2012-08-01 |  | 138 | 2.7 | 0 | 0 | 0 | COMAL | COMAL | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 10TPIT0082 | Carlton Switch to Mountary Rebuild | Rebuild Carlton Switch to Mountary with 959ACSS |  | Carlton | Mountary | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08051 | 2012-08-07 |  | 69 | 0 | 9.6 | 0 | 0 | ERATH | COMANCHE | Tier 4 |  |  |  | 297, 294 | Y | N
Old Project | Change in Service Date. Changed from 12/23/2011 to 8/10/2012 | 10TPIT0080 | Olney to South Bend Switch Rebuild | Rebuild Olney to South Bend Switch with 959ACSS |  | Olney | South Bend Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08011 | 2012-08-10 |  | 69 | 0 | 24 | 0 | 0 | YOUNG | YOUNG | Tier 4 |  |  |  | 788, 795 | Y | N
Old Project | No Change | 12TPIT0102 | Lone Tree: Construct 69 kV Station | Lone Tree Station: Construct New Distribution Substation in the Victoria to Leary Lane 69 kV transmission line. | Removed "From an To" info because this is a Station |  |  | Planned | 555 - 0496 | AEP/TCC | Dave Goetz 918-599-2653 | 2555 | 2012-08-31 |  | 69 | 0 | 0 | 0 | 0 | VICTORIA |  | Tier 1 |  |  |  | 88179 | Y | N
Old Project | No Change | 12TPIT0087 | Wilson Substation | Add T2, 138kV-13.09x26.18 dual kV, 40 MVA PWT w/associated bus, structures, panels, etc | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2012-08-31 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 12TPIT0104 | Rio Hondo: Add 138 kV double breaker terminal for new generation | Construct a 138 kV double breakered terminal at the Rio Hondo | Removed "From an To" info because this is a Station |  |  | Under Construction | 487 - 0689 | AEP/TCC | Rich Haley 918-599-2653 | 3365 | 2012-09-30 |  | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  | 8319 | Y | N
Old Project | Change in Service Date. Changed from 6/30/2012 to 9/30/2012 | 12TPIT0094 | De-energization of Crosby - Mont Belvieu Ckt. 43 | De-energize Ckt. 43 Crosby - Mont Belvieu. Remove autotransformers from Crosby and Mont Belvieu. Move Highlands tap from Ckt. 43 to Ckt. 66 Haney - Baytown. | Delay in project schedule |  |  | Under Construction |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-09-30 |  | 138 | 0 | 0 | -158 | 0 | HARRIS | CHAMBERS | Tier 4 |  |  |  | 40391, 49010, 40380, 40812, 41112, 49023, 41111 | Y | N
Old Project | Change in Service Date. Changed from 4/1/2013 to 10/1/2012 | 13TPIT0091 | Big Hill Reactive Devices | Install two each 50 MVAR Reactor Banks and two each 72 MVAR Capacitor Banks at the Big Hill station (76003). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-10-01 |  | 345 | 0 | 0 | 0 | -100, 144 | SCHLEICHER |  | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | Cost is included in the 12TPIT0028 project
Old Project | No Change | 12TPIT0115 | Bullick Hollow Substation (7535) | Construct a new 4 breaker ring-bus to serve load at Austin Energy's WTP#4. New substation will be constructed approximately 3.7 miles north of Marshall Ford Substation on T-325. | New substation required by AE to serve WTP#4 load,. | Bullick Hollow | Marshall Ford/Balcones | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2012-10-10 |  | 138 | 0 | 2.3 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 12TPIT0090 | Whitney 2nd Auto | Replace 60 MVA, 138/69 kV auto with 75 MVA auto |  | Whitney |  | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10048 | 2012-10-15 |  | 138 | 0 | 0 | 75 | 0 | BOSQUE |  | Tier 4 |  |  |  | 241, 243 | Y | N
Old Project | No Change | 09TPIT0125 | East Abilene, Build new 138 kV switch station, terminate new 138 kV Leon line | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | Removed "From an To" info because this is a Station |  |  | Planned | 479 - 0681 | AEP/ETT | Larry Roberson 918-599-2653 | 2272 | 2012-10-31 |  | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 10TPIT0086 | East Abilene to Putnam, Add 138 kV to existing 69 kV line | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line |  | East Abilene | Putnam | Planned | 466 - 0666 | AEP/ETT | Larry Roberson 918-599-2653 | 2346 | 2012-10-31 |  | 138 | 0 | 32 | 0 | 0 | NUECES | CALLAHAN | CREZ Modified |  |  |  |  | Y | N
New Project | New Project | 12TPIT0133 | PH Robinson Autotransformer A3 | Install temporary 600MVA Autotransformer A3 at PH Robinson |  |  |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-10-31 |  | 345/138 | 0 | 0 | 600 | 0 | GALVESTON |  | Tier 4 |  |  |  | 42000, 42010, 49049 | Y | N |  | EPRI sponsored autotransformer project
Old Project | No Change | 08TPIT0172 | Gunsight 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R829-WA | 2012-11-01 |  | 138 | 0 | 0 | 0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1360 | Y | N
Old Project | No Change | 12TPIT0028 | Twin Buttes to Big Hill | Construct a new double circuit capable 345 kV transmission line (approximately 31 miles) between the existing LCRA TSC Twin Buttes (76009) and new Big Hill station (76003). The new transmission line will consist of Cumberland conductor to provide a thermal rating of 2988 MVA. |  | Twin Buttes | Big Hill | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-11-14 |  | 345 | 31 | 0 | 0 | 0 | TOM GREEN | SCHLEICHER | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
New Project | New Project | 12TPIT0129 | Industrial Substation Conversion | Convert Industrial substation from double-tap to 138kV loop service Ckt. 84. |  | Industrial | Haden/Port | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-11-30 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40841, 40842 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2015 to 12/1/2012 | 15TPIT0012 | Petteway to Ben Hur | Rebuild Petteway to Ben Hur 69 kV line with 795 ACSR |  | Petteway | Ben Hur | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10046 | 2012-12-01 |  | 69 | 0 | 23.59 | 0 | 0 | ROBERTSON | LIMESTONE | Tier 4 |  |  |  | 93, 85, 99 | Y | N
Old Project | No Change | 11TPIT0040 | Uvalde 138 kV Substation Upgrade | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | Update Status and Removed "From an To" info because this is a Station |  |  | Under Construction | 291 - 0046 | AEP/TCC | Terry Weeks (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 1525 | 2012-12-01 |  | 138 | 0 | 0 | 0 | 0 | UVALDE |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | Change in Service Date. Changed from 6/15/2012 to 12/1/2012 | 10TPIT0010 | Coppell to Roanoke Reconductor | Reconductor existing Coppell to Roanoke 138kv line with 959ACSS conductor |  | Coppell | Roanoke | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 02005 | 2012-12-01 |  | 138 | 0 | 17 | 0 | 0 | TARRANT | DALLAS | Tier 4 |  |  |  | 1852, 661, 556, 555, 648 | Y | N
New Project | New Project | 12TPIT0135 | Spring to Bridgeport Switch | Rebuild 30.3 miles of line with 959 ACSS |  | Spring | Bridgeport Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11008 | 2012-12-01 |  | 138 | 0 | 33.3 | 0 | 0 | COOKE | WISE | Tier 3 |  |  |  | 684, 587, 17008, 634, 992 | Y | N
Old Project | No Change | 12TPIT0123 | Braunig West Bus - 138 kV Substation Equipment Upgrade | Upgrade Terminals at Braunig West for Valley Rd., Mauermann Rd., Streich Rd. circuits and upgrade terminals at remote ends to ensure a 2420 A rating and remove the existing MLSE on the 138kV transmission lines |  |  |  |  | T-0181 | CPS | Blake Williams | S-0658 | 2012-12-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5025 5465 5297 5417 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 7/1/2012 to 12/1/2012 | 11TPIT0114 | Alberta Switch-Doedyns 138kV Line | Rebuild 3.1 Miles of 138kV line from Alberta Switch to Doedyns Substation | Delay Engineering Design | Alberta Switch | Doedyns | Planned | 07TPIT7777 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2012-12-01 |  | 138 | 0 | 3.1 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8753 - 8759 | Y | N
Old Project | No Change | 09TPIT0121 | Sun Switch - Sacroc 138 kV line | Rebuild 138 kV line |  | Sun Switch | Sacroc | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R812-E | 2012-12-01 |  | 138 | 0 | 1.8 | 0 | 0 | SCURRY | SCURRY | Tier 4 |  |  |  | 1064, 1311 | Y | N
Old Project | No Change | 12TPIT0079 | Roanoke Switch - Southlake - Coppell Tap - Coppell 138 kV line | Rebuild 138 kV line |  | Roanoke Switch | Coppell | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5118 | 2012-12-01 |  | 138 | 0 | 19.63 | 0 | 0 | Denton | Tarrant | Tier 4 |  |  |  | 1852, 2018, 2020 | Y | N | 2007-R4 | 2007 ERCOT Five-year Transmission Plan Project No. 2007-R9
Old Project | Change in Service Date. Changed from 5/1/2012 to 12/1/2012 | 14TPIT0015 | Troup - Walnut Grove - Whitehouse - Tyler Grande 138 kV line | Upgrade existing line | Construction schedule change | Troup | Tyler Grande | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6002-E | 2012-12-01 |  | 138 | 0 | 13.34 | 0 | 0 | CHEROKEE | SMITH | Tier 4 |  |  |  | 3147, 3227, 3156 | Y | N
Old Project | No Change | 10TPIT0125 | Killeen Switch | Install circuit breakers and second 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C006-WA | 2012-12-01 |  | 345 | 0 | 0 | 600 | 0 | BELL |  | CREZ |  |  |  | 3422, 3423 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. The autotransformer was placed in service in 12/2010.
Old Project | No Change | 11TPIT0059 | Odessa EHV Switch #2 | Build new switching station adjacent to existing switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1010-E | 2012-12-01 |  | 345 | 0 | 0 | 0 | 0 | ECTOR |  | CREZ |  |  |  | 11028 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 12TPIT0036 | Brown - Newton 345 kV line | Construct double-circuit 345 kV line with one circuit |  | Brown | Newton | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C048-E | 2012-12-01 |  | 345 | 98.6 | 0 | 0 | 0 | BROWN | LAMPASAS | CREZ |  |  |  | 1444, 3690 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 12TPIT0037 | Newton - Killeen Switch 345 kV line | Construct double-circuit 345 kV line with one circuit. |  | Newton | Killeen Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C049-E & C006B-E | 2012-12-01 |  | 345 | 27.9 | 0 | 0 | 0 | LAMPASAS | BELL | CREZ |  |  |  | 3690, 3422 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 12TPIT0038 | Brown - Killeen Switch 345 kV line | Add 345 kV circuit to the structures of the Brown - Newton - Killeen Switch line |  | Brown | Killeen Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C048-E & C049-E | 2012-12-01 |  | 345 | 126.5 | 0 | 0 | 0 | BROWN | BELL | CREZ |  |  |  | 1444, 3691, 3422 | Y | Y | 2007-E7f | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. Cost estimate is included in the estimate for Brown - Newton - Killeen Switch 345 kV line.
Old Project | No Change | 12TPIT0039 | Newton Switch | Construct 345 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C023-E | 2012-12-01 |  | 345 | 0 | 0 | 0 | 0 | LAMPASAS |  | CREZ |  |  |  | 3690 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 14TPIT0037 | Mount Enterprise Switching Station and 345 kV line | Reconfigure switching station and 345 kV lines from Martin Lake and Trinidad |  | Martin Lake | Mount Enterprise | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6006=E | 2012-12-01 |  | 345 | 0 | 1.2 | 0 | 0 | GREGG |  | Tier 2 | 2010-11-01 | 2010-12-01 |  | 3116 | Y | N
Old Project | Change in Service Date. Changed from 10/1/2012 to 12/7/2012 | 11TPIT0134 | Dye Mound Capacitor Bank | Install 25 MVAR at Dye Mound sub |  | Dye Mound |  | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10026 | 2012-12-07 |  | 138 | 0 | 0 | 0 | 25 | MONTAGUE |  | Tier 4 |  |  |  | 741 | Y | N
Old Project | Change in Service Date. Changed from 9/10/2013 to 12/12/2012 | 10TPIT0049 | Koppe Bridge to Wellborn Transmission | Build (5.8) miles of 138 kV line(s) to serve station |  | Koppe Bridge | Wellborn | planned | 10TPIT0048 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2012-12-12 |  | 138 | 5.8 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  | 32860 32895 | Y | N
Old Project | No Change | 05TPIT0072 | Mountain Top-Blanco-Devil's Hill | Close the 69-kV switch (SW 458) at the Blanco substation(7482) to loop the load located at the Blanco substation. Upgrade the capacity of the 138-69-kV auto-transformer (T2) at the Devil’s Hill substation(7493) from 20-MVA to 45-MVA. |  | Mountain Top | Devil's Hill | Planned |  | PEC | Randy Buchanan (830) 868-6058 | 1005443 | 2012-12-13 |  | 138 | 0 | 0 | 45 | 0 | BLANCO | COMAL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 09TPIT0073 | Jupiter-Apollo 69 kV line | Line reconductor | On Hold For Funding | Switch 1377 at Jupiter | Switch 6612 at Apollo | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-30 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 806, 802 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 09TPIT0074 | Jupiter-Lawler 69 kV line | Line reconductor | On Hold For Funding | Switch 1378 at Jupiter | Switch 931 at Lawler Tap | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-30 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 806, 815, 820 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 09TPIT0076 | Lawler-College 69 kV line | Line reconductor | On Hold For Funding | Switch 932 at Lawler Tap | Switch 6832 at College | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2012-12-30 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 803, 815, 820 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 11TPIT0076 | Cottonwood 345 kV Station and Cotttonwood to Dermott 345 kV line | Establish new 345 kV Cottonwood station and construct a new double circuit 345 kV transmission line WETT new Cottonwood and Oncor's Dermott 345 kV stations. |  | Cottonwood | Dermott | Planned |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2012-12-30 |  | 345 | 74.2 | 0 | 0 | 2 x -50 | DICKENS | SCURRY | CREZ |  |  |  | 59904 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | No Change | 12TPIT0099 | Knippa to Sabinal 69 kV line, transfer to new 138/69 double circuit line | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | Update Status | Knippa | Sabinal | Under Constuction | 291 - 0046 | AEP/TCC | Terry Weeks (AEP) 918-599-2653 | 1521 | 2012-12-31 |  | 69 | 0 | 8.5 | 0 | 0 | UVALDE | MEDINA | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0100 | Uvalde to Knippa 69 kV line, tranfer to new 138/69 double circuit line | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | Update Status | Uvalde | Knippa | Under Constuction | 291 - 0046 | AEP/TCC | Terry Weeks AEP) 918-599-2653 | 1520 | 2012-12-31 |  | 69 | 0 | 4.5 | 0 | 0 | UVALDE | MEDINA | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0101 | Knippa 69 kV Substation Upgrade | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW |  | Uvalde | Sabinal | Planned | 291 - 0046 | AEP/TCC | Terry Weeks (AEP) 918-599-2653 | 1523 | 2012-12-31 |  | 69 | 0 | 0 | 0 | 0 | UVALDE | MEDINA | Tier 1 |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0108 | Wolfgang, Build new Switch Tap | Interconnect Mozart Wind Farm at Wolfgang to connect Mozart to the Jayton to Rotan 69 kV line | Project Title, Description & Owner Update | Jayton | Rotan | Planned | 493 - 695 | AEP/TNC | Dave Goetz 918-599-2653 | 2441 | 2012-12-31 |  | 69 | 0 | 0 | 0 | 0 | KENT | FISHER | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 08TPIT0018 | Uvalde to Castroville, build 138 kV line, double circuit capable | Construct Uvalde to CPS Castroville 138 kV line with 2x795 ACSR utilizing open circuit for existing 69kV circuits in ROW | Status Update | Uvalde | Castroville | Under Construction | 291 - 0046 | AEP/ETT | Terry Weeks (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 1522 | 2012-12-31 |  | 138 | 77.5 | 0 | 0 | 0 | UVALDE | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 5430, 8234 | Y | N
New Project | New Project | 12TPIT0138 | Tardis, Build new three breaker ring bus | Interconnect Kaiser Creek Wind Farm at Tardis to connect Kaiser Creek to the East Abilene to Putnam 138 kV line | NEW | East Abilene | Putnam | Planned | 500 - 707 | AEP/ETT | Dave Goetz 918-599-2653 | 2471 | 2012-12-31 |  | 138 | 0 | 0 | 0 | 0 | CALLAHAN |  | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 12TPIT0136 | STEC Sioux - El Gato: Construct 138 kV Line | Construct El Gato 138 kV partial ringbus substation and build a new 138 kV transmission line from STEC Sioux to El Gato | New | El Gato | Sioux | Under Construction | 255 - 488 | AEP/TCC/STEC | Ashley Beasley (AEP) 918-599-2653 | 1326 | 2012-12-31 |  | 138 | 5.43 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-11 | 2005-04-20 | Unknown | 85005, 8792 | Y | N
Old Project | No Change | 14TPIT0030 | Bellaire - HO Clarke Ckt. 09 | Upgrade substation equipment to increase thermal ratings. |  |  |  | Planned | 14TPIT0002 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47010, 47050, 47150 | Y | N |  | Identified as part of ERCOT RPG review of North to Houston Constraint Mitigation Project
New Project | New Project | 12TPIT0128 | WA Parish - Sienna Ckt. 02 | Upgrade 138 kV Ckt. 02 WA Parish to Sienna to increase thermal ratings. |  | WA Parish | Sienna | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 |  | 138 | 0 | 4.2 | 0 | 0 | FORT BEND | FORT BEND | Tier 4 |  |  |  | 44651, 44010 | Y | N
New Project | New Project | 12TPIT0130 | Oates Substation Conversion | Convert Oates substation from double-tap to 138kV loop service Ckt. 08. |  | Oates | Anbush/Greens Bayou | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 |  | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41191, 41192 | Y | N
New Project | New Project | 12TPIT0132 | BARNES 138kV Substation | Construct service to new 138kV BARNES customer-owned substation. Loop through Ckt.88 SRB - ROHMAS |  | BARNES | SR Bertron/ROHMAS | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2012-12-31 |  | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 41355 | Y | N
Old Project | No Change | 13TPIT0071 | Bullick Hollow 138kV Substation | Establish a new substation with (2) 50MVA unit transformers to serve the Water Treatment Plant |  | Bullick Hollow Substation | Bullick Hollow Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P070 PLAN_117_P355 | 2013-01-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9162 | Y | N |  | Will add idev file to the cases
Old Project | Change in Service Date. Changed from 7/1/2012 to 2/1/2013 | 12TPIT0109 | Laguna to Naval Base | Upgrade the 3.09-mile Laguna (8494)-Naval Base (8495) 69 kV transmission line to 69kV 795 ACSR , 115 MVA, (930 Amps) with 138 kV capable structures. |  | Laguna | Naval Base | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-02-01 |  | 69 | 0 | 3.09 | 0 | 0 | NUECES | NUECES | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 12TPIT0056 | Grelton 345 kV Station and Grelton to Long Draw 345 kV line | Establish new 345 kV Grelton station and construct a new single circuit, double circuit capable 345 kV transmission line between new Grelton and new Long Draw 345 kV stations. |  | Grelton | Long Draw | Planned |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2013-02-28 |  | 345 | 55.4 | 0 | 0 | 0 | MARTIN | BORDEN | CREZ |  |  |  | 59901 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | No Change | 12TPIT0057 | Grelton to Odessa 345 kV line | Construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Grelton and Oncor's existing Odessa 345 kV stations. |  | Grelton | Odessa | Planned |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2013-02-28 |  | 345 | 49.9 | 0 | 0 | 50 | MARTIN | SCURRY | CREZ |  |  |  |  | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | No Change | 12TPIT0058 | Long Draw 345 kV Station and Long Draw to Scurry County South 345 kV line | Establish new 345 kV Long Draw station and construct a new double circuit 345 kV transmission line between WETT's new Long Draw and Oncor's Scurry County South 345 kV stations. |  | Long Draw | Scurry | Planned |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2013-02-28 |  | 345 | 50.7 | 0 | 0 | 0 | BORDEN | SCURRY | CREZ |  |  |  | 59900 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | No Change | 13TPIT0026 | Tesla 345kv Switching Station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Cost & Status Update and Removed "From an To" info because this is a Station |  |  | Under Construction | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2393 | 2013-03-01 |  | 345 | 0 | 0 | 0 | 0 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 10TPIT0031 | Dunlap 138/345kV Autotransformer Project | Install a 138/345 kV 672 MVA autoxfmr at Dunlap, configuring a Dunlap to Lost Pines 345 kV circuit, add a new 345kV line from Dunlap to Austrop and combine 138kv Dunlap to Decker and Decker to Techridge into one single circuit bypassing Decker. |  | Dunlap Substation | Dunlap Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P132 | 2013-03-01 |  | 345 | 0 | 0 | 672 | 0 | TRAVIS | TRAVIS | Tier 3 | 2010-04-01 | 2010-06-01 | N/A | 9044, 9045 | Y | N
Old Project | No Change | 13TPIT0048 | Scurry County (Central A) - West Shackelford (Central C) | CREZ Assigned Project to build West Shackelford (Central C) substation in Shackelford county and the double ckt 345 kV lines from Scurry County sub (Oncor Central A facility) to West Shackelford substation utilizing 2-1590 ACSS/TW "Falcon" conductor. Approximate distance is 90.5 miles. Two 100 MVar (2 x -100) shunt reactors will be place on the line terminals to Sam Switch and Navarro at West Shackelford. |  | Scurry County South | West Shackelford | under construction |  | Lone Star Transmission, LLC | Julius Horvath 512-236-3135 julius.horvath@lonestar-transmission.com |  | 2013-03-01 |  | 345 | 204 | 0 | 0 | -200 | SCURRY | SHACKELFORD | CREZ | N/A | N/A | N/A | West Shackelford 68000 | Y | N |  | Total project costs are preliminary and assume two 100 MVAR reactors and associated components at West Shackelford. There will be 2 x 100 MVAR shunt reactor banks at West Shackelford. 1 x 100 MVAR bank will be on the line to Navarro and 1 x 100 MVAR bank will be on the line to Sam Switch. Both banks will have the capability to be operated with either or both lines out of service.
Old Project | No Change | 13TPIT0049 | West Shackelford (Central C) - Sam Switch/Navarro | CREZ Assigned Project to build Sam Switch (Hill County) and Navarro (Navarro County) substations. There will be a double circuit line from West Shackelford (Central C) substation to Sam Switch utilizing a 2-1590 ACSS/TW "Falcon" conductor. At Sam Switch one of the circuits will terminate in the substation and the other will continue to Navarro as a single circuit line utilizing the same 2-1590 ACSS/TW "Falcon" conductor. The towers from Sam Switch to Navarro will be designed so that a second 345kV circuit can be added in the future. Approximate distance from West Shackelford to Sam Switch is 187.2 miles and approximate distance from Sam Switch to Navarro is 33.3 miles. Both lines will be series compensated at about 50% of the reactance in two banks; one approximately at 60 miles from West Shackelford at Romney (Eastland Co) and another at approximately 120 miles from West Shackelford at Kopperl (Bosque Co). There will be four 50 MVar (4 x -50) shunt reactors at the Romney station, two on the east side of the series capacitors and two on the west side. |  | West Shackelford | Circuit 1 - Sam Switch Circuit 2 - Navarro | under construction |  | Lone Star Transmission, LLC | Julius Horvath 512-236-3135 julius.horvath@lonestar-transmission.com |  | 2013-03-01 |  | 345 | 402 | 0 | 0 | -200 | SHACKELFORD | HILL / NAVARRO | CREZ | N/A | N/A | N/A | Romney 1 W 68010 Romney 2 W 68050 Romney 1 E 68020 Romney 2 E 68060 Kopperl 1 W 68030 Kopperl 2 W 68070 Kopperl 1 E 68040 Kopperl 2 E 68080 Sam Switch 68090 Navarro 68091 Sam Reactr 68005 Nav Reactr 68006 | Y | N | Planned in-service date for Sam Switch and Navarro stations only is by May 1, 2012. The existing Oncor lines will be cut into these stations by this date. | Total project costs are preliminary and assume two series capacitor bank stations (Kopperl, Romney) equally spaced between West Shackelford and Sam Switch consisting of two series capacitor banks rated at 683 MVAR and 817 MVAR, with associated switches and line terminals and associated components at both Sam Switch and Navarro substations. There will be 4 x 50 MVAR shunt reactor banks at Romney, 2 x 50 MVAR on the east side of the series capacitors and 2 x 50 MVAR on the west side.
Old Project | No Change | 12TPIT0049 | LS04 Silverton to Cottonwood | Construct a new 345kV double circuit line from Silverton switching station to WETT's Cottonwod switching station | New | Cottonwood | Silverton | Planned | 12TPIT0050 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-03-01 |  | 345 | 64.5 | 0 | 0 | 0 | BRISCOE | DICKENS | CREZ |  |  |  | 99103-99104 | Y | N |  | CCN Granted under PUC Docket # 38560
Old Project | No Change | 12TPIT0050 | Silverton Collection Station | Construct the new 345 kV Silverton switching station.Initial build is 14 element folded breaker and one half bus arrangement. | New |  |  | Planned | 12TPIT0049 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-03-01 |  | 345 | 0 | 0 | 0 | 100 -50 | BRISCOE |  | CREZ |  |  |  | 99103 | Y | N |  | Filed under PUC Docket # 38560
Old Project | No Change | 13TPIT0051 | Gray to Tesla, build double circuit 345 kV line | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | Updated Project Cost based on Approved CCN and revised bus numbers | Gray | Tesla | Planned |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-09 |  | 345 | 218 | 0 | 0 | 0 | GRAY | CHILDRESS | CREZ |  |  |  | 79000-60501, CKT 1 & 79000-60501, CKT 2 | Y | Y
Old Project | No Change | 13TPIT0052 | Gray Substation (Panhandle B-B), build new collector substation | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | Updated Project Cost. | - | - | Planned |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-09 |  | 345 | 0 | 0 | 0 | 0 | GRAY | - | CREZ |  |  |  | 79000 | Y | N
Old Project | No Change | 13TPIT0053 | Gray Substation (Panhandle B-B), build 150 to 200 MVAR of Reactive Compensation | Build new Gray Substation (Panhandle B-B) including 150 to 200 MVAR of reactive compensation and 345 kV double circuit line from Gray to Tesla | Updated Project Cost. | - | - | Planned |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-09 |  | 345 | 0 | 0 | 0 | -200 | GRAY | - | CREZ |  |  |  | 79000 | Y | N
Old Project | No Change | 13TPIT0054 | Gray to White Deer, build double circuit 345 kV line | Build 345 kV double circuit line from Gray to White Deer | Updated Project Cost based on Approved CCN and revised bus numbers | Gray | White Deer | Planned |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-03-11 |  | 345 | 80 | 0 | 0 | 0 | GRAY | CARSON | CREZ |  |  |  | 79000-79500,CKT 1 & 79000-79500,CKT 2 | Y | N
Old Project | No Change | 13TPIT0019 | Riley to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | Riley | Edith Clarke | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2381 | 2013-03-25 |  | 345 | 85.6 | 0 | 0 | 0 | WILBARGER | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0023 | Edith Clarke 345kV station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Status Updateand Removed "From an To" info because this is a Station |  |  | Under Construction | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2387 | 2013-03-25 |  | 345 | 0 | 0 | 0 | 0 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0020 | Tesla to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | Tesla | Edith Clarke | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2382 | 2013-03-27 |  | 345 | 79.8 | 0 | 0 | 0 | COTTLE | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0028 | Tesla, add four 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Project Title, Cost & Reactive Capability Update |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2395 | 2013-03-27 |  | 345 | 0 | 0 | 0 | -200 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 10TPIT0070 | Magruder to North Victoria: Rebuild 69 kV Line | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | Magruder | North Victoria | Planned | 389 - 0566 | AEP/TCC | Dave Goetz 918-599-2653 | 3261 | 2013-03-31 |  | 69 | 0 | 3.7 | 0 | 0 | VICTORIA | VICTORIA | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 1/1/2013 to 3/31/2013 | 13TPIT0024 | Edith Clarke, add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule & Cost Update and Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2389 | 2013-03-31 |  | 345 | 0 | 0 | 0 | +261.8 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0027 | Tesla, add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost & Status Updateand Removed "From an To" info because this is a Station |  |  | Under Construction | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2394 | 2013-03-31 |  | 345 | 0 | 0 | 0 | +261.8 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 7/31/2013 to 3/31/2013 | 13TPIT0025 | Edith Clarke, add four 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2390 | 2013-03-31 |  | 345 | 0 | 0 | 0 | -200 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 07TPIT0096 | Pockrus Substation - Reconstruct 138kV Section of the Station | Reconstruct the 138kV section of the station to install transmission circuit breakers in a ring bus configuration | On schedule |  |  | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600852 | 2013-04-12 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 917 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2013 | 11TPIT0014 | Muenster - St. Jo (BEC) 69 kV line | Upgrade existing 69 kV line | Construction schedule change | Muenster | St. Jo | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R186B-E | 2013-05-01 |  | 69 | 0 | 7.8 | 0 | 0 | COOKE | COOKE | Tier 4 |  |  |  | 1712, 1716 | Y | N
Old Project | Change in Service Date. Changed from 5/31/2013 to 5/1/2013 | 07TPIT0024 | Lytle: Add 138/69 kV Auto | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Update Cost and schedule and Removed "From an To" info because this is a Station |  |  | Planned | 028 - 0028 | AEP/ETT | Terry Weeks (AEP) 918-599-2653 | 3373 | 2013-05-01 |  | 138 | 0 | 0 | 93 | 0 | MEDINA |  | Tier 4 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | No Change | 10TPIT0013 | Apollo to East Richardson | BEPC's portion of the line. |  | Apollo | East Richardson | conceptual | 09TPIT0044 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 05010 | 2013-05-01 |  | 138 | 0 | 1.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 802, 2690 | Y | N |  | mileage shown is for Bepc portion of line
Old Project | No Change | 13TPIT0046 | Flatonia-Yoakum Gartner Road | Upgrade and convert the 27.7 mile Flatonia (7248)-Moulton (7236)-Henkhaus (7237)-Shiner (7238)-Yoakum Gartner Road (7242) 2/0 ACSR 69 kV transmission line to 795 ACSR 138 kV. |  | Flatonia | Yoakum Gartner Road | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-05-01 |  | 138 | 0 | 27.7 | 0 | 0 | FAYETTE | DEWITT | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0077 | Kendall to Miller Creek to Paleface | Upgrade existing Kendall (7152) to Miller Creek (7148)line to 1433 ACSS/TW (Merrimack) and Miller (7148) Creek to Paleface (7476) line to 795 ACSR (Drake). |  | Kendall | Paleface | Planned |  | LCRA TSC | Brad Woods brad.woods@lcra.org 512 369 4104 |  | 2013-05-01 |  | 138 | 0 | 56.88 | 0 | 0 | KENDALL | Burnet | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 09TPIT0044 | E. Richardson - Apollo 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  | E. Richardson | Apollo | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3033-WA | 2013-05-01 |  | 138 | 0 | 2.32 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 802, 2690 | N | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2013 | 10TPIT0017 | Allen Switch - Plano Custer - Collin Junction 138 kV line | Upgrade existing double-circuit 138 kV line | Construction schedule change | Allen Switch | Collin Junction | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3047-E | 2013-05-01 |  | 138 | 0 | 9 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2509, 2525, 2510,2526,2524 | Y | N
Old Project | No Change | 11TPIT0032 | NW Carrollton - Collin 138 kV line | Rebuild existing 138 kV line for double-circuit operation. |  | NW Carrollton | Collin | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M368-E | 2013-05-01 |  | 138 | 16.93 | 16.93 | 0 | 0 | DALLAS | COLLIN | Tier 4 |  |  |  | 2363, 2370 | Y | N | 2009-R13
Old Project | No Change | 13TPIT0060 | Cedar Hill Switch - Mountain Creek 138 kV line | Upgrade existing line |  | Cedar Hill Switch | Mountain Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4068-E | 2013-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2422, 2421, 2412, 2411 | Y | N
Old Project | No Change | 13TPIT0092 | Killeen Switch - Harker Heights 138 kV line | Upgrade existing 138 kV line |  | Killeen Switch | Harker Heights | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R777-E | 2013-05-01 |  | 138 | 0 | 15 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 3633 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2013 | 14TPIT0011 | Midland East - Windwood 138 kV line | Upgrade existing line | Construction schedule change | Midland East | Windwood | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8009-E | 2013-05-01 |  | 138 | 0 | 1.7 | 0 | 0 | MIDLAND | MIDLAND | Tier 4 |  |  |  | 1023, 1116 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2013 | 14TPIT0016 | West Mesquite - Prairie Creek 138 kV line | Upgrade existing line | Construction schedule change | West Mesquite | Prairie Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4069-E | 2013-05-01 |  | 138 | 0 | 2.8 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2754, 2441 | Y | N | 2009-R19
New Project | New Project | 13TPIT0112 | North Andrews | Install 138 kV capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8015-E | 2013-05-01 |  | 138 | 0 | 0 | 0 | 36.8 | ANDREWS |  | Tier 4 |  |  |  | 1159 | Y | N
Old Project | Change in Service Date. Changed from 3/1/2013 to 5/1/2013 | 13TPIT0012 | Zorn Autotransformer Addition | Add a new 345-138 kV 478 MVA autotransformer at the Zorn substation (7042). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-05-01 |  | 345 | 0 | 0 | 478 | 0 | GUADALUPE |  | Tier 3 | 2008-01-30 | 2008-06-10 | N/A | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 12TPIT0051 | LS01 Silverton to Nazareth | Construct a new 345kV single circuit line from Silverton switching station to Nazareth switching station. | New | Silverton | Nazareth | Planned | 12TPIT0053 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-05-01 |  | 345 | 46 | 0 | 0 | 0 | BRISCOE | CASTRO | CREZ |  |  |  | 99103-99101 | Y | N |  | CCN Granted under PUC Docket # 38750
Old Project | No Change | 12TPIT0053 | Nazareth Collection Station | Construct the new 345 kV Nazareth switching station.Initial build is 7 element ring bus arrangement. | New |  |  | Planned | 12TPIT0051 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-05-01 |  | 345 | 0 | 0 | 0 | -50 | CASTRO |  | CREZ |  |  |  | 99101 | Y | N |  | Filed under PUC Docket # 38750
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2013 | 07TPIT0126 | Tri Corner - Seagoville Switch 345 kV line | Upgrade existing 345 kV line | Construction schedule change | Tricorner | Seagoville | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4044-E | 2013-05-01 |  | 345 | 0 | 9.4 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2432, 2433 | Y | N
Old Project | No Change | 09TPIT0042 | Collin 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M318-E | 2013-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2370, 2372 | N | N | 2009-R15
New Project | New Project | 13TPIT0113 | Renner | Replace existing 345/138 kV autotransformer with larger autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3099-E | 2013-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2355, 2354, 2355 | Y | N
Old Project | No Change | 11TPIT0038 | CSU Northgate Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities | Name changed back to Northgate (from Finfeather) at CSU's request | CSU Northgate | CSU Northgate | planned |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-05-06 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 6/1/2013 to 5/15/2013 | 13TPIT0069 | Panther Springs - New 138kV Substation | Loop new 138kV substation into existing 138kV Hill Country to Stonegate circuit #1 line |  | Panther Springs | Hill Country/Stonegate | Planned | T-0172 | CPS | PM: Don Stanton | S-0616 | 2013-05-15 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5331 5210 5415 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 12/31/2012 to 5/31/2013 | 11TPIT0107 | Happy Valley: Tie 69 kV tap into Steamboat | Happy Valley: Tie 69 kV tap into Steamboat | Schedule Update | Happy Valley | Happy Valley | Planned | 341 - 0515 | AEP/ETT | Teresa Trotman 918-599-2653 | 2092 | 2013-05-31 |  | 69 | 0 | 0.6 | 0 | 0 | TAYLOR | TAYLOR | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 13TPIT0114 | Silver to Silver Tap 1: Reterminate the 69 kV line into the Cedar Hill 69 kV station | Reterminate Silver Tap 1 to Silver with 795 ACSR | NEW | Cedar Hill | Silver Tap 1 | Conceptual | 557 - 719 | AEP/TNC | Paul Hassink 918-599-2654 | 2559 | 2013-05-31 |  | 69 | 0.02 | 0 | 0 | 0 | COKE | COKE | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 13TPIT0115 | Barnhart: Add 3.6 Mvar capacitor | Barnhart: Add 3.6 Mvar capacitor | NEW | Barnhart |  | Conceptual | 558 - 721 | AEP/TNC | Paul Hassink 918-599-2655 | 2560 | 2013-05-31 |  | 69 | 0 | 0 | 0 | +3.6 | IRION |  | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 13TPIT0116 | North Brady: Add two 7.2 Mvar capacitors at 69 kV and intergrate with DRCS | Add reactive support to the Brady area | NEW | North Brady |  | Conceptual | 559 - 722 | AEP/TNC | Paul Hassink 918-599-2656 | 2561 | 2013-05-31 |  | 69 | 0 | 0 | 0 | +14.4 | MCCULLOCH |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 07TPIT0027 | CPS Lytle to ETT Lytle: Build 138 kV Line and CPS Lytle Substation Upgrades | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle |  | CPS Lytle | ETT Lytle | Planned | 028 - 0028 | CPS/AEP/ETT | Terry Weeks (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 21 | 2013-05-31 |  | 138 | 4 | 0 | 0 | 0 | BEXAR | MEDINA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 | 5290, 8962 | Y | N |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0062 | UTMB Substaion- New Substation | This project will build new 138 kV / 12.47 kV substation to serve proposed UTMB Medical Center at Victory Lakes in League City. |  | Magnolia | League City | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE04512 | 2013-05-31 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  |  | N | N
New Project | New Project | 13TPIT0109 | Ajo to Rio Hondo: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | NEW | Ajo | Rio Hondo | Planned | 071 - 0281 | AEP/ETT/TCC | Paul Hassink 918-599-2653 | 3182 | 2013-05-31 |  | 345 | 0 | 66.708 | 0 | 0 | KENEDY | CAMERON | Tier 3 | 2011-03-10 | 2011-08-12 | PENDING | 80076, 8318 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
New Project | New Project | 13TPIT0110 | Rio Hondo: Reconfigure 345 kV Series Capacitors | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | NEW |  |  | Planned | 071 - 0281 | AEP/TCC | Paul Hassink 918-599-2653 | 3185 | 2013-05-31 |  | 345 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 3 | 2011-03-10 | 2011-08-12 | PENDING | 8318 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
Old Project | Change in Service Date. Changed from 5/30/2013 to 5/31/2013 | 12TPIT0059 | Sand Bluff 345 kV Station and Sand Bluff to Divide 345 kV line | Establish new 345 kV Sand Bluff station and construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and LCRA TSC's Divide 345 kV stations. |  | Sand Bluff | Divide | Planned |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2013-05-31 |  | 345 | 37 | 0 | 0 | 0 | GLASSCOCK | COKE | CREZ |  |  |  | 59902 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 5/30/2013 to 5/31/2013 | 12TPIT0060 | Bearkat 345 kV Station and Bearkat to Sand Bluff 345 kV line | Establish new 345 kV Bearkat station and construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and new Bearkat 345 kV stations. |  | Berkat | Sandbluff | Planned |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2013-05-31 |  | 345 | 28.9 | 0 | 0 | 0 | GLASSCOCK | STERLING | CREZ |  |  |  | 59903 | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
Old Project | Change in Service Date. Changed from 5/30/2013 to 5/31/2013 | 12TPIT0061 | Sand Bluff to Long Draw 345 kV line | Construct a new single circuit, double circuit capable 345 kV transmission line between WETT's new Sand Bluff and new Long Draw 345 kV stations. |  | Sand Bluff | Long Draw | Planned |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2013-05-31 |  | 345 | 77.4 | 0 | 0 | 0 | GLASSCOCK | BORDEN | CREZ |  |  |  |  | Y | N |  | Projects are shown in the DSB 2013 and later (2014, 2015, etc) cases starting with the August 2009 TPIT and the 2010 SSWG DSB cases
New Project | New Project | 13TPIT0102 | Greens Bayou Autotransformer Upgrade | Replace existing 400MVA Greens Bayou autotransformer A2 with 800MVA autotransformer. |  |  |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 345/138 | 0 | 0 | 400 | 0 | HARRIS |  | Tier 4 |  |  |  | 40700, 40716, 49019 | Y | N
New Project | New Project | 13TPIT0103 | Obrien Autotransformer Upgrade | Replace existing 400MVA Obrien autotransformer A3 with 800MVA autotransformer. |  |  |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-05-31 |  | 345/138 | 0 | 0 | 400 | 0 | FORT BEND |  | Tier 4 |  |  |  | 44500, 44510, 49063 | Y | N
Old Project | Change in Service Date. Changed from 6/13/2013 to 6/1/2013 | 10TPIT0079 | Morris Sheppard to Oran Rebuild | Rebuild Morris Sheppard to Oran with 959ACSS | row issues | Morris Sheppard | Oran | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 07018 | 2013-06-01 |  | 69 | 0 | 18.4 | 0 | 0 | PALO PINTO | PALO PINTO | Tier 4 |  |  |  | 343785 | Y | N
New Project | New Project | 13TPIT0105 | Silver City to Calvert Switch | Intall additional poles and modify existing structures to raise normal operating temperature to 100° C |  | Silver City | Calvert Switch | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11051 | 2013-06-01 |  | 69 | 0 | 7.95 | 0 | 0 | MILAM | MILAM | Tier 4 |  |  |  | 65, 73 | Y | N
Old Project | No Change | 12TPIT0068 | South Bend Switch to Morris Sheppard Rebuild | Rebuild South Bend Switch to Morris Sheppard 69 kV line |  | South Bend Switch | Morris Sheppard | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 09008 | 2013-06-01 |  | 138 | 0 | 18.2 | 0 | 0 | YOUNG | PALO PINTO | Tier 4 |  |  |  | 795, 343 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2014 to 6/1/2013 | 14TPIT0035 | Northgate Substaton Addition | Build new distibution substation in BTU transmission line from TAMU Substation to Atkins Substation |  | BTU Adkins 138 kV Line Switch 8027 | BTU Switch 8011 & BTU Switch 8042 @ TAMU 138 kV Substation (ring bus) | Planned |  | COCS/BTU | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2013-06-01 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32006 | Y | N
Old Project | Change in Service Date. Changed from 6/1/2015 to 6/1/2013 | 15TPIT0006 | Bandera to Broadview - 138kV substation equipment upgrade | Upgrade substation equipment at Broadview to remove existing MLSE on the Bandera to Broadview 138kV line | [5 empty] | CPS | PM: Ulrich Skerhut | S-0603 | 2013-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5020 5040 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 6/1/2012 to 6/1/2013 | 09TPIT0037 | Blossom - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Harmony Hills to Skyline line | Delayed due to budget constraint | Blossom | Harmony Hills/Skyline | Planned | T-0178 | CPS | PM: Ulrich Skerhut | S-0602 | 2013-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5022 | N | No |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Valley Rd line and the Cagnon to Howard line |  | Masterson Rd. | Cagnon/Valley/Howard | Planned |  | CPS | Blake Williams |  | 2013-06-01 |  | 138 | 20 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5296 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 13TPIT0011 | Palo Alto - New 138kV Substation | Loop new 138kV substation into the existing 138kV Leon Creek to Chavaneaux line |  | Palo Alto | Leon Creek/Chavaneaus | Conceptual |  | CPS | Blake Williams |  | 2013-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5330 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0038 | College-Brand 138 kV line | Line reconductor | On Hold For Funding | Switch 8832 at College | Switch 1364 at Brand | Planned |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2013-06-01 |  | 138 | 0 | 4.2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 829, 827 | Y | N |  | This project is a line reconductor for solving overload
Old Project | No Change | 11TPIT0078 | Riley, add four 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 467 - 0668 | AEP/ETT | Paul Hassink 918-599-2653 | 2380 | 2013-06-01 |  | 345 | 0 | 0 | 0 | -200 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 11TPIT0079 | Riley, Expand 345 kV switch station for the additon of the West Krum to Riley 345 kV double circuit | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 | Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 467 - 0668 | AEP/ETT | Paul Hassink 918-599-2653 | 2435 | 2013-06-01 |  | 345 | 0 | 0 | 0 | 0 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 6/30/2013 to 6/1/2013 | 13TPIT0022 | Gray to Oklaunion double circuit 345kV line (Tesla to Riley portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Cost Update | Tesla | Riley | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2384 | 2013-06-01 |  | 345 | 132.2 | 0 | 0 | 0 | GRAY | WILBARGER | CREZ |  |  |  |  | Y | N
New Project | New Project | 13TPIT0104 | Jack County Auto | Install 345/138 kV, 700 MVA auto at Jack County |  | Jack County | Jack County | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11038 | 2013-06-01 |  | 345 | 0 | 0 | 700 | 0 | JACK |  | Tier 4 |  |  |  | 575, 579 | Y | N
Old Project | No Change | 11TPIT0026 | Cagnon - Install a Third 345kV Autotransformer | Install one 600 MVA autotransformer. | [5 empty] | CPS | Blake Williams |  | 2013-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5055 5056 | Y | No |  | There are no transmission line additions associated with this project
Old Project | No Change | 13TPIT0036 | Krum West - Riley (Oklaunion) 345 kV line (Oncor Electric Delivery portion) | Construct double-circuit 345 kV line |  | Krum West | Riley | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C050-E | 2013-06-01 |  | 345 | 322.8 | 0 | 0 | 0 | DENTON | WILBARGER | CREZ |  |  |  | 1730, 6101 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0037 | Krum West Switch | Construct 345 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C017-E | 2013-06-01 |  | 345 | 0 | 0 | 0 | 0 | DENTON |  | CREZ |  |  |  | 1730 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0038 | Hicks Switch | Construct 345 kV switching station |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C030-E | 2013-06-01 |  | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  | 2081 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0039 | Hicks Switch - Willow Creek 345 kV line | Construct double-circuit 345 kV line |  | Hicks Switch | Willow Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C061-E | 2013-06-01 |  | 345 | 80.4 | 0 | 0 | 0 | TARRANT | WISE | CREZ |  |  |  | 2081, 1421 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | Change in Service Date. Changed from 12/1/2013 to 6/1/2013 | 13TPIT0040 | Willow Creek Switch circuit breakers | Install 345 kV circuit breakers. | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C012B-E | 2013-06-01 |  | 345 | 0 | 0 | 0 | 0 | WISE |  | CREZ |  |  |  | 1421 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | Change in Service Date. Changed from 12/1/2013 to 6/1/2013 | 13TPIT0096 | Krum West Switch reactors | Install shunt reactors | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C085R-E | 2013-06-01 |  | 345 | 0 | 0 | 0 | -100 | DENTON |  | CREZ |  |  |  | 2373 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | Change in Service Date. Changed from 6/1/2013 to 6/3/2013 | 12TPIT0081 | 36th St - New 138kV Substation | Loop new 138kV substation into existing 138kV Merida to Medina Base line and replace exiting Kelly Field #3 138kV substation | Delayed due to Budget Constraints | Merida | Medina Base | Planned | T-0161 | CPS | PM: Bruce Raney | S-0578 | 2013-06-03 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5427 5245 5305 5310 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 5/31/2014 to 6/30/2013 | 14TPIT0034 | Build Westminster Substation | Load projects indicate the Whitewright Station will be overloaded and a new station will be needed to serve Westminster, Texas. |  | Whitewright | Westminster | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE02713 | 2013-06-30 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | N | N
New Project | New Project | 13TPIT0100 | Westminster T Line | Build Westminster T line |  | Westminster | Westminster | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE076AB | 2013-06-30 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 4/1/2013 to 6/30/2013 | 11TPIT0077 | Riley, Add two 130.9 MVar capacitors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule, Cost & Status Updateand Removed "From an To" info because this is a Station |  |  | Under Construction | 467 - 0668 | AEP/ETT | Paul Hassink 918-599-2653 | 2379 | 2013-06-30 |  | 345 | 0 | 0 | 0 | +261.8 | WILBARGER |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0022 | North McCamey Autotransformer Addition | Add two new 345-138 kV 800 MVA autotransformer at the North McCamey substation (76595). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-06-30 |  | 345 | 0 | 0 | 1600 | 0 | UPTON |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y | N |  | CREZ Default project assigned to LCRA TSC
Old Project | Change in Service Date. Changed from 3/1/2012 to 7/1/2013 | 10TPIT0095 | VH Braunig - Grandview 138kV Line Reroute | Reroute VH Braunig - Grandview to become VH Braunig - Coliseum Rd | Delayed due to Rail Road permit | VH Braunig | Grandview | Planned | S-0554 | CPS | PM: Ulrich Skerhut | T-0130 | 2013-07-01 |  | 138 | 2.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5030 5095 5175 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0048 | Hereford Collection Station | Construct the new 345 kV Hereford switching station.Initial build is 7 element folded breaker and one half bus arrangement | New |  |  | Planned | 13TPIT0042, 13TPIT0043 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-07-01 |  | 345 | 0 | 0 | 0 | -200 | DEAF SMITH |  | CREZ |  |  |  | 99102 | Y | N |  | Filed under PUC Docket # 38290
Old Project | No Change | 12TPIT0052 | LS02 Nazareth to Hereford | Construct a new 345kV single circuit line from Nazareth Switching to Hereford switching station | New | Nazareth | Hereford | Planned |  | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-07-01 |  | 345 | 25.5 | 0 | 0 | 0 | CASTRO | DEAF SMITH | CREZ |  |  |  | 99101-99102 | Y | N |  | CCN Granted under PUC Docket # 38750
Old Project | No Change | 12TPIT0007 | FM-725 - New Substation | Build a 138-26.18 kV, 40 MVA substation on the GVEC McQueeney(7606) - Schumansville(7609) 138 kV transmission line |  | FM 725 | McQueeney/Schumansville | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2013-07-31 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 13TPIT0018 | McCamey C to McCamey D (Bakersfield to Big Hill) | Construct new 113 miles 1590 ACSR 345 kV line from Bakersfiled to Big Hill (McCamey C to McCamey D). |  | Bakersfield | Big Hill | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-08-01 |  | 345 | 112 | 0 | 0 | 0 | PECOS | SCHLEICHER | CREZ |  |  |  | 76002-76003 | Y | N
Old Project | No Change | 13TPIT0083 | Snook Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138/69 auto transformer relocated from Thompson Creek. |  | Snook Substation | Snook Substation | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-01 |  | 138 | 0 | 0 | 0 | 0 | BURLESON |  | Tier 4 |  |  |  | 32857 32865 | Y | N
Old Project | Change in Service Date. Changed from 12/30/2013 to 9/1/2013 | 12TPIT0029 | Big Hill to Kendall | Construct a new double circuit 345 kV transmission line (approximately 137 miles) between the new Big Hill (76003) and the existing Kendall station (7046). The new transmission lines will consist of Cumberland conductor to provide a thermal rating of 2988 MVA each. |  | Big Hill | Kendall | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2013-09-01 |  | 345 | 274 | 0 | 0 | 0 | SCHLEICHER | KENDALL | CREZ |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0042 | LS03 White Deer to Hereford | Construct a new 345kV single circuit line from White Deer switching station to Hereford switching station | New | White Deer | Hereford | Planned | 12TPIT0048, 13TPIT0043 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-09-01 |  | 345 | 91.2 | 0 | 0 | 0 | CARSON | DEAF SMITH | CREZ |  |  |  | 99201-99102 | Y | N |  | CCN Granted under PUC Docket # 38290
Old Project | No Change | 13TPIT0043 | White Deer Collection Station | Construct the new 345 kV White Deer switching station.Initial build is 10 element folded breaker and one half bus arrangement. | New |  |  | Planned | 12TPIT0048, 13TPIT0042 | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-09-01 |  | 345 | 0 | 0 | 0 | -100 | CARSON |  | CREZ |  |  |  | 99201 | Y | N |  | Filed under PUC Docket # 38290
Old Project | No Change | 13TPIT0015 | Wellborn Switching Sub | Install (3) Breaker ring to include (2) 138 lines and (1) 138/69 auto transformer relocated from Greens Prairie |  | Wellborn | Wellborn | planned | 10TPIT0049 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-10 |  | 138 | 0 | 0 | 20 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32895 (138) 32898 (69) | Y | N
Old Project | No Change | 13TPIT0016 | Greens Prairie to Wellborn Transmission | ReBuild-Reconductor (3.75) miles of 69kV line converting to 138 kV to serve Wellborn |  | Greens Prairie | Wellborn | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-10 |  | 138 | 0 | 4 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  | 32878 32895 | Y | N
Old Project | No Change | 13TPIT0017 | Greens Prairie Substation | Install (1) Breaker in existing ring bus for a 138 line from Wellborn/Millican Substation(s) |  | Greens Prairie | Greens Prairie | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2013-09-10 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32878 | Y | N
Old Project | No Change | 13TPIT0055 | Silverton to Tesla, build double circuit 345 kV line | Build 345 kV double circuit line from Silverton to Tesla | Updated Project Cost. | Silverton | Tesla | Planned |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-09-12 |  | 345 | 170 | 0 | 0 | 0 | BRISCOE | CHILDRESS | CREZ |  |  |  | 79503-79001, 79002-60501 & 79503-79003, 79004-60501 | Y | Y
Old Project | No Change | 13TPIT0056 | Silverton to Tesla, build series compensation | Add series compenstion to both circuit of the 345 kV double circuit line from Silverton to Tesla | Updated Project Cost. | - | - | Planned |  | CTT | Tim Cook 636-534-3310 Tcook@LSPower.com |  | 2013-09-12 |  | 345 | 0 | 0 | 0 | 0 | Hall | - | CREZ |  |  |  | 79001-79002 & 79003-79004 | Y | N
Old Project | No Change | 11TPIT0108 | Penascal Wind Phases 3 Generation Interconnect | Penascal Wind Phases 2 and 3 |  |  |  | Under Construction | 489 - 0690 | AEP/ETT/TCC | John Pulay 918-599-2653 | 3370 | 2013-09-21 |  | 345 | 0 | 0 | 0 | 0 | KENNEDY |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0032 | Edith Clarke to West Shackelford double circuit 345kV line (Edith Clarke to Clear Crossing portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | Edith Clarke | Clear Crossing | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2385 | 2013-09-25 |  | 345 | 150.6 | 0 | 0 | 0 | COTTLE | SHACKELFORD | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 9/30/2013 | 13TPIT0033 | Edith Clarke to West Shackelford double circuit 345kV line (Clear Crossing to West Shackelford portion) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis | Schedule Update | Clear Crossing | West Shackleford | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2386 | 2013-09-30 |  | 345 | 59.6 | 0 | 0 | 0 | COTTLE | SHACKELFORD | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 9/30/2013 | 13TPIT0085 | Clear Crossing 345 kV station | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT | Schedule Update and Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2486 | 2013-09-30 |  | 345 | 0 | 0 | 0 | 0 | HASKELL |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0030 | Dermott to Willow Creek (Dermott to Clear Crossing portion) double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | Dermott | Clear Crossing | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2391 | 2013-09-30 |  | 345 | 189 | 0 | 0 | 0 | SCURRY | HASKELL | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 10/31/2013 to 9/30/2013 | 13TPIT0088 | Clear Crossing add six 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Update Cost and schedule Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2489 | 2013-09-30 |  | 345 | 0 | 0 | 0 | -300 | HASKELL |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0050 | LS05 Silverton to White Deer | Construct a new 345kV double circuit line from Silverton switching station to White Deer switching station | New | Silverton | White Deer | Planned |  | SU | Mark Caskey, (214) 978-8243, mcaskey@sharylandutilities.com |  | 2013-09-30 |  | 345 | 68.2 | 0 | 0 | 0 | BRISCOE | CARSON | CREZ |  |  |  | 99103-99201 | Y | N |  | CCN Granted under PUC Docket # 38829
Old Project | No Change | 13TPIT0021 | Cottonwood to Edith Clarke double circuit 345kV line | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis |  | Cottonwood | Edith Clarke | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2383 | 2013-10-01 |  | 345 | 149 | 0 | 0 | 0 | DICKENS | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0089 | Tesla, add dynamic reactive compensation | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2491 | 2013-10-31 |  | 345 | 0 | 0 | 0 | +300 / -100 | COTTLE |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0090 | Hamilton Road, add dynamic reactive compensation | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost Update and Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2492 | 2013-10-31 |  | 345 | 0 | 0 | 0 | +200 / -50 | VALVERDE |  | CREZ Modified |  |  |  |  | Y | N
Old Project | No Change | 07TPIT0050 | Decker to Techridge 138kV Circuit Relocation/Reconductor | This project will reroute existing Ckt 975 (Decker to Techridge) from Yager corner to Techridge substation. The reroute will adopt 3000 Amps bundled 795 ACSS Drake. |  | Decker Switchyard | Techridge Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P071 | 2013-11-01 |  | 138 | 0 | 4.5 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 | 2009-01-26 | 2009-06-01 | N/A | 9195, 9190 | Y | N
Old Project | No Change | 12TPIT0075 | Knob Creek 345 kV Switching Station | Construct 345 kV switching station to connect a new generator |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R749-E | 2013-11-01 |  | 345 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 13413 | Y | N
Old Project | No Change | 13TPIT0070 | Nash Creek Substation | Replace 5.6 MVA with 10 MVA 69-13.09x26.18-KV transformer | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2013-11-30 |  | 69 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
New Project | New Project | 13TPIT0099 | Rebuild League City-UTMB-Magnolia | This project will rebuild League City to Magnolia 138kV transmission line with 795 ACSS wire |  | League City | Magnolia | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2013-11-30 |  | 138 | 0 | 3.62 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38920, 38930, 38950 | Y | N
Old Project | Change in Service Date. Changed from 5/31/2014 to 12/1/2013 | 07TPIT0078 | Devine to Lytle: Rebuild 69 kV Line | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Update Cost and schedule | Devine | Lytle | Planned | 028 - 0028 | AEP/ETT | Terry Weeks (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 1778 | 2013-12-01 |  | 69 | 0 | 7 | 0 | 0 | MEDINA | MEDINA | Tier 4 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | No Change | 09TPIT0039 | Woodrow to Kings Row 69kV Transmission Line Reconstruction | Reconstruct 4.2 miles of existing 69V transmission line | On schedule | Woodrow Substation PSS/E Bus 901 | Kings Row Substation PSS/E Bus 909 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600483 | 2013-12-01 |  | 69 | 0 | 4 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 901, 909 | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 12/1/2013 | 12TPIT0015 | Barney Davis to Laguna: Construct 138 kV transmission line | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintnenance |  | Barney Davis | Laguna | Planned | 400 - 0648 | AEP/ETT | Michael Glueck 918-599-2653 | 3302 | 2013-12-01 |  | 138 | 4.2 | 0 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-26 | 2009-10-09 | 2009-12-01 |  | Y | N
New Project | New Project | 13TPIT0106 | Killeen SS to Ding Dong | Intall additional poles and modify existing structures to raise normal operating temperature to 100° C |  | Killeen SS | Ding Dong | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11037 | 2013-12-01 |  | 138 | 0 | 23.8 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 136, 117, 115 | Y | N
Old Project | No Change | 06TPIT0043 | Sherry - Liggett 138 kV line & Liggett - International Airport 138 kV line | Upgrade 138 kV line |  | Sherry | Liggett | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5042-WA | 2013-12-01 |  | 138 | 0 | 13 | 0 | 0 | TARRANT | DALLAS | Tier 4 |  |  |  | 1920, 2140, 1922, 2124, 2128, 2133, 2137 | Y | N |  | Sherry - GM section was completed in 2009.
Old Project | No Change | 13TPIT0094 | Lamesa - Ackerly Vealmoor 138 kV line | Add second circuit to existing line upgrade Ackerly Vealmoor and Lamesa switching stations |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8032-E, R8033-E & R8034-E | 2013-12-01 |  | 138 | 21.5 | 0 | 0 | 0 | DAWSON | HOWARD | Tier 2 | 2008-10-01 | 2011-01-01 |  | 1355, 1163 | Y | N
Old Project | No Change | 07TPIT0140 | Trinidad - Tri Corner - Watermill 345 kV line | Upgrade existing 345 kV line |  | Trinidad | Watermill | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4045-E | 2013-12-01 |  | 345 | 0 | 52 | 0 | 0 | HENDERSON | DALLAS | Tier 3 |  |  |  | 2427, 3123 | Y | N
Old Project | No Change | 10TPIT0020 | Anna Switch - Krum W. Switch 345 kV line | Construct a double-circuit 345 kV line |  | Anna Switch | Krum W. Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C060-E | 2013-12-01 |  | 345 | 140 | 0 | 0 | 0 | DENTON | COLLIN | CREZ |  |  |  | 1730, 2373 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0035 | Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery section) | Construct double-circuit 345 kV line |  | Willow Creek | Dermott Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C054-E | 2013-12-01 |  | 345 | 220 | 0 | 0 | 0 | WISE | HASKELL | CREZ |  |  |  | 1421 | Y | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0041 | Anna Switch circuit breakers | Install 345 kV circuit breakers |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C015-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 0 | COLLIN |  | CREZ |  |  |  | 1730 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0064 | Series reactive compensation for Willow Creek - Clear Crossing - Dermott Switch (Central B) 345 kV line (Oncor Electric Delivery part) | Install series capacitor |  | Willow Creek | Dermott Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C079-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 0 | HASKELL |  | CREZ |  |  |  |  | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0072 | Scurry County South Switch (Central A) | Install shunt capacitor |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC0088-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 160 | SCURRY |  | CREZ |  |  |  | 11318 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0073 | Killeen Switch | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC0089-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 160 | BELL |  | CREZ |  |  |  | 3422 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0074 | Willow Creek Switch | Install shunt reactors. |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C054B-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | -100 | WISE |  | CREZ |  |  |  | 1421 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0075 | Graham Switching Station | Install shunt reactor |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC083-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | -300 | YOUNG |  | CREZ |  |  |  | 1430 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0076 | Parker Switching Station | Install a dynamic reactive device |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC087-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 300 -265 | PARKER |  | CREZ |  |  |  | 1436 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0081 | Brown Switch capacitors | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC082-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 240 | BROWN |  | CREZ |  |  |  | 1444 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. The estimated cost is included in the estimated cost of Brown Switch (12TPIT0045).
Old Project | No Change | 13TPIT0082 | Brown Switch dynamic reactive device | Install two dynamic reactive devices |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | RC086-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 600, -530 | BROWN |  | CREZ |  |  |  | 1444 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. The estimated cost is included in the estimated cost of Brown Switch (12TPIT0045).
Old Project | No Change | 13TPIT0093 | Willow Valley Switch | Install 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8029-E | 2013-12-01 |  | 345 | 0 | 0 | 600 | 0 | BORDEN |  | Tier 2 | 2011-03-01 | 2011-04-01 |  | 1301 | Y | N
Old Project | No Change | 13TPIT0095 | Krum West Switch capacitors | Install shunt capacitors |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C085-E | 2013-12-01 |  | 345 | 0 | 0 | 0 | 80 | DENTON |  | CREZ |  |  |  | 2373 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
Old Project | No Change | 13TPIT0029 | Big Hill to Kendall Series Compensation (Edison) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost Update | Edison | Edison | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2398 | 2013-12-09 |  | 345 | 0 | 0 | 0 | +933 | SCHLEICHER | KENDALL | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0031 | Dermott to Clear Crossing Series Compensation (Kirchoff) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Project Title & Cost Update | Kirchoff | Kirchoff | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2392 | 2013-12-09 |  | 345 | 0 | 0 | 0 | +737 | SCURRY | HASKELL | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0034 | Edith Clarke to West Shackelford Series Compensation (Gauss) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost Update | Gauss | Gauss | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2388 | 2013-12-09 |  | 345 | 0 | 0 | 0 | +737 | COTTLE | COTTLE | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0098 | Faraday Switch | Establish new 345 kV Faraday station in WETT's Long Draw-S. Scurry 345 kV line. |  |  |  | Conceputal |  | Wind Energy Transmission Texas (WETT) | Paul Steckley (508) 251-7790 Paul.Steckley@brookfieldpower.com |  | 2013-12-30 |  | 345 | 0 | 0 | 0 | 0 | BORDEN |  | Tier 2 | 2011-03-18 | 2011-04-18 | N/A |  | N | No
Old Project | No Change | 07TPIT0250 | Foster Field: Install 2-7.2 MVAR 69 kV Cap Banks | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. |  | Foster Field |  | Planned | 389 - 0667 | AEP/TCC | Dave Goetz 918-599-2653 | 2047 | 2013-12-31 |  | 69 | 0 | 0 | 0 | 14.4 | VICTORIA |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 12TPIT0008 | Kings Row to Denton North 69kV Transmission Line Reconstruction | Reconstruct 1.91 miles of existing 69V transmission line | On schedule | Kings Row Substation PSS/E Bus 909 | Denton North Interchange PSS/E Bus 912 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602674 | 2013-12-31 |  | 69 | 0 | 2 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 909, 912 | Y | N
Old Project | No Change | 12TPIT0088 | Kings Row Substation Reconstruction | Completely reconstruct the Kings Row Substation | On schedule |  |  | Planned | 09TPIT0039 12TPIT0008 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | Not Assigned | 2013-12-31 |  | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 909 | Y | N
Old Project | No Change | 12TPIT0014 | Laguna: Add 138/69 kV Auto | Construct new 138 kV line and add tranformation at Laguna to remove contingency overloads during off-peak maintnenance |  |  |  | Planned | 400 - 0648 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3307 | 2013-12-31 |  | 138 | 0 | 0 | 240 | 0 | NUECES |  | Tier 1 | 2009-03-24 | 2009-10-09 | 2009-12-01 |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 12/31/2013 | 13TPIT0086 | Edison, add two 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule & Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2487 | 2013-12-31 |  | 345 | 0 | 0 | 0 | -100 | KENDALL |  | CREZ |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2013 to 12/31/2013 | 13TPIT0087 | Orsted, add two 50 MVar reactors | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Schedule & Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2488 | 2013-12-31 |  | 345 | 0 | 0 | 0 | -100 | KENDALL |  | CREZ |  |  |  |  | Y | N
Old Project | No Change | 13TPIT0084 | Big Hill to Kendall Series Compensation (Orsted) | PUCT mandated facility additions and upgrades identified from ERCOT's scenario 2 analysis, as modified by ERCOT through the reactive study | Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 478 - 0680 | AEP/ETT | Paul Hassink 918-599-2653 | 2485 | 2013-12-31 |  | 345 | 0 | 0 | 0 | +933 | KENDALL |  | CREZ |  |  |  |  | Y | N
New Project | New Project | 13TPIT0108 | Nelson Sharpe to Ajo: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | NEW | Nelson Sharpe | Ajo | Planned | 071 - 0281 | AEP/ETT/TCC | Paul Hassink 918-599-2653 | 3181 | 2013-12-31 |  | 345 | 0 | 37.044 | 0 | 0 | KLEBERG | KENEDY | Tier 3 | 2011-03-10 | 2011-08-12 | PENDING | 85000, 80076 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
Old Project | No Change | 12TPIT0027 | North McCamey (76000) to Bakersfield (76002) | Construct a new double circuit capable 345 kV transmission line (approximately 12 miles) between the LCRA TSC North McCamey (76000) and Bakersfield (76002) stations. The new transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA | Project reassigned by PUCT to STEC from LCRA. | Bakersfield | North McCamey | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-12-31 |  | 345 | 15 | 0 | 0 | 0 | UPTON | PECOS | CREZ |  |  |  | 76000-76002 | Y | N |  | Cost estimates for this project have been included with TPIT project # 12TPIT0026. Both projects will be filed in one PUCT Project # in 2011.
Old Project | No Change | 12TPIT0026 | North McCamey (76000) to Odessa EHV (11028) | Construct a new double circuit capable 345 kV transmission line (approximately 50 miles) between the existing LCRA TSC North McCamey (McCamey A) and the existing Oncor Odessa EHV stations. The new transmission line will consist of 2x1590 ACSR Falcon conductor to provide a thermal rating of 1678 MVA. | Project reassigned by PUCT to STEC from LCRA. | Odessa | North McCamey | Planned |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2013-12-31 |  | 345 | 50 | 0 | 0 | 0 | UPTON | ECTOR | CREZ |  |  |  | 76000-11028 | Y | N |  | Cost estimates for this project include TPIT project # 12TPIT0027. Both projects will be filed in one PUCT Project # in 2011.
New Project | New Project | 13TPIT0111 | WA Parish Split Bus | Split WA Parish 345kV Bus 44000 |  |  |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2013-12-31 |  | 345 | 0 | 0 | 0 | 0 | FORT BEND |  | Tier 2 | 2011-02-08 | 2011-09-23 |  | 44000, 44005 | Y | N
Old Project | Change in Service Date. Changed from 5/31/2014 to 5/1/2014 | 07TPIT0077 | Big Foot to Devine: Rebuild 69 kV Line | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Update Cost | Big Foot | Devine | Planned | 028 - 0028 | AEP/ETT/TCC | Terry Weeks (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 1777 | 2014-05-01 |  | 69 | 0 | 6.1 | 0 | 0 | FRIO | MEDINA | Tier 4 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | Y
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2014 | 07TPIT0116 | Handley - Duval 69 kV line | Upgrade existing 69 kV line | Construction schedule change | Handley | Duval | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5116-E | 2014-05-01 |  | 69 | 0 | 5.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1952, 2158 | Y | N
Old Project | No Change | 14TPIT0008 | Holt - Emma 69 Tap kV line | Upgrade existing line |  | Holt | Emma | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8006-E | 2014-05-01 |  | 69 | 0 | 6.2 | 0 | 0 | ECTOR | ANDREWS | Tier 4 |  |  |  | 1262, 1142 | Y | N | 2009-R5
New Project | New Project | 14TPIT0049 | Big Foot SW Station: Install 138 kV Ring Bus | Add CPS Lytle to ETT Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | NEW |  |  | Planned |  | AEP/TCC | Terri Weeks 918-599-2653 | 1786 | 2014-05-01 |  | 138 | 0 | 0 | 0 | 0 | FRIO | FRIO | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 11TPIT0009 | Dunlap 138kV substation | Establish new 138kV Dunlap substation with one 30MVA transformer and will cut into existing Ckt 921 (Austrop - Decker). |  | Dunlap Substation | Dunlap Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_2930 3230_117_2933 3240_117_4930 3240_117_4933 | 2014-05-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9045 | Y | N
New Project | New Project | 14TPIT0047 | Denton 138kV System Upgrades | Proposed reliability projects necessary for the Denton area. Reconductoring 138kV loop line segments, adding second circuits, substation expansions, etc. |  | West Denton, North Denton, Jim Cristal, Arco, Pockrus, Teasley, Industrial | West Denton, North Denton, Jim Cristal, Arco, Pockrus, Teasley, Industrial | Conceptual |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T11009 | 2014-05-01 |  | 138 | 10 | 30 | 0 | 0 | Denton | Denton | Tier 3 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/1/2017 to 5/1/2014 | 06TPIT0143 | Temple Switch - Temple SE 138 kV line | Upgrade existing 138 kV line | Studies indicate timing of project should be changed | Temple Switch | Temple SE | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R448-E | 2014-05-01 |  | 138 | 0 | 4.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3415, 3612, 3602, 3611 | Y | N
Old Project | No Change | 07TPIT0236 | N. Terrell Tap - Rose Hill 138 kV line | Rebuild existing line |  | N. Terrell Tap | Rose Hill | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3059-E | 2014-05-01 |  | 138 | 0 | 8.68 | 0 | 0 | KAUFMAN | KAUFMAN | Tier 4 |  |  |  | 2715, 2717, 2714, 2723, 2719 | Y | N
Old Project | No Change | 08TPIT0153 | Elkton - Athens North Tap 138 kV line | Upgrade existing 138 kV line |  | Elkton | Athens North Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R651-E | 2014-05-01 |  | 138 | 0 | 29.1 | 0 | 0 | HENDERSON | HENDERSON | Tier 4 | 2007-11-26 |  |  | 3177, 3178, 3172, 3131 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2014 | 09TPIT0117 | Stryker Creek - Dialville 138 kV line | Upgrade existing 138 kV line | Construction schedule change | Stryker Creek | Dialville | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R664-E | 2014-05-01 |  | 138 | 0 | 15.2 | 0 | 0 | CHEROKEE | CHEROKEE | Tier 4 |  |  |  | 3110, 3160 | Y | N
Old Project | No Change | 09TPIT0118 | Fisher Road - Wichita Falls 138 kV line | Upgrade existing 138 kV line. |  | Fisher Road | Wichita Falls | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R191-E | 2014-05-01 |  | 138 | 0 | 1.45 | 0 | 0 | WICHITA | WICHITA | Tier 4 |  |  |  | 1427, 1448 | Y | N
Old Project | No Change | 09TPIT0122 | Shamburger - Tyler NW 138 kV line | Upgrade existing 138 kV line |  | Shamburger | Tyler NW | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6001-E | 2014-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3104, 3141 | Y | N | 2009-E6
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2014 | 10TPIT0091 | Elm Mott - Waco Northcrest 138 kV line upgrade | Upgrade existing 138 kV line | Construction schedule change | Elm Mott | Waco Northcrest | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R714-E | 2014-05-01 |  | 138 | 0 | 3.6 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3407, 3575 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2014 | 11TPIT0048 | Austin Ranch 138 kV capacitors | Install capacitors | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3074-E | 2014-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | DENTON |  | Tier 4 |  |  |  | 2378, 2377 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2014 | 13TPIT0059 | Cedar Crest - Industrial 138 kV line | Upgrade existing line | Construction schedule change | Cedar Crest | Industrial | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4072-E | 2014-05-01 |  | 138 | 0 | 3.2 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2494, 2981, 2976 | Y | N | 2009-R23
Old Project | No Change | 14TPIT0012 | Mountain Creek - Norwood 138 kV line | Upgrade existing line |  | Mountain Creek | Norwood | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4074-E | 2014-05-01 |  | 138 | 0 | 7.2 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2412, 2804, 2805, 2407 | Y | N
Old Project | No Change | 14TPIT0013 | Norwood - East Levee 138 kV line | Upgrade existing line |  | Norwood | East Levee | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4073-E | 2014-05-01 |  | 138 | 0 | 6.6 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2481, 2405 | Y | N
Old Project | No Change | 14TPIT0014 | NW Carrollton - Lakepointe (TNMP) 138 kV line (Oncor Electric Delivery's section) | Upgrade existing line |  | NW Carrollton | Lakepointe (TNMP) | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5156-E | 2014-05-01 |  | 138 | 0 | 2.1 | 0 | 0 | DALLAS | DENTON | Tier 4 |  |  |  | 2362, 37010 | Y | N
New Project | New Project | 14TPIT0052 | Midland East - Stanton East 138 kV line | Upgrade existing line |  | Midland East | Stanton East | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8025-E | 2014-05-01 |  | 138 | 0 | 18.6 | 0 | 0 | MIDLAND | MARTIN | Tier 4 |  |  |  | 1023, 1326 | Y | N
New Project | New Project | 14TPIT0053 | Moss - Westover 138 kV line | Upgrade existing line |  | Moss | Westover | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8016-E | 2014-05-01 |  | 138 | 0 | 3.4 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1019, 1129 | Y | N
New Project | New Project | 14TPIT0054 | Odessa - Odessa North 138 kV line | Upgrade existing line |  | Odessa | Odessa North | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8019-E | 2014-05-01 |  | 138 | 0 | 7.2 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1126, 1122 | Y | N
New Project | New Project | 14TPIT0055 | Seagoville - Wilmer 138 kV line | Upgrade existing line |  | Seagoville | Wilmer | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4081-E | 2014-05-01 |  | 138 | 0 | 10.9 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 3076, 3083 | Y | N
New Project | New Project | 14TPIT0056 | Northaven - Welch 138 kV line | Upgrade existing line |  | Northaven | Welch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4088-E | 2014-05-01 |  | 138 | 0 | 6 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2657, 2658, 2660, 2661 | Y | N
New Project | New Project | 14TPIT0057 | Cedar Hill - Mayfield Tap North 138 kV line | Upgrade existing line |  | Cedar Hill Switch | Mayfield Tap North | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5041-E | 2014-05-01 |  | 138 | 0 | 4.3 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2422, 2421, 1912 | Y | N
Old Project | No Change | 12TPIT0080 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4037 | 2014-05-01 |  | 345 | 0 | 0 | 600 | 0 | KAUFMAN |  | Tier 4 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | N | 2007-R2
Old Project | Change in Service Date. Changed from 5/30/2015 to 5/31/2014 | 15TPIT0014 | Rebuild Wink-Cochise-Pecos 69kV | Project includes rebuilding of the Wink-Cochise-PecosMain 69KV line with 795 ACSS wire. The termination of the line at the Wink station would be ONCOR Wink. |  | Wink | Pecos | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE08711 | 2014-05-31 |  | 69 | 0 | 33.12 | 0 | 0 | Reeves | Ward | Tier 3 | 2011-07-08 | 2011-08-24 | N/A | 1075,38090, 38160 | Y | N
Old Project | No Change | 14TPIT0040 | Springwoods 138kV Substation | Build new 138kV Springwoods distribution substation. Loop through Ckt.66 Rayford to Westfield. |  | Springwoods | Rayford/ Louetta | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 138 | 3.1 | 0 | 0 | 0 | MONTGOMERY |  | Tier 4 |  |  |  | 46270, 46295, 46051 | N | N
New Project | New Project | 14TPIT0048 | Maxwell Substation | Construct 69kV/12.5kV distribution substation Maxwell (7195) on T-519 between Reedville and Lockhart. |  | Maxwell | Reedville/Lockhart | planned for 2014 |  | BBEC | Thomas Ellis |  | 2014-06-01 |  | 69 | 0 | 0 | 0 | 0 | CALDWELL |  | Tier 4 |  |  |  | see project description | Y | N
Old Project | No Change | 08TPIT0044 | Circuit 1013 Double Breaker at Decker Power Plant | Install one 138 kV, 3000 Amp, 63 kA circuit breaker and two switches to connect Ckt 1013 (Decker to McNeil) to the Decker MB2 Bus. |  | Decker Switchyard | Decker Switchyard | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P138 | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9187, 9188 | N | N |  | The double breaker configuration will not be reflected in the SSWG models because the planning models are bus based.
Old Project | No Change | 14TPIT0038 | Northland to Mag Plant Circuit 979 Upgrade | Reconductor the existing Northland to Mag Plant circuit from single 795SCAR to bundle 795 ACSR Drake and increase rating to 2000 Amp |  | Northland Substation | Mag Plant Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | NEW | 2014-06-01 |  | 138 | 0 | 4.11 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9128, 9238 | Y | N |  | Will add the project to the base case
Old Project | No Change | 13TPIT0058 | Circuit 941 Summit - Williamson Reconductor | Reconductor the entire circuit from single 795 ACSR to 2000A bundle 795 ACSR conductor. |  | Summit Substation | Williamson Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_079 | 2014-06-01 |  | 138 | 0 | 3.54 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9279, 9295 | Y | No
Old Project | No Change | 14TPIT0045 | Anderson to Cagnon - 138 kV Substation Equipment Upgrade | Upgrade terminals at Anderson and Cagnon to ensure at 2420 A rating and remove the existing MLSE on Anderson to Cagnon 138kV transmission line | [5 empty] | CPS | Blake Williams | S-0479 | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5054 5003 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0042 | Five Points to Broadview - 138 kV Transmission Line Rebuild | Rebuild 9.4 miles of 138 kV transmission line from Five Points to Broadview and ensure a minimum conductor rating of 331 MVA | [5 empty] | CPS | Blake Williams | T-0208 | 2014-06-01 |  | 138 | 0 | 9.4 | 0 | 0 | BEXAR | BEXAR | Tier 3 |  |  |  | 5025 5428 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0044 | Helotes to Hill Country - 138 kV Substation Equipment Upgrade | Upgrade terminals at Helotes and Hill Country to ensure a 2420 A rating and remove existing MLSE on Helotes to Hill Country 138 kV transmission line | [5 empty] | CPS | Blake Williams | S-0651 | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5200 5210 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0046 | Hill Country to La Sierra - 138 kV Substation Equipment Upgrade | Upgrade termainls at Hill Country and La Sierrra to ensure a 2420 A rating and remove the existing MLSE on Hill Country to La Sierra 138kV transmission line | [5 empty] | CPS | Blake Williams | S-0485 | 2014-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5209 5257 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0003 | Ranchtown - New 138 kV Substation | Loop new 138kV substation into the existing 138kV Helotes to Menger Creek line |  | Ranchtown | Helotes/Menger Creek | Conceptual | T-0175 | CPS | Blake Williams | S-0567 | 2014-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5200 5358 7663 | Y | No |  | There are no transformers associated with this project. There is no transmission line additions associated with this project
Old Project | No Change | 14TPIT0043 | Tri-County - New 138kV Substation | Loop new 138kV substation into the existing Skyline to Wiederstein transmission line |  | Skyline | Tri_Conty/Wiederstein | Conceptual | T-0191 | CPS | Blake Williams | S-0620 | 2014-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5370 5445 7461 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0031 | Cagnon - Install a Fourth 345kV Autotransformer | Install one 600 MVA autotransformer. |  |  |  |  | T-0176 | CPS | Blake Williams | S-0588 | 2014-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5056 5055 | Y | No |  | There are no transmission line additions associated with this project
Old Project | No Change | 14TPIT0032 | Downing to Mountary | Existing 69 kV line. |  | Downing | Mountary | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10044 | 2014-06-15 |  | 69 | 0 | 14.64 | 0 | 0 | COMANCHE | COMANCHE | Tier 4 |  |  |  | 281, 294 | Y | N | 2009-R29
Old Project | No Change | 14TPIT0004 | Cushman-Highway 123 | Construct a new 6.2 mile single 795 ACSR 138 kV transmission line (rated 220 MVA) from the new Highway 123 substation (7221) located near the intersection of State Highway 123 and the GVEC Hickory Forest (7225)-New Berlin (7612) 138 kV (T–529) transmission line to the LCRA TSC Cushman substation (7226). |  | Highway 123 | Cushman/New Berlin/Hickory Forrest | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2014-06-30 |  | 138 | 6.2 | 0 | 0 | 0 | GUADALUPE |  | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 05TPIT0065 | Highway 32-Wimberley | Construct a new 795 ACSR (220-MVA) 138-kV double circuit transmission line (approximately four miles) between the Highway 32(7546) and Wimberley(7496) substations. |  | Highway 32 | Wimberley | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2014-06-30 |  | 138 | 4 | 0 | 0 | 0 | HAYS | HAYS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N | N
Old Project | No Change | 14TPIT0021 | Buttercup-Whitestone Upgrade | Upgrade the 2.3-mile Buttercup (7531)-Whitestone (7529) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). |  | Buttercup Substation | Whitestone Substation | Planned |  | PEC | Randy Buchanan (830) 868-6058 |  | 2014-06-30 |  | 138 | 0 | 2.3 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 13TPIT0047 | Parkway to EC Mornhinweg | Construct a new 138 kV 795 ACSR transmission line between the new EC Mornhinweg substation (7463) and the Parkway substation (7611). |  | Parkway | EC Mornhinweg | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2014-08-01 |  | 138 | 8 | 0 | 0 | 0 | COMAL | GUADALUPE | Tier 2 | 2009-02-06 | 2009-06-01 | N/A | SEE PROJECT DESCRIPTION | Y | N
Old Project | Change in Service Date. Changed from 5/30/2013 to 8/31/2014 | 13TPIT0079 | Rebuild Alvin-North Alvin | This project will rebuild Alvin to North Alvin 138kV transmission line with 795 ACSS wire |  | Alvin | North Alvin | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07211 | 2014-08-31 |  | 138 | 0 | 2.08 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 39015, 39030 | Y | N
Old Project | Change in Service Date. Changed from 5/30/2015 to 8/31/2014 | 15TPIT0015 | Rebuild Hastings-Friendswood | This project will rebuild Hastings to Friendswood 138kV transmission line with 795 ACSS wire |  | Hastings | Friendswood | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE08112 | 2014-08-31 |  | 138 | 0 | 7.3 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38980, 39010 | Y | N
Old Project | No Change | 06TPIT0057 | Magruder: Add 138/69 kV, 187 MVA, auto, 3 breaker 138 kV ringbus, 1 69 kV lowside breaker | Reconductor Victoria to North Victoria and North Victoria to Magruder 69 kV line to 1590 ACSR. Install 138/69 kV, 187 MVA, autotransformer at Magruder on the Victoria to Thomaston 138kV line. | Removed "From an To" info because this is a Station |  |  | Planned | 389 - 0567 | AEP/ETT/TCC | Dave Goetz 918-599-2653 | 3375 | 2014-09-30 |  | 138 | 0 | 0 | 187 | 0 | VICTORIA |  | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0022 | Sand Dollar 345 kV: Construct GIS 4 Breaker Ring Bus | Las Brisas Energy Center 1200 MW Generator Interconnect |  |  |  | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2653 | 3388 | 2014-09-30 |  | 345 | 0 | 0 | 0 | 0 | NUECES |  | Tier 3 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0023 | Nopalito 345 kV: Construct 5 Breaker Ring Bus | Las Brisas Energy Center 1200 MW Generator Interconnect |  |  |  | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2653 | 3390 | 2014-09-30 |  | 345 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 3 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0024 | Lon Hill to Sand Dollar 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect |  | Lon Hill | Sand Dollar | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2653 | 3389 | 2014-09-30 |  | 345 | 11.5 | 0 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y | N
Old Project | No Change | 14TPIT0026 | Sand Dollar to Las Brisas Energy Center #1 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect | Added note | Sand Dollar | Las Brisas | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2653 | 3392 | 2014-09-30 |  | 345 | 2 | 0 | 0 | 0 | NUECES | NUECES | Tier 2 |  |  |  |  | Y | N |  | backfeed 13 months prior to commercial operation date
Old Project | No Change | 14TPIT0041 | Coliseum to Kirby - 138 kV Transmission Line Rebuild | Rebuild 4.2 miles of 138 kV transmission line from Coliseum to Holbrook to Kirby and ensure a minimum conductor rating of 331 MVA | [5 empty] | CPS | Blake Williams | T-0164 | 2014-12-01 |  | 138 | 0 | 4.2 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5095 5218 5250 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 14TPIT0039 | E C Mornhinweg (7463) | Add E C Mornhinweg (7463) substation to LCRA TSC Parkway to GPI switching station 138 kV transmission line. |  | EC Mornhinweg | Parkway/GPI | Planned |  | NBU | Greg Baumbach (830) 629-8441 gbaumbach@nbutexas.com |  | 2014-12-01 |  | 138 | 0 | 0 | 0 | 0 | COMAL |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | No Change | 08TPIT0104 | Elgin Switching Station - Elgin 69 kV line conversion to 138 kV | Rebuild existing 69 kV line and convert to 138 kV operation |  | Elgin Switching Station | Elgin | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R471-E | 2014-12-01 |  | 138 | 0 | 5.9 | 0 | 0 | WILLIAMSON | BASTROP | Tier 4 |  |  |  | 3655, 3650 | Y | N
Old Project | Change in Service Date. Changed from 12/1/2013 to 12/1/2014 | 13TPIT0063 | Salado 138 kV Switch | Construct 138 kV switching station | Construction schedule change |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R445B-E | 2014-12-01 |  | 138 | 0 | 0 | 0 | 0 | BELL |  | Tier 4 |  |  |  | 13640 | Y | N
Old Project | No Change | 10TPIT0063 | Geronimo(7604)-CMC (SMI) 138 kV Line rebuild | Rebuild the existing 69-kV 4/0 transmission line to 138-kV 795 MCM between Geronimo and CMC (SMI) substations on existing right-of-way, and extend to CMC (SMI) station. | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2014-12-31 |  | 138 | 0 | 5.5 | 0 | 0 | GUADALUPE | GUADALUPE | Tier 4 |  |  |  | See Project Title | N | N
New Project | New Project | 14TPIT0050 | Lon Hill to North Edinburg: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | NEW | Lon Hill | North Edinburg | Planned | 071 - 0281 | AEP/TCC | Paul Hassink 918-599-2653 | 3183 | 2014-12-31 |  | 345 | 0 | 122.94 | 0 | 0 | NUECES | HIDALGO | Tier 1 | 2011-03-10 | 2011-08-12 | PENDING | 8455, 8383 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
New Project | New Project | 14TPIT0051 | North Edinburg: Reconfigure 345 kV Series Capacitors and Terminate 345 kV Lobo Line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | Updated Cost |  |  | Planned | 071 - 0281 | AEP/TCC | Paul Hassink 918-599-2653 | 3184 | 2014-12-31 |  | 345 | 0 | 0 | 0 | 0 | HIDALGO |  | Tier 3 | 2011-03-10 | 2011-08-12 | PENDING | 8455 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
Old Project | Change in Service Date. Changed from 12/1/2014 to 1/1/2015 | 15TPIT0009 | Fayette Power Project-Fayetteville | Loop Fayette Power Project (7056)– Salem (7058) 345 kV line into Fayetteville (7057) and upgrade Fayette Power Project (7056) – Fayetteville (7057) 345 kV double circuit lines. | Date revised after ERCOT BOD approval | FPP | Fayetteville | Planned | 14TPIT0002 | LCRA TSC | Brad Woods brad.woods@lcra.org 512 369 4104 |  | 2015-01-01 |  | 345 | 0 | 16.4 | 0 | 0 | FAYETTE | FAYETTE | Tier 1 | 2009-07-01 | 2010-07-27 | 2010-08-17 | SEE PROJECT DESCRIPTION | Y | Y |  | Part of North to Houston Constraint Mitigation Project
New Project | New Project | 15TPIT0022 | Dobbin to Highway 6 | Build 23 miles of 138 kV transmission line with 959 ACSS |  | Dobbin | Highway 6 | planned | 13TPIT0107 15TPIT0022 16TPIT0016 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11047 | 2015-02-09 |  | 138 | 23 | 0 | 0 | 0 | MONTGOMERY | BRAZOS | Tier 1 | 2010-10-04 | 2010-12-20 | 2011-05-05 | 3, 5, 6 | Y | N
New Project | New Project | 13TPIT0107 | Dobbin switching station | Construct 345/138 kV switching station in CNP's Roans Prairie to Kuykendahl line |  | Dobbin | Dobbin | planned | 13TPIT0107 15TPIT0022 16TPIT0016 | BRAZOS-CNP | Brion Ryan, 254-750-6353, Wayne E. Kemper 713 207 2192 | 11045 | 2015-02-09 |  | 345 | 0 | 0 | 700 | 0 | MONTGOMERY |  | Tier 1 | 2010-10-04 | 2010-12-20 | 2011-05-05 | 40630, 3 | Y | Y
Old Project | Change in Service Date. Changed from 6/1/2015 to 3/1/2015 | 15TPIT0018 | Kerrville Stadium to Raymond F. Barker | Upgrade the 10.1-mile Kerrville Stadium (7136) – Kerrville Travis (7162) – Kerrville Legion (7160) - Raymond F. Barker (7159) 69 kV transmission lines to 795 ACSR, 138 kV (220 MVA / 920 Amperes) and OPGW. |  | Kerrville Stadium | Raymond F Barker | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2015-03-01 |  | 138 | 0 | 10.1 | 0 | 0 | KERR | KERR | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | Change in Service Date. Changed from 3/31/2014 to 3/31/2015 | 07TPIT0252 | Greta: Install 1-7.2 MVAR 69 kV Cap Bank | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date changed and removed "From an To" info because this is a Station |  |  | Planned | 100 - 0104 | AEP/TCC | Paul Hassink 918-599-2653 | 2045 | 2015-03-31 |  | 69 | 0 | 0 | 0 | 7.2 | REFUGIO |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 3/31/2014 to 3/31/2015 | 08TPIT0131 | Melon Creek: Install 138/69 KV Auto | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date change and Removed "From an To" info because this is a Station |  |  | Planned | 100 - 0100 | AEP/TCC | Paul Hassink 918-599-2653 | 2021 and 2022 | 2015-03-31 |  | 138 | 0 | 0 | 50 | 0 | REFUGIO |  | Tier 4 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2015 | 07TPIT0210 | Hilltop - White Settlement 69 kV line | Rebuild 4/0 ACSR section of line | Construction schedule change | Hilltop | White Settlement | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5135-E | 2015-05-01 |  | 69 | 0 | 14.33 | 0 | 0 | PARKER | TARRANT | Tier 4 |  |  |  | 502, 1588, 2089 | Y | N
Old Project | No Change | 09TPIT0116 | Gatesville Tap - Gatesville TDC 69 kV line | Upgrade existing 69 kV line |  | Gatesville Tap | Gatesville TDC | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R497-WA | 2015-05-01 |  | 69 | 0 | 4.4 | 0 | 0 | MCLENNAN | CORYELL | Tier 4 |  |  |  | 3587, 3583 | Y | N
Old Project | No Change | 11TPIT0015 | Sherry - Park Row - Grand Prairie 138 kV line | Upgrade existing 138 kV line |  | Sherry | Grand Prairie | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5121-E | 2015-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1919, 1920, 2257, 2258 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2015 | 13TPIT0061 | Terrell Switch - North Terrell Tap 138 kV line | Upgrade existing line | Construction schedule change | Terrell Switch | North Terrell Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M363-E | 2015-05-01 |  | 138 | 0 | 7.9 | 0 | 0 | KAUFMAN | KAUFMAN | Tier 4 |  |  |  | 2718, 2715, 2721 | Y | N
New Project | New Project | 15TPIT0025 | Monticello SES - Monticello Tap 138 kV line | Upgrade existing line |  | Monticello SES | Monticello Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R906-E | 2015-05-01 |  | 138 | 0 | 20.1 | 0 | 0 | TITUS | FRANKLIN | Tier 4 |  |  |  | 1795, 1994 | Y | N
Old Project | No Change | 14TPIT0000 | CSU Graham Rd Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  | CSU Graham Rd | CSU Graham Rd | planned |  | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2015-05-06 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 12/1/2012 to 6/1/2015 | 15TPIT0011 | Shannon to Montague | Rebuild Shannon to Montague 69 kV line with 959 ACSS. |  | Shannon | Montague | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10045 | 2015-06-01 |  | 69 | 0 | 23.36 | 0 | 0 | CLAY | MONTAGUE | Tier 4 |  |  |  | 772, 769, 768, 633 | Y | N
Old Project | No Change | 15TPIT0013 | Seymour to Lake Kemp Switch | Rebuild Semour to Lake Kemp Switch 69 kV line with 795 ACSR |  | Seymour | Lake Kemp Switch | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 10047 | 2015-06-01 |  | 69 | 0 | 6.9 | 0 | 0 | BAYLOR | BAYLOR | Tier 4 |  |  |  | 779, 782 | Y | N
Old Project | No Change | 15TPIT0002 | Hickory Substation to Locust Substation 69kV Transmission Line Reconstruction | Reconstruct 2.5 miles of existing 69V transmission line | On schedule | Hickory Substation, 910 | Locust Substation, 914 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | Not Assigned | 2015-06-01 |  | 69 | 0 | 2.5 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910, 914 | N | N
Old Project | No Change | 10TPIT0025 | Rinard Creek 138kV substation | Establish 138kV Rinard Ck substation with (2) 30MVA transformers and will cut into existing Ckt 987 (Lytton Springs to Slaughter Lane). |  | Rinard Creek substation | Rinard Creek Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P151 PLAN_117_P152 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9262 | Y | N
Old Project | No Change | 07TPIT0060 | Howard Lane to Techridge Reconductor | The project re-conductors Circuit 1004 (Techridge to Howard Lane) using 795 ACSS Drake conductors to increase the capacity to 3000 Amp. |  | Howard Lane Substation | Techridge Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P067 PLAN_117_P194 | 2015-06-01 |  | 138 | 0 | 1.72 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9190, 9217 | Y | N
Old Project | Change in Service Date. Changed from 6/15/2013 to 6/1/2015 | 10TPIT0083 | Mustang Capacitor Bank | Install 100mvar capacitors at future Mustang sub |  | Mustang |  | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 08052 | 2015-06-01 |  | 138 | 0 | 0 | 0 | 100 | DENTON |  | Tier 4 |  |  |  | 654 | Y | N
New Project | New Project | 15TPIT0023 | Seaton Auto | Upgrade 138/69 kV auto to 100 MVA |  | Seaton | Seaton | planned |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11036 | 2015-06-01 |  | 138 | 0 | 0 | 100 | 0 | BELL |  | Tier 4 |  |  |  | 130, 131 | Y | N
Old Project | No Change | 15TPIT0004 | Converse - New 138kV Substation | Loop new 138kV substation into existing 138kV Deely to Skyline line |  | Converse | Deely/Skyline | Conceptual | T-0177 | CPS | Blake Williams | S-0601 | 2015-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5098 5110 5370 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0005 | Deely to Laredo - 138kV substation equipment upgrade | Upgrade substation equipment at Deely and Laredo to remove existing MLSE on the Deely to Laredo 138kV line | [5 empty] | CPS | Blake Williams | S-0604 | 2015-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5210 5255 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0007 | Green Mountain to Stonegate - 138kV 2nd Circuit | Build second 138kV transmission line from Green Mountain to Stonegate on existing transmission structures |  | Green Mountain | Stonegate | Conceptual | S-0608 | CPS | Blake Williams | T-0179 | 2015-06-01 |  | 138 | 11.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5180 5415 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 6/1/2014 to 6/1/2015 | 14TPIT0020 | Spencer Interchange to Pockrus 138kV Transmission Line New Construction | Construct 3.25 miles of new 138V transmission line | On schedule | Spencer Interchange PSS/E Bus 982 | Pockrus Substation PSS/E Bus 917 | Planned | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | Not Assigned | 2015-06-01 |  | 138 | 3.25 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 982, 917 | N | N
Old Project | No Change | 15TPIT0019 | Blockhouse (7527) | Add a 31.2 MVAR Capacitor Bank at the Blockhouse (7527) substation | [5 empty] | PEC | Randy Buchanan (830) 868-6058 |  | 2015-06-01 |  | 138 | 0 | 0 | 0 | 31.2 | WILLIAMSON |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N | N
Old Project | No Change | 08TPIT0033 | Gilleland to Techridge 138kV Circuit | Establish a new 138kV circuit from Gilleland to Techridge and maintain a normally close tie between AEN and LCRA's switchyard at Gilleland. |  | Gilleland Substation | Techridge Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_4276 PLAN_117_P207 | 2015-06-01 |  | 345 | 8 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 1 |  |  | 2004-12-01 | 9053, 9054 | Y | N
Old Project | Change in Service Date. Changed from 12/31/2013 to 6/30/2015 | 11TPIT0084 | South League City Substation-New Substation | Build a new distribution substation in order to accommodate new subdivision growth along the FM 517 and FM 646 corridor in Dickinson, Texas |  | League City | South Shore | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE02411 | 2015-06-30 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 38900 | Y | N
New Project | New Project | 15TPIT0024 | Lon Hill to Nelson Sharpe: Reconductor 345kV line | Reconductor Lon Hill to North Edinburg and Lon Hill to Rio Hondo 345kV lines, Reconfigure Series Capacitors at North Edinburg and Rio Hondo | NEW | Lon Hill | Nelson Sharpe | Planned | 071 - 0281 | AEP/TCC | Paul Hassink 918-599-2653 | 3180 | 2015-06-30 |  | 345 | 0 | 20.81 | 0 | 0 | NUECES | KLEBERG | Tier 4 | 2011-03-10 | 2011-08-12 | PENDING | 8455, 85000 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
Old Project | Change in Service Date. Changed from 4/30/2013 to 8/30/2015 | 13TPIT0067 | Coleto Creek Substation: Interconnect New Generation to the 345 kV Rung Co-located with the Pawnee Line | Add a generation interconnection terminal at the Coleto Creek 345 kV bus. Upgrade protection, disturbance monitoring, communications, and metering for new generation. | Date change. PM updated | Coleto Creek | Pawnee Line (STEC) | Planned | 453 - 0670 | AEP/TCC | Dave Goetz 918-599-2653 | 3341 | 2015-08-30 |  | 345 | 0 | 0 | 0 | 0 | GOLIAD |  | Tier 4 |  |  |  |  | Y | N
New Project | New Project | 15TPIT0021 | Upgrade PHRobison-South Shore 138kV Line | This project will rebuild 5.6 miles of 138 kV transmission line from Centerpoint's PH Robinson Substation to TNMP's South Shore Substation |  | PHRobinson | South Shore | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE08410 | 2015-09-01 |  | 138 | 0 | 5.6 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38890, 42015 | Y | N
Old Project | No Change | 14TPIT0025 | Nopalito to Sand Dollar 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect |  | Nopalito | Sand Dollar | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2653 | 3391 | 2015-09-01 |  | 345 | 14.5 | 0 | 0 | 0 | NUECES | SAN PATRICIO | Tier 2 |  |  |  |  | Y | N
Old Project | Change in Service Date. Changed from 7/1/2016 to 9/30/2015 | 15TPIT0003 | Sand Dollar to Las Brisas Energy Center #2 345 kV: Construct New 345 kV Transmission Line | Las Brisas Energy Center 1200 MW Generator Interconnect | Schedule update | Sand Dollar | Las Brisas | Planned | 495 - 0698 | AEP/ETT | Larry Roberson 918-599-2653 | 3393 | 2015-09-30 |  | 345 | 2 | 0 | 0 | 0 | NUECES | NUECES | Tier 2 |  |  |  |  | Y | N |  | backfeed 13 months prior to commercial operation date
Old Project | No Change | 15TPIT0020 | Braunig to Brooks - 138 kV Substation Equipment Upgrade | Replace Line and Bus Switches at Brooks and ensure a 1385 A rating and remove existing MLSE on the Braunig to Brooks 138 kV transmission line |  |  |  |  | T-0194 | CPS | Blake Williams | S-0669 | 2015-12-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5025 5045 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0008 | Triple R - New Substation | Build a 138-26.18 kV, 40 MVA substation on the GVEC Wilson - Sutherland Springs (T549) 138 kV transmission line |  | Triple R | Wilson/Sutherland Springs | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2015-12-30 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 12/31/2014 to 12/31/2015 | 14TPIT0002 | Zenith to Fayetteville 345kV Circuits | Build 345kV double circuit from Zenith to Fayetteville as part of North to Houston Constraint Mitigation Project. | Delay in project schedule | ZENITH | Fayetteville | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2015-12-31 |  | 345 | 120 | 0 | 0 | 0 | HARRIS | FAYETTE | Tier 1 | 2009-07-01 | 2010-07-01 | 2010-08-01 | 44900, 7057 | Y | Y |  | Part of North to Houston Constraint Mitigation Project
Old Project | Change in Service Date. Changed from 3/31/2014 to 3/31/2016 | 08TPIT0132 | Melon Creek to Tatton: Build 69 KV Line & Tatton Substation Upgrades | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date change | Melon Creek | Tatton | Planned | 100 - 0100 | AEP/TCC | Paul Hassink 918-599-2653 | 2028 | 2016-03-31 |  | 69 | 7.7 | 0 | 0 | 0 | REFUGIO | ARANSAS | Tier 2 |  |  |  |  | Y | N
New Project | New Project | 16TPIT0016 | Dobbin to Fish Creek | Build 15.5 miles of 138 kV transmission line with 959 ACSS |  | Dobbin | Fish Creek | planned | 13TPIT0107 15TPIT0022 16TPIT0016 | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 11046 | 2016-04-05 |  | 138 | 15.5 | 0 | 0 | 0 | MONTGOMERY | MONTGOMERY | Tier 1 | 2010-10-04 | 2010-12-20 | 2011-05-05 | 3, 22, 23, 24 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2015 to 5/1/2016 | 11TPIT0050 | Roanoke Switch - Elizabeth Creek 138 kV line | Construct new line. | Studies indicate timing of project should be changed | Roanoke Switch | Elizabeth Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M509-E | 2016-05-01 |  | 138 | 3.75 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1850, 1852, 1866, 1867 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2015 to 5/1/2016 | 11TPIT0050 | Hicks Switch - Elizabeth Creek 138 kV line | Construct new 138 kV line |  | Hicks Switch | Elizabeth Creek | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M523-E | 2016-05-01 |  | 138 | 10 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 2 |  |  |  | 1866, 1867, | Y | N
Old Project | Change in Service Date. Changed from 5/1/2015 to 5/1/2016 | 11TPIT0034 | Sargent Road 345/138 kV autotransformer | Install second 345/138 kV autotransformer | Studies indicate timing of project should be changed |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M486-E | 2016-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2946, 2949 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2016 | 11TPIT0097 | Norwood Switch autotransformer | Replace #1 345/138 kV autotransformer | Studies indicate timing of project should be changed |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4070-E | 2016-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2405, 2406 | Y | N
New Project | New Project | 16TPIT0018 | Hicks Switch Autotransformer | Install 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5145-E | 2016-05-01 |  | 345 | 0 | 0 | 600 | 0 | TARRANT |  | Tier 4 |  |  |  | 2081 | Y | N
Old Project | Change in Service Date. Changed from 10/31/2016 to 5/31/2016 | 11TPIT0001 | Lobo to Rio Bravo, build 345 kV line energized at 138kV, Stations upgrade | Construct 345 kV line from Lobo to Rio Bravo energized at 138 kV | Schedule update | Lobo | Rio Bravo | Planned | 206 - 0288 | AEP/ETT | Bill Eakin 918-599-2653 | 880 | 2016-05-31 |  | 345 | 30 | 0 | 0 | 0 | WEBB | WEBB | Tier 1 |  |  |  |  | Y | N
Old Project | No Change | 16TPIT0007 | McNeil to MagPlant Ckt 977 Upgrade | Reconductor existing McNeil to MagPlant circuit from 2000 to 3000 Amp. Relocate McNeil to Summit Circuit 907 and McNeil to MagPlant Circuit 977 to separate structures |  | McNeil Substation | Mag Plant Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | NEW | 2016-06-01 |  | 138 | 0 | 3.24 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9077, 9238 | Y | N |  | Will add the ptoject to the base case.
Old Project | No Change | 16TPIT0010 | Bulverde - New 138kV Substation | Loop new 138kV substation into the existing Hill Country to Stonegate transmission line |  | Hill Country | Bulverde/Stonegate | Conceptual | T-0189 | CPS | Blake Williams | S-0665 | 2016-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5210 5051 5415 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 16TPIT0012 | Encino to Skyline - 138 kV Substation Equipment Upgrade | Upgrade terminals at Encino and Skyline to ensure a 2420 A rating and remove existing MLSE on Encino to Skyline 138 kV transmission line | [5 empty] | CPS | Blake Williams | S-0671 | 2016-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5140 5369 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 16TPIT0011 | JT Deely to Streich - 138 kV Substation Equipment Upgrade | Upgrade terminals at JT Deely and Streich Rd. to ensure a 2420 A rating and remove existing MLSE on JT Deely to Streich 138 kV transmission line | [5 empty] | CPS | Blake Williams | S-0674 | 2016-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5110 5417 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0001 | Trumbo - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Leon Creek to Pleasanton Rd line | Accelarated by Disribution Planning | Trumbo | Leon Creek/Pleasanton Rd | Conceptual | T-0082 | CPS | Blake Williams | S-0181 | 2016-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5429 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 6/1/2020 to 6/1/2016 | 09TPIT0012 | Hill Country to Skyline - 345 kV 2nd Circuit | Build second 345 kV line from Hillcountry to Skyline. The second circuit will be installed on existing transmission structures |  | Hill Country | Skyline | Conceptual |  | CPS | Blake Williams | T-0052 | 2016-06-01 |  | 345 | 11 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5211 5371 | N | No |  | There are no transformers associated with this project
Old Project | No Change | 16TPIT0013 | Skyline to Spruce - 345 kV Substation Equipment Upgrade | Replace the Line MDS at Skyline and Spruce (both circuits) and ensure all terminals have a 2420 A rating and remove existing MLSE on Skyline to Spruce 345 kV transmission lines (both circuits) | [5 empty] | CPS | Blake Williams | S-0468 | 2016-06-01 |  | 345 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5371 5400 | Y | No |  | There are no transformers associated with this project
Old Project | No Change | 15TPIT0000 | Bird Pond Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  | Bird Pond | Bird Pond | planned |  | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2016-06-11 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | N | N
New Project | New Project | 16TPIT0015 | Bells, TX- New Substation | Build new substation in Bells, TX |  | Bells | Bells | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE02211 | 2016-06-30 |  | 69 | 0 | 0 | 0 | 0 | Grayson | Grayson | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/31/2015 to 6/30/2016 | 15TPIT0017 | Construct Blossom Substation | Install 138kV Dead end structure. Purchase 138/22kV 7500kVA transformer. Install 138kV bus and fuses for transformer. Install 22kV distribution bay with 2 feeders and getaways. Purchase and install 22kV electronic reclosers and Remote Terminal Unit (RTU). Coordination with Texas Utilities (TXU) will be necessary. |  | Blossom | Blossom | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE02914 | 2016-06-30 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/31/2016 to 6/30/2016 | 16TPIT0004 | Princeton South 138KV Station | Purchase and install three 138kV breakers, construct 138kV ring bus, install control house and relays to accommodate transmission position in Farmersville West Substation site to feed the Princeton South Substation and connect to ONCOR's Royce City to Climax transmission line. |  | Princeton South | West Farmersville | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07315 | 2016-06-30 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/31/2016 to 6/30/2016 | 16TPIT0005 | Build 138kV Farm West-Princeton South | Build approximately 7.5 miles of 138 kV transmission line from Farmersville West Substation to Princeton South to provide a source to this station and a transmission feed to Longneck Substation and complete ring bus in Farmersville West and 1st 138KV position in Princeton South Station. |  | Farm West | Princeton | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07213 | 2016-06-30 |  | 138 | 7.5 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/31/2016 to 6/30/2016 | 16TPIT0006 | Convert Climax-Longneck 69kV line to 138 kV | Convert existing 69kV transmission line from Climax Station to Longneck Substation to 138kV. Purchase and install three 138kV breakers, bus, relaying, wiring and transmission dead-end tower in both stations. |  | Climax | Longneck | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07214 | 2016-06-30 |  | 138 | 7.5 | 4.2 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/31/2017 to 6/30/2016 | 17TPIT0000 | Farmersville West 138KV Station | Purchase and install a 42MVA 138KV - 22kV transformer, three 138kV breakers, construct 138kV ring bus, two distribution breakers, install control house and relays to accommodate both transmission and distribution positions in Farmersville West Substation Site to feed the Princeton South Substation and connect to ONCOR's Royce City to Climax transmission line. |  | Farmersville West | Farmersville West | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07212 | 2016-06-30 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 10/31/2016 to 7/1/2016 | 16TPIT0000 | Del Sol : Add 25% Series Capacitor Compensation | Construct 345 kV series compensated line from Lobo to Rio Bravo to Del Sol to North Edinburg | Schedule and Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 065 - 0273 | AEP/ETT | Paul Hassink 918-599-2653 | 629 | 2016-07-01 |  | 345 | 0 | 0 | 0 | +368.5 | HIDALGO |  | Tier 3 | 2011-03-10 | On-going |  | 80355 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
New Project | New Project | 16TPIT0017 | Rio Bravo: Add 25% Series Capacitor Compensation | Construct 345 kV series compensated line from Lobo to Rio Bravo to Del Sol to North Edinburg | NEW |  |  | Planned | 065 - 0273 | AEP/ETT | Paul Hassink 918-599-2653 | 630 | 2016-07-01 |  | 345 | 0 | 0 | 0 | +368.5 | WEBB |  | Tier 3 | 2011-03-10 | 2011-08-12 | PENDING | 80220 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
Old Project | Change in Service Date. Changed from 10/31/2016 to 7/1/2016 | 11TPIT0002 | Lobo to North Edinburg: Construct 345 kV line | Construct 345 kV series compensated line from Lobo to Rio Bravo to Del Sol to North Edinburg | Title, Schedule, & Cost Update | Lobo | North Edinburg | Planned | 065 - 0273 | AEP/ETT/TCC | Paul Hassink 918-599-2653 | 3421 | 2016-07-01 |  | 345 | 163 | 0 | 0 | 0 | WEBB | HIDALGO | Tier 1 | 2011-03-10 | On-going |  | 80219, 80220, 80355, 8383 | N | N |  | SSWG CASES TO BE UPDATED WITH SEPT TPIT WINDOW
New Project | New Project | 16TPIT0014 | Sanderson T Line Rebuild | Rebuild Sanderson T Line |  | Sanderson | Sanderson | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE075AA | 2016-08-31 |  | 69 | 0 | 0 | 0 | 0 | Terell | Terrell | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 5/31/2016 to 8/31/2016 | 16TPIT0003 | Build 138kV Longneck-Princeton South Line to finish Princeton S. Ring | The project will consist of building 3.5 miles of 138kV transmission single pole slim line type construction. This will is one segment of an ongoing project to install a 138kV transmission loop and construct two new substation and improve to existing station to better serve the customers of Princeton Texas and the surrounding communities. Complete the ring bus in Princeton South Substation |  | Longneck | Princeton | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE07314 | 2016-08-31 |  | 138 | 3.5 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  |  | N | N
Old Project | Change in Service Date. Changed from 12/1/2015 to 12/1/2016 | 12TPIT0025 | Refugio - Tatton: Rebuild Irreparable 69 kV Line | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV, 93 MVA, auto. Build new 69 kV line from Melon Creek to Tatton. Rebuild 69 kV line from Refugio to Tatton. | Date change | Refugio | Tatton | Planned | 100 - 0100 | AEP/TCC | Paul Hassink 918-599-2653 | 2025 and 2027 | 2016-12-01 |  | 69 | 0 | 13.9 | 0 | 0 | REFUGIO | ARANSAS | Tier 4 |  |  |  |  | Y | N
Old Project | No Change | 16TPIT0009 | Five Points to Westside - 138 kV Transmission Line Rebuild | Rebuild 3.8 miles of 138 kV transmission line from Five Points to Westside and ensure a minimum conductor rating of 331 MVA | [5 empty] | CPS | Blake Williams | T-0195 | 2016-12-01 |  | 138 | 0 | 3.8 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5150 5490 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 5/1/2013 to 4/1/2017 | 13TPIT0045 | Blumenthal | Construct a new 8.4-mile 138 kV transmission line from a tap point on the Kendall CTEC (7147) - Mountain Top (7148)138 kV transmission line to the new Blumenthal substation (7418). | Delayed from initial May 2013 in-service date | Blumenthal | Kendall CTEC/Mountain Top | Planned |  | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2017-04-01 |  | 138 | 8.4 | 0 | 0 | 0 | KENDALL |  | Tier 2 |  |  |  | SEE PROJECT DESCRIPTION | Y | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2017 | 14TPIT0010 | Handley - Pantego 138 kV line | Upgrade existing line | Studies indicate timing of project should be changed | Handley | Pantego | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5155-E | 2017-05-01 |  | 138 | 0 | 3.8 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 1951, 2247 | Y | N
Old Project | No Change | 11TPIT0008 | Rainey St 138kV substation | Establish a new 138kV Rainey St substation with (2) 50MVA transformers and cut into existing Ckt 1015 (Pedernales to Seaholm). |  | Rainey St Substation | Rainey St Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P158 PLAN_117_P166 PLAN_117_P167 | 2017-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9261 | Y | N
Old Project | No Change | 11TPIT0011 | Northeast 138kV Substation | Establish a 138kV substation with (2) 30MVA transformers and 4 distribution circuits with underground get-a-ways. The station will cut into existing Gilleland - Techridge line. | Original Project title is "East Substation" | Northeast Substation | Northeast Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P142 PLAN_117_P143 PLAN_117_P144 | 2017-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9195 | Y | N
Old Project | Change in Service Date. Changed from 10/31/2016 to 10/31/2017 | 13TPIT0005 | Del Sol: Build 345 kV station | Construct 345 kV line from Frontera to Del Sol | Schedule and Cost Updateand Removed "From an To" info because this is a Station |  |  | Planned | 508 - 0507 | AEP/ETT | Paul Hassink 918-599-2653 | 631 | 2017-10-31 |  | 345 | 0 | 0 | 0 | 0 | HIDALGO |  | Tier 3 | 2011-03-10 | On-going |  | 80355 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | Change in Service Date. Changed from 10/31/2016 to 10/31/2017 | 13TPIT0007 | Frontera to Del Sol: Construct 345 kV Line | Construct 345 kV line from Frontera to Del Sol | Schedule Update | Frontera | Del Sol | Planned | 508 - 0507 | AEP/ETT | Paul Hassink 918-599-2653 | 288 | 2017-10-31 |  | 345 | 12.4 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2011-03-10 | On-going |  | 80119, 80355 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | Change in Service Date. Changed from 10/31/2016 to 10/31/2017 | 08TPIT0005 | Frontera: Build 345 kV station with 345/138 kV autotransformer | Construct 345 kV line from Frontera to Del Sol | Schedule Updateand Removed "From an To" info because this is a Station |  |  | Planned | 508 - 0507 | AEP/ETT/TCC | Paul Hassink 918-599-2653 | 1277 | 2017-10-31 |  | 345 | 0 | 0 | 675 | 0 | HIDALGO |  | Tier 3 | 2011-03-11 | 2011-08-12 | ENDORSEMENT DEFERRED | 80119, 8980 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 13TPIT0001 | Ranchito: Build 138 kV station with 138 KV Auto and Ring Bus | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer | Removed "From an To" info because this is a Station |  |  | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 1329 | 2017-12-01 |  | 138 | 0 | 0 | 187 | 0 | CAMERON |  | Tier 4 |  |  |  | 8376 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 12TPIT0002 | South McAllen 345 kV Station Upgrade and build 138kV line to South McAllen 138kV | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | South McAllen 345 kV | South McAllen 138 kV | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 1276 | 2017-12-01 |  | 345 | 0 | 0.5 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 80122, 8371 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 08TPIT0006 | South McAllen, new SS with 345/138 kV autotransformer | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen | Removed "From an To" info because this is a Station |  |  | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 293 | 2017-12-01 |  | 345 | 0 | 0 | 675 | 0 | HIDALGO |  | Tier 3 |  |  |  | 80122 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 13TPIT0000 | Frontera to South McAllen, build 345 KV line | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | Frontera | South McAllen | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 292 | 2017-12-01 |  | 345 | 12.18 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 |  |  |  | 80119, 80122 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 00TPITno15 | Ranchito, New SS with 345/138 kV autotransformer | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer | Removed "From an To" info because this is a Station |  |  | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 1059 | 2017-12-01 |  | 345 | 0 | 0 | 675 | 0 | CAMERON |  | Tier 3 |  |  |  | 8364 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 11TPIT0036 | Caddo - New Substation | Construct a new 69-13.09x26.18-KV, 10 MVA substation | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2017-12-31 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 00TPITno19 | Ranchito to South McAllen, new 345 kV line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | Ranchito | South McAllen | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 295 | 2017-12-31 |  | 345 | 38 | 0 | 0 | 0 | CAMERON | HIDALGO | Tier 1 |  |  |  | 8364, 80122 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | Change in Service Date. Changed from 3/30/2017 to 3/30/2018 | 06TPIT0068 | Hamilton Road to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System | Schedule Update | Hamilton Road | Picacho | Conceptual | 301 - 0449 | AEP/TCC | Paul Hassink 918-599-2653 | 1544 | 2018-03-30 |  | 138 | 0 | 8.67 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | No Change | 13TPIT0002 | Villa Cavazos to Military Highway: Reconductor 138 KV Line | Construct 345 kV line from LaPalma to Villa Cavazos to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | Villa Cavazos | Military Highway | Conceptual | 236 - 0277 | AEP/TCC | Paul Hassink 918-599-2653 | 1332 | 2018-03-31 |  | 138 | 0 | 10 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  | 80229, 8339 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | Change in Service Date. Changed from 4/30/2017 to 4/30/2018 | 06TPIT0084 | Hamilton Road to Del Rio reconductor 138 kV line | Reconductor Del Rio 138 kV System | Schedule Update | Hamilton Road | Del Rio | Conceptual | 301 - 0449 | AEP/TCC | Paul Hassink 918-599-2653 | 1545 | 2018-04-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | No Change | 06TPIT0092 | Wichita Falls Switch - Wichita Falls Basin 69 kV line | Upgrade existing 69 kV line |  | Wichita Falls Switch | Wichita Falls Basin | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168A-E | 2018-05-01 |  | 69 | 0 | 1 | 0 | 0 | ARCHER | WICHITA | Tier 4 |  |  |  | 1449, 1508 | N | N
Old Project | No Change | 08TPIT0110 | Temple - Little River 69 kV line | Rebuild existing 69 kV line |  | Temple | Little River | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R097-E | 2018-05-01 |  | 69 | 0 | 7.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3645, 3644 | N | N
Old Project | No Change | 09TPIT0068 | W. Weatherford - Weatherford 69 kV line | Rebuild existing 69 kV line |  | W. Weatherford | Weatherford | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R515-E | 2018-05-01 |  | 69 | 0 | 7.5 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 1586, 1585 | N | N
Old Project | No Change | 10TPIT0027 | West Batesville, Install 138 kV ring bus | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus | Removed "From an To" info because this is a Station |  |  | Conceptual | 383 - 0560 | AEP/ETT | Paul Hassink 918-599-2653 | 2168 | 2018-05-01 |  | 138 | 0 | 0 | 0 | 0 | ZAVALA |  | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | N | N
Old Project | No Change | 10TPIT0028 | Escondido to West Batesville, build 138 kV Line | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus |  | Escondido | West Batesville | Conceptual | 383 - 0560 | AEP/ETT | Paul Hassink 918-599-2653 | 2169 | 2018-05-01 |  | 138 | 46.2 | 0 | 0 | 0 | MAVERICK | ZAVALA | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | N | Y
Old Project | No Change | 12TPIT0003 | LaPalma to Villa Cavazos: Reconductor 138 KV Line | Construct 345 kV line from LaPalma to Villa Cavazos to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | La Palma | Villa Cavasos | Conceptual | 236 - 0277 | AEP/TCC | Paul Hassink 918-599-2653 | 1519 | 2018-05-01 |  | 138 | 0 | 10.5 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  | 8314, 80229 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 06TPIT0036 | Ennis Switch - Ennis 138 kV line | Upgrade existing 138 kV line |  | Ennis Switch | Ennis | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M280-E | 2018-05-01 |  | 138 | 0 | 6.32 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2324, 2326 | N | N
Old Project | No Change | 06TPIT0042 | Lake Wichita Switch - Wichita Falls Switch 69 kV line | Upgrade existing 69 kV line |  | Lake Wichita Switch | Wichitia Falls Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168-E | 2018-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | ARCHER | WICHITA | Tier 4 |  |  |  | 1447, 1449 | N | N
Old Project | No Change | 06TPIT0047 | Elkton - Tyler West 138 kV line | Upgrade existing 138 kV line |  | Elkton | Tyler | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R323-E | 2018-05-01 |  | 138 | 0 | 4.98 | 0 | 0 | SMITH | SMITH | Tier 4 |  |  |  | 3106, 3139 | N | N
Old Project | No Change | 07TPIT0012 | Trinity Switch - Richland 138 kV line | Upgrade existing 138 kV line |  | Trinity Switch | Richland | Conceptual | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5069-E | 2018-05-01 |  | 138 | 0 | 0.5 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2096, 2100 | N | N
Old Project | No Change | 07TPIT0115 | Elgin Switch - Taylor 138 kV line | Upgrade existing 138 kV line |  | Elgiin Switch | Taylor | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R026-E | 2018-05-01 |  | 138 | 0 | 11.4 | 0 | 0 | BASTROP | BASTROP | Tier 4 |  |  |  | 3650, 3658 | N | N
Old Project | No Change | 07TPIT0119 | Lavon Switch - Allen Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | Lavon Switch | Allen Switch | Conceptual | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375B-E | 2018-05-01 |  | 138 | 8.9 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2475, 2477, 2509 | N | N
Old Project | No Change | 07TPIT0122 | Royse - Dalrock 138 kV line | Upgrade existing 138 kV line |  | Royse | Dalrock | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3035-E | 2018-05-01 |  | 138 | 0 | 6.8 | 0 | 0 | ROCKWALL | ROCKWALL | Tier 4 |  |  |  | 2472, 2733, 2735 | N | N
Old Project | No Change | 07TPIT0138 | Oates (GPL) - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  | Oats (GPL) | Garland Bobtown Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M322-E | 2018-05-01 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 831, 2739 | N | N
Old Project | No Change | 08TPIT0007 | Austin Ranch - Hebron 138 kV line | Upgrade existing 138 kV line |  | Austin Ranch | Hebron | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3002-E | 2018-05-01 |  | 138 | 0 | 0.7 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 2376, 2377 | N | N
Old Project | No Change | 08TPIT0069 | Lake Creek - East Waco 138 kV line | Upgrade existing 138 kV line |  | Lake Creek | East Waco | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R470-E | 2018-05-01 |  | 138 | 0 | 10.5 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3410, 3452, 3438 | N | N
Old Project | No Change | 08TPIT0111 | Lufkin Switching Station - Texas Foundries Tap 138 kV line | Upgrade existing 138 kV line |  | Lufkin Switching Station | Texas Foundries Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R389-E | 2018-05-01 |  | 138 | 0 | 0.73 | 0 | 0 | ANGELINA | ANGELINA | Tier 4 |  |  |  | 3326, 3327, 3328 | N | N
Old Project | No Change | 09TPIT0043 | Coppell - North Lake 138 kV line | Construct 138 kV line |  | Coppell | North Lake | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M549-E | 2018-05-01 |  | 138 | 4.8 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2015, 2386 | N | N
Old Project | No Change | 09TPIT0046 | N. Midlothian - Midlothian TXI Tap 138 kV line | Upgrade existing 138 kV line |  | N. Midlothian | Midlothian TXI Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3031-E | 2018-05-01 |  | 138 | 0 | 6.2 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2310, 2311, 2313 | N | N
Old Project | No Change | 09TPIT0050 | Rowlett - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  | Rowlett | Garland Bobtown Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3032-E | 2018-05-01 |  | 138 | 0 | 4.1 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2736, 2739 | N | N
Old Project | No Change | 09TPIT0051 | Salado Switch - Cedar Valley Switch (BEC) 138 kV line and switching stations | Establish two new 138 kV switching stations and connect them with a new 138 kV line |  | Saldo Switch | Cedar Valley Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R469-E | 2018-05-01 |  | 138 | 7 | 0 | 0 | 0 | BELL | BELL | Tier 2 |  |  |  | 117, 3640 | N | N
Old Project | No Change | 09TPIT0066 | Boggy Creek 138 kV Switching Station and associated line | Construct 138 kV switching station and add second circuit to a 138 kV line |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R488-E | 2018-05-01 |  | 138 | 3.5 | 0 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3424, 3415, 3425, 13645 | N | N
Old Project | No Change | 09TPIT0067 | Bonham Switching Station 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R516-E | 2018-05-01 |  | 138 | 0 | 0 | 100 | 0 | FANNIN |  | Tier 4 |  |  |  | 1760, 1761 | N | N
Old Project | No Change | 10TPIT0009 | Trinity Switch - Hurst 138 kV line | Upgrade existing 138 kV line |  | Trinity Switch | Hurst | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5040-E | 2018-05-01 |  | 138 | 0 | 4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2096, 2115 | N | N
Old Project | No Change | 10TPIT0034 | Leon Switch #2 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R517-E | 2018-05-01 |  | 138 | 0 | 0 | 100 | 0 | EASTLAND |  | Tier 4 |  |  |  | 1624, 1626 | N | N
Old Project | No Change | 11TPIT0027 | East Richardson Switch - Ben Davis Switch (TMPA) 138 kV line | Create a new 138 kV line by reconfiguring existing lines |  | East Richardson Switch | Ben Davis Switch | Conceptual | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375D-E | 2018-05-01 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | DALLAS | Tier 4 |  |  |  | 968, 2690 | N | N
Old Project | No Change | 11TPIT0028 | Allen Switch - West Plano Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | Allen Switch | West Plano Switch | Conceptual | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375C-E | 2018-05-01 |  | 138 | 3.5 | 0 | 0 | 0 | COLLIN | COLLIN | Tier 4 |  |  |  | 2510, 2691, 2673 | N | N
Old Project | No Change | 14TPIT0029 | Lake Creek - Robinson 138 kV line | Rebuild 138 kV line |  | Lake Creek | Robinson | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R476 | 2018-05-01 |  | 138 | 0 | 8.3 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3410, 3567 | N | N | 2007-R8
Old Project | No Change | 00TPITno06 | Loma Alta - Ranchito or la Palma 345-kV line | Install 345-kV line from Loma Alta to La Palma or Ranchito |  | La Palma or Ranchito Substation | Loma Alta Substation | Conceptual |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2018-05-01 |  | 345 | 25 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 2 | 2011-05-03 | On-going |  |  | N | N
Old Project | No Change | 00TPITno07 | Loma Alta - Rio Hondo 345-kV line | Install 345-kV line from Loma Alta to Rio Hondo |  | Loma Alta Substation | Rio Hondo Substation | Conceptual |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2018-05-01 |  | 345 | 35 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 2 |  |  |  |  | N | N
Old Project | No Change | 00TPITno10 | Loma Alta 345kV station and autotransformer | Construct a 345 substation and connect to the existing Loma Alta 138 substation. |  | New 345-kV Substation | Existing 138-kV Substation | Conceptual |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2018-05-01 |  | 345 | 0 | 0 | 600 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | N | N
Old Project | No Change | 00TPIT0004 | DeCordova - Benbrook 345 kV line upgrade | Upgrade existing 345 kV line |  | DeCordova | Benbrook | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5034-E | 2018-05-01 |  | 345 | 0 | 27 | 0 | 0 | HOOD | TARRANT | Tier 4 |  |  |  | 1873, 1890 | N | N
Old Project | No Change | 07TPIT0001 | Liggett - Trinity Switch 345 kV line | Construct Liggett - Trinity 345 kV line |  | Liggett | Trinity Switch | Conceptual | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5015-E | 2018-05-01 |  | 345 | 12.8 | 0 | 0 | 0 | DALLAS | TARRANT | Tier 2 |  |  |  | 2095, 2097 | N | N
Old Project | No Change | 07TPIT0002 | Trinity Switch 345/138 kV autotransformer | Create Trinity Switch and install a 600 MVA 345/138 kV autotransformer |  |  |  | Conceptual | M5015-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5014-E | 2018-05-01 |  | 345 | 0 | 0 | 600 | 0 | TARRANT |  | Tier 4 |  |  |  | 2096, 2097 | N | N
Old Project | No Change | 07TPIT0118 | Lavon 345/138 kV Switching Station | Construct 345/138 kV switching station |  |  |  | Conceptual | M375B, M375C | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375A-E | 2018-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  | Tier 4 |  |  |  | 2475, 2476 | N | N
Old Project | No Change | 08TPIT0071 | North Lake 345/138 kV autotransformer | Install a 345/138 kV autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3020-E | 2018-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2334, 2333 | N | N
Old Project | Change in Service Date. Changed from 5/30/2017 to 5/30/2018 | 06TPIT0083 | Del Rio to Buena Vista, reconductor 138 kV line | Reconductor Del Rio 138 kV System | Schedule Update | Del Rio | Buena Vista | Conceptual | 301 - 0449 | AEP/TCC | Paul Hassink 918-599-2653 | 1546 | 2018-05-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | No Change | 00TPITno14 | LaPalma to Ranchito, new 345 kV line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | La Palma | Ranchito | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 1060 | 2018-05-31 |  | 345 | 10 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 2 |  |  |  | 8317, 8364 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 18TPIT0000 | Ranchito to Villa Cavazos: Build Double circuit 138kV Line | Construct 345 kV line from LaPalma to Villa Cavazos to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | Ranchito | Villa Cavasos | Conceptual | 236 - 0277 | AEP/ETT | Paul Hassink 918-599-2653 | 1333 | 2018-06-01 |  | 138 | 5 | 0 | 0 | 0 | HIDALGO | CAMERON | Tier 2 |  |  |  | 8376, 80229 | N | N |  | INSV DATE BEYOND ACTIVE SSWG DSB CASES
Old Project | No Change | 12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV OW Sommers to Kirby line |  | Sulpher Springs | OW Sommers/Kirby | Conceptual |  | CPS | Blake Williams | S-0385 | 2018-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5416 | Y | No |  | There are no transformers associated with this project
Old Project | Change in Service Date. Changed from 6/30/2017 to 6/30/2018 | 07TPIT0083 | Picacho to CFE, construct new 138 kV line | Convert Amistad to CFE Amistad 12.5 kV distribution to 138 kV line | Update Schedule | Picacho | CFE | Conceptual | 301 - 0449 | AEP/ETT | Paul Hassink 918-599-2653 | 1548 | 2018-06-30 |  | 138 | 8.8 | 0 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | Y
Old Project | Change in Service Date. Changed from 6/30/2017 to 6/30/2018 | 06TPIT0082 | Buena Vista to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System | Schedule Update | Buena Vista | Picacho | Conceptual | 301 - 0449 | AEP/TCC | Paul Hassink 918-599-2653 | 1547 | 2018-06-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y | N
Old Project | Change in Service Date. Changed from 6/30/2016 to 6/30/2018 | 10TPIT0062 | Weil Road (Marion South) - New Substation | Build a 138-26.18 kV 40 MVA substation on the GVEC Marion(7178)-Cibolo(7608) 138 kV transmission line near the Marion Interchange |  | Weil Road | Marion/Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2018-06-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 11TPIT0037 | Santa Clara - New Substation | Build a new 138-26.18 kV 40 MVA substation on the GVEC McQueeney(7606)-Cibolo(7608) 138 kV transmission line |  | Santa Clara | McQueeney/Cibolo | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2018-06-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 18TPIT0001 | Wiederstein Substation | Replace T1, 20 MVA with a 40 MVA 138-26.18 kV transformer | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2018-12-15 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | Change in Service Date. Changed from 5/1/2013 to 5/1/2019 | 12TPIT0019 | Pleasant Valley second 138/69 kV autotransformer | Install second 138/69 kV autotransformer | Studies indicate timing of project should be changed |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R555-E | 2019-05-01 |  | 138 | 0 | 0 | 100 | 0 | WICHITA |  | Tier 4 |  |  |  | 1450, 1451 | N | N
Old Project | No Change | 13TPIT0062 | Cedar Hill Switch second 345/138 kV autotransformer | Install autotransformer |  |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4071-E | 2019-05-01 |  | 345 | 0 | 0 | 504 | 0 | DALLAS |  | Tier 4 |  |  |  | 2420, 2422, 2421 | N | N
Old Project | No Change | 19TPIT0000 | Weser substation | Replace 5.6 MVA with 69-13.09 kV, 20 MVA transformer | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2019-06-15 |  | 69 | 0 | 0 | 0 | 0 | GOLIAD |  | Tier 4 |  |  |  | See Project Title | Y | N
Old Project | Change in Service Date. Changed from 5/15/2016 to 5/1/2020 | 09TPIT0024 | Electra - KMA Tap 69 kV line | Upgrade existing 69 kV line | Studies indicate timing of project should be changed | Electra | KMA Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R185-E | 2020-05-01 |  | 69 | 0 | 9.9 | 0 | 0 | WICHITA | WICHITA | Tier 4 |  |  |  | 1538, 1536 | N | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2020 | 14TPIT0009 | Odessa North - North Cowden 69 kV line | Upgrade existing line | Studies indicate timing of project should be changed | Odessa North | North Cowden | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8008-E | 2020-05-01 |  | 69 | 0 | 12.4 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 1259, 1123 | N | N | 2009-R4
Old Project | Change in Service Date. Changed from 5/15/2016 to 5/1/2020 | 07TPIT0014 | Plano West - Richardson Tap 138 kV line | Upgrade existing 138 kV line | Studies indicate timing of project should be changed | Plano West | Richardson Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M364-E | 2020-05-01 |  | 138 | 0 | 1.9 | 0 | 0 | COLLIN | DALLAS | Tier 4 |  |  |  | 2673, 2685 | N | N
Old Project | Change in Service Date. Changed from 5/1/2017 to 5/1/2020 | 08TPIT0109 | Payne - Collin Switching Station 138 kV line | Rebuild existing 138 kV line | Studies indicate timing of project should be changed | Payne | Collin Switching Station | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R519-E | 2020-05-01 |  | 138 | 0 | 31.75 | 0 | 0 | GRAYSON | COLLIN | Tier 3 | 2008-01-07 |  |  | 1758, 1757, 2350, 2366, 2349, 2364, 2370 | N | N | 2009-R12
Old Project | Change in Service Date. Changed from 5/1/2017 to 5/1/2020 | 09TPIT0047 | N. Waco - NE. Waco 138 kV line | Upgrade existing 138 kV line | Studies indicate timing of project should be changed | N. Waco | NE. Waco | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R477-E | 2020-05-01 |  | 138 | 0 | 1.9 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3551, 3552 | N | N
Old Project | Change in Service Date. Changed from 5/1/2016 to 5/1/2020 | 10TPIT0019 | Everman - Cleburne Switch 138 kV line sections | Upgrade existing 138 kV line | Studies indicate timing of project should be changed | Everman | Cleburne Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3034-E | 2020-05-01 |  | 138 | 0 | 8.5 | 0 | 0 | TARRANT | JOHNSON | Tier 4 |  |  |  | 2279, 2210, 2209, 2208, 1883 | N | N
Old Project | Change in Service Date. Changed from 5/1/2017 to 5/1/2020 | 10TPIT0053 | Kaufman South 138 kV capacitors | Install 138 kV capacitors | Studies indicate timing of project should be changed |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3064-E | 2020-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | KAUFMAN |  | Tier 4 |  |  |  | 2728 | N | N
Old Project | Change in Service Date. Changed from 5/1/2017 to 5/1/2020 | 10TPIT0054 | Royse 138/69 kV autotransformer | Install larger autotransformer | Studies indicate timing of project should be changed |  |  | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3065-E | 2020-05-01 |  | 138 | 0 | 0 | 120 | 0 | ROCKWALL |  | Tier 4 |  |  |  | 2462, 2463 | N | N
Old Project | Change in Service Date. Changed from 5/1/2016 to 5/1/2020 | 11TPIT0012 | Euless - Grapevine Ball Street 138 kV line | Upgrade existing 138 kV line | Studies indicate timing of project should be changed | Euless | Grapevine Ball Street | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5131-E | 2020-05-01 |  | 138 | 0 | 5.9 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2016, 2021 | N | N
Old Project | Change in Service Date. Changed from 5/1/2016 to 5/1/2020 | 11TPIT0033 | Saginaw - American MFG Tap 138 kV line | Upgrade existing 138 kV line | Studies indicate timing of project should be changed | Saginaw | American MFG Tap | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5070-E | 2020-05-01 |  | 138 | 0 | 1.37 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2146, 1957 | N | N
Old Project | Change in Service Date. Changed from 5/1/2014 to 5/1/2020 | 07TPIT0073 | Venus - Webb 345 kV line | Upgrade existing 345 kV line | Studies indicate timing of project should be changed | Venus | Webb | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5098-E | 2020-05-01 |  | 345 | 0 | 11.3 | 0 | 0 | ELLIS | DALLAS | Tier 4 |  |  |  | 1906, 1904 | N | N
Old Project | No Change | 20TPIT0000 | Parkway Substation | Replace T1, 20 MVA with a 40 MVA 138-13.09 kV transformer | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2020-05-15 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 09TPIT0011 | Cagnon to Hill Country - 345kV 2nd Circuit | Build second 345 kV line from Cagnon to Hill Country. The circuit will be installed on existing transmission structures |  | Cagnon | Hill Country | Conceptual |  | CPS | Blake Williams | T-0053 | 2020-06-01 |  | 345 | 19.5 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5056 5211 | N | No |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0006 | Olmos(7613) - New Substation | Build a 138-13.09 kV 20 MVA substation on the Olmos switching station site |  | Olmos | Olmos Switching Station | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2020-11-30 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | Y | N
Old Project | Change in Service Date. Changed from 6/1/2014 to 12/1/2020 | 14TPIT0033 | Muenster to Red River | Add 60 MVA 138/69 kV auto at Munester. Build 11 miles of 795 ACSR line to Red River. |  | Muenster | Red River | conceptual |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com | 09033 | 2020-12-01 |  | 69 | 11 | 0 | 60 | 0 | COOKE | COOKE | Tier 2 |  |  |  | 694, 694, 735 | Y | N
Old Project | Change in Service Date. Changed from 5/1/2016 to 5/1/2022 | 07TPIT0069 | Sterrett - Sardis 138 kV line | Upgrade existing 138 kV line | Studies indicate timing of project should be changed | Sterrett | Sardis | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M361-E | 2022-05-01 |  | 138 | 0 | 1.95 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 2317, 203 | N | N
Old Project | Change in Service Date. Changed from 5/1/2016 to 5/1/2022 | 07TPIT0234 | Collin Switch - NW. Carrollton 345 kV line | Upgrade existing 345 kV line | Studies indicate timing of project should be changed | Collin Switch | NW. Carrollton | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3061-E | 2022-05-01 |  | 345 | 0 | 19.3 | 0 | 0 | COLLIN | DALLAS | Tier 4 | 2006-10-01 | 2007-02-01 | N/A | 2372, 2361 | N | N |  | The ERCOT Staff determined this project is not economically justified in their February 2007 study.
Old Project | No Change | 22TPIT0000 | Parkway Substation | Replace T2, 20 MVA with a 40 MVA 138-13.09 kV transformer | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2022-05-15 |  | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N | N
Old Project | No Change | 12TPIT0078 | Southeast Nacogdoches - Lufkin Switch 345 kV line | Construct new 345 kV line, add second circuit to existing structures and add 345 kV circuit breakers at existing switching stations |  | Southeast Nacogdoches | Lufkin Switch | Conceptual |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R862 | 2022-12-01 |  | 345 | 8 | 13 | 0 | 0 | NACOGDOCHES | ANGELINA | Tier 2 | 2008-07-01 |  | 2008-09-01 | 3117, 3119 | N | N | 2007-E4

## CompletedTPIT09012011NoCost
SEPTEMBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) COMPLETED PROJECTS As Of 09/01/2011.
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location for Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional)
08TPIT0050 | Gustine to Hamilton Rebuild | Rebuild Hamilton to Gustine 69kv line with 795 and 138kv construction | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-05-01 | 2009-01-01 | 69 | 0 | 17.1 | 0 | 0 | COMANCHE | HAMILTON |  |  |  |  | 258, 279 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0062 | Bell County to Schwertner Rebuild | Rebuild Bell County to Schwertner 69kv line | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-11-01 | 2009-01-01 | 69 | 0 | 13.7 | 0 | 0 | BELL | WILLIAMSON |  |  |  |  | 133114122 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0040 | Temple Switch - Bell County 138 kV line | Upgrade existing 138 kV line |  |  |  |  | R494 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R704A-E | 2010-05-01 | 2009-01-01 | 138 | 0 | 8.2 | 0 | 0 | WILLIAMSON | WILLIAMSON |  | 2006-11-01 |  | 2007-07-01 | 3666, 3673, 3658 | Y
09TPIT0164 | Scurry Chevron terminal equipment | Replace terminal equipment | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R844-E | 2009-01-01 | 2009-01-01 | 138 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | 1312 | Y
08TPIT0196 | Construct Bender 138kV Substation | Serve substation by looping into Ckt.86 Barhill to Crosby | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-11-30 | 2009-01-05 | 138 | 0.2 | 0 | 0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 40155 | Y |  |  | No transformer capacity added.
08TPIT0073 | Convert Cardinal Lane substation and Zilker Demolition | Rebuild Cardinal Lane substation as a 138kV substation and decommission Zilker substation and relocate the Seaholm cap bank to Cardinal Lane substation. | The final 4th unit has been installed and the circuit breakers are also installed. |  |  |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | 3230_117_2884 3240_117_4884 3240_117_2859 3240_117_4859 PLAN_117_P133 PLAN_117_P139 | 2009-01-01 | 2009-01-09 | 138 | 0 | 0 | 90 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9120,9179,9299, 9132 | Y
08TPIT0117 | New Gulf tap - Pledger tap - West Columbia Ckt.04 | Raise conductors, partially rebuild Ckt.04 and upgrade limiting equipment at West Columbia to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-31 | 2009-01-16 | 138 | 0 | 27.47 | 0 | 0 | WHARTON | WHARTON | Tier 4 |  |  |  | 43340, 43011, 43120, 43380 | Y |  |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added.
08TPIT0108 | Lufkin E. - Lufkin S. 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R388-WACF | 2009-01-01 | 2009-01-23 | 138 | 0 | 6.3 | 0 | 0 | ANGELINA | ANGELINA | Tier 4 |  |  |  | 3326 | Y
08TPIT0155 | Jefferson - College Tap - Pasadena Ckt.06 | Reconductor 138kV Ckt.06 Jefferson to College Tap to Pasadena to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-31 | 2009-01-24 | 138 | 0 | 4.73 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41240, 42312 | Y |  |  | No transformer capacity added.
09TPIT0205 | Austrop SPS | Establish a Special Protection System for the Austrop 138/345kV autotransformers. | For the overload of one Austrop autotransformer due to the loss of the other Austrop autotransformer, the SPS will open circuit 921 or circuits 921 and 920 if necessary |  |  |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com |  | 2009-01-29 | 2009-01-29 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  |  | 9040, 7328 | Y
07TPIT0230 | Tyler GE - Tyler Omen Road 138 kV line | Rebuild existing 138 kV line |  |  |  |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R386-WACF | 2009-05-01 | 2009-01-30 | 138 | 0 | 2.4 | 0 | 0 | SMITH | SMITH | Tier 4 | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3213, 3212 | Y
06TPIT0179 | West Denton Sub: Expand 138 bus, add terminal for DME's line to R.G. Wells Sub | Expand 138 kV breaker and a half substation for new line to Denton's RD Wells Interchange and Substation | Delayed due to problems with site acquisition |  |  |  |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05006 | 2008-12-08 | 2009-02-01 | 138 | 0 | 0 | 0 | 0 | DENTON |  | Tier 4 |  |  |  | 986 | Y
08TPIT0098 | Gabriel to Schwertner Rebuild | Rebuild existing Gabriel to Schwertner | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-05-01 | 2009-02-17 | 69 | 0 | 9.4 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | 122, 123, 7345 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0088 | TCC - New 138kV Substation | Install new 138kV substation and connect to AMD |  |  |  |  | T-0106 | CPS | PM: Janna Junkin | S-0269 | 2009-02-28 | 2009-02-19 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5423 | Y |  |  | Underground transmission being installed at customer cost.
09TPIT0059 | Lago Vista-Nameless | Replace under-rated limiting line terminal equipment at Lago Vista to increase Lago Vista (7352)-Nameless (7526) to the conductor's rating. | [5 empty] | PEC | Randy Buchanan (830) 868-6058 |  | 2010-12-01 | 2009-02-19 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0046 | Tyler NE - Tyler East 138 kV line | Upgrade existing 138 kV line |  |  |  |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R337B-WACF | 2009-05-01 | 2009-02-25 | 138 | 0 | 3.74 | 0 | 0 | SMITH | SMITH | Tier 4 | 2007-09-11 | 2008-01-01 | 2008-03-01 | 3210, 3211 | Y
06TPIT0098 | Newman 138 kV new switching substation and installing a 138 kV/69 kV autotransformer (168 MVA) | Install a 138 kV/69 kV autotransformer (168 MVA) at Newman substation | [5 empty] | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2009-03-02 | 2009-03-02 | 138 | 0 | 0 | 168 | 0 | DALLAS |  | Tier 4 |  |  |  | 849, 814 | Y
06TPIT0100 | Newman-Walnut line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  | Switch 928 at Newman | Switch 7422 at Walnut | Completed |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2009-03-02 | 2009-03-02 | 138 | 0 | 0.55 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 814, 823 | Y | N
09TPIT0154 | Lake Creek terminal equipment | Replace terminal equipment on circuit to Temple Pecan Creek. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R725-WACF | 2009-05-01 | 2009-03-06 | 138 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3410 | Y
09TPIT0181 | Lake Creek terminal equipment | Replace terminal equipment on circuit to Temple Switch. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R730-WACF | 2009-05-01 | 2009-03-06 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3409 | Y
07TPIT0076 | Friendship-Escarpment-Manchaca | Construct a new 795 ACSR 138-kV transmission line (approximately eight miles) between the Friendship(7507) and Manchaca(7504) substations. Construct a new 138-26.18-kV 22.4-MVA distribution substation to serve the load requirements in the area south of Austin. The new Escarpment(7672) substation will be cut midway into the new 138-kV Friendship-Manchaca transmission line. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | 1006535 | 2009-03-16 | 2009-03-26 | 138 | 8 | 0 | 0 | 0 | TRAVIS | HAYS | Tier 2 |  |  |  | SEE PROJECT DESCRIPTION | Y |  |  | The name of the new substation was changed from HWY 45 to Escarpment.
09TPIT0162 | Odessa terminal equipment | Replace terminal equipment | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R871-WACF | 2009-05-01 | 2009-03-26 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1127 | Y
07TPIT0172 | Freer 69 kV, add 1-7.2 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | IN-SERVICE |  |  |  | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2035 | 2009-03-27 | 2009-03-27 | 69 | 0 | 0 | 0 | 7.2 | Val VERDE | Val VERDE | Tier 4 |  |  |  |  | Y
09TPIT0198 | Alliance Substation | Replace terminal equipment at substation in the Roanoke Switch - Eagle Mountain 345 kV line. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C031-E | 2009-06-01 | 2009-03-27 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  | 1855 | Y |  |  | CREZ default project
07TPIT0262 | Abilene South to Putnam, ugrades to improve ratings | Abilene South to Putnam 138 kV line, upgrades to improve rating | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2171 | 2009-03-31 | 2009-03-31 | 138 | 0 | 35.3 | 0 | 0 | TAYLOR | CALLAHAN | Tier 4 |  |  |  |  | Y
08TPIT0206 | Leon Switch #5 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R553-WACF | 2009-05-01 | 2009-04-01 | 138 | 0 | 0 | 100 | 0 | EASTLAND |  | Tier 4 |  |  |  | 1624, 1626 | Y
09TPIT0159 | Midland West terminal equipment | Replace terminal equipment | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R843-WACF | 2009-05-01 | 2009-04-03 | 138 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  |  | 1117 | Y
09TPIT0063 | Whitney to Bosque Reconductor | Reconductor existing Whitney to Bosque 138kv line | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-04-01 | 2009-04-06 | 138 | 0 | 13.4 | 0 | 0 | BOSQUE | MCLENNAN | Tier 4 |  |  |  | 241181177 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0172 | Wichita Falls Switch terminal equipment | Replace terminal equipment on circuit to Wichita Falls South. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R576-WACF | 2009-05-01 | 2009-04-08 | 138 | 0 | 0 | 0 | 0 | WICHITA |  | Tier 4 |  |  |  | 1448 | Y
09TPIT0187 | T.H. Wharton - T.H. Wharton tap Ckt.81 | Move tap to T.H. Wharton (THW) distribution transformer TR5 from ckt.81 THW - Bammel to ckt.81 THW - Fairbanks. Upgrade the newly created THW - THW tap section. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 | 2009-04-09 | 138 | 0 | 0.05 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 45515, 45511 | Y |  |  | No transformer capacity to be added.
07TPIT0132 | West Denton Re-route 138 KV Line Exits | Relocate 138 lines and add new line to R.D. Wells Interchange and Substation | Delayed due to line routing issues in Denton |  |  |  | 06TPIT0179 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06014 | 2009-05-08 | 2009-04-09 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 988 | Y
09TPIT0182 | Tradinghouse terminal equipment | Replace terminal equipment on circuit to Temple Pecan Creek. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R731-WACF | 2009-05-01 | 2009-04-16 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3405 | Y
09TPIT0029 | Hilltop Lakes Sw. to Hearne Rebuild | Rebuild existing Hilltop Lakes to Hearne | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-03-01 | 2009-04-17 | 69 | 0 | 14.5 | 0 | 0 | ROBERTSON | ROBERTSON | Tier 4 |  |  |  | 36,53,57,43 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0152 | Big Spring - Chalk - McDonald 69 kV line | Rebuild existing 69 kV line for double-circuit operation with one 138 kV circuit and one 69 kV circuit | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R645-WAC | 2009-05-01 | 2009-04-17 | 138 | 17.6 | 17.6 | 0 | 0 | HOWARD | HOWARD | Tier 3 | 2007-09-01 | 2008-01-18 | N/A | 1323, 1352, 1333 | Y |  |  | Big Spring - Signal Mountain section wll be completed by 12/2008.
07TPIT0231 | Tyler Grande 345/138 kV Switching Station | Construct switching station and install a 345/138 kV autotransformer |  |  |  |  | R387, R337B & R386 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R384-WACF | 2009-05-15 | 2009-04-20 | 345 | 0 | 0 | 600 | 0 | SMITH |  | Tier 3 | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3102, 3196 | Y
07TPIT0016 | Saginaw - Euless/Roanoke Switch 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M507-WAC | 2009-05-01 | 2009-04-22 | 138 | 0 | 17.4 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1957, 2039, 2040, 2041, 2042, 2043, 2044, 2047 | Y
07TPIT0158 | Sandow Switch - Salty - Thorndale North - Taylor 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R485-WACF | 2009-05-01 | 2009-04-22 | 138 | 0 | 21.86 | 0 | 0 | MILAM | WILLIAMSON | Tier 4 | 2007-04-23 | 2007-08-01 | N/A | 3430, 3661, 3659, 3658 | Y |  |  | Sandow Switch - Thorndale N section will be completed in 12/2008.
08TPIT0157 | Blodgett - Garrott Ckt.37 | Raise conductors to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2009-03-30 | 2009-04-23 | 138 | 0 | 1.64 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47521, 47660 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0087 | Singleton Switching Station | Build a new 345 kV Singleton substation. Loop Ckt.1 Jewett - T.H. Wharton, Ckt.1 Jewett - Tomball, Ckt.75 Gibbons Creek - Roans Prairie and Ckt.99 Gibbons creek - Obrien into the new substation. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-04-30 | 2009-04-24 | 345 | 0 | 0.5 | 0 | 0 | GRIMES |  | Tier 3 | 2007-01-08 | 2007-07-16 | 2007-08-21 | 44645 | Y |  |  | 1)_Part of Houston Area Constraint Mitigation Project, Phase II. 2)_No transformer capacity to be added.
09TPIT0157 | Tri Gas (Liquid Air) terminal equipment | Replace terminal equipment | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R869-WACF | 2009-05-01 | 2009-04-30 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1128 | Y
09TPIT0062 | West Weatherford to Shady Grove Rebuild | Rebuild existing West Weatherford to Shady Grove 69kv line | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-05-01 | 2009-05-01 | 69 | 0 | 2.35 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 515, 1585 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0186 | Dunlavy - Heights Ckt.31 | Upgrade Dunlavy - Heights 69kV Ckt.31 to increase thermal ratings. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 | 2009-05-01 | 69 | 0 | 2.35 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47580, 47680 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
06TPIT0113 | McNeil autotransformer replacement | With the completion of 138kV conversion of circuit 822 and 824, the Seaholm auto will replace the autotransformer at the McNeil substation. | COMPLETE |  |  |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P049 | 2009-05-07 | 2009-05-01 | 138 | 0 | 0 | 200 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9079, 9080 | Y
09TPIT0184a | Alvin Auto Substation 138/69kV Autotransformer | Add new 83MVA Autotransformer (A1) at Alvin Auto substation | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 | 2009-05-01 | 138 | 0 | 0 | 83 | 0 | BRAZORIA |  | Tier 4 |  |  |  | 42130, 42140 | Y |  |  | 1) Part of the Post-Ike Galveston area recovery plan. 2) 83MVA Autotransformer A1 to be moved from West Galveston to Alvin Auto substation and a new 69kV bus #42140 will be added to the base cases 3). No transmission circuits to be built, rebuilt or reconductored.
09TPIT0147 | China Grove terminal equipment | Replace terminal equipment on circuit to Paint Creek. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R864-E | 2009-05-01 | 2009-05-01 | 138 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1318 | Y
09TPIT0165 | Shamburger Switch terminal equipment | Replace terminal equipment on circuit to Tyler Grande. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R866-E | 2009-05-01 | 2009-05-01 | 138 | 0 | 0 | 0 | 0 | SMITH |  | Tier 4 |  |  |  | 3104, 3210 | Y
08TPIT8889 | STEC Southmost Substation Approach Span | Build 0.42 Mile Approach Spans into Southmost Substation |  |  |  |  | 08TPIT8888 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2009-05-09 | 2009-05-01 | 138 | 0.42 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
10TPIT0035 | Roanoke Switching Station #1 345/138 kV autotransformer replacement | Replace existing 345/138 kV autotransformer | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5122-WACF | 2009-05-01 | 2009-05-01 | 345 | 0 | 0 | 600 | 0 | DENTON |  | Tier 4 | 2007-12-31 | 2008-02-26 | N/A | 1850, 1851 | Y
09TPIT0092 | VH Braunig to Streich to OW Sommers - 138kV Transmission Line Reroute | Open VH Braunig tie breakers in order to reduce fault current Braunig E - Streich becomes Braunig W - Streich Sommers - Streich becomes Deely - Streich Braunig - OW Sommers upgrade substation equipment to 3000A |  |  |  |  | S-0369 | CPS | T: Adam Marin S: Keith Calle | T-0122 | 2009-05-04 | 2009-05-08 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5025 5110 5395 5417 | Y |  |  | There are no transformers associated with this project
09TPIT0025 | Second Concord 345/138 Autotransformer | Install second 300MVA 345/138KV auto at Concord | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-09-01 | 2009-05-09 | 345 | 0 | 0 | 300 | 0 | JOHNSON |  | Tier 4 |  |  |  | 393, 394 | Y |  |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
10TPIT0046 | Austin to Tuttle - 138kV Transmission Line Rebuild | Reconductor existing 138 kV line |  |  |  |  | S-0396 | CPS | T: Kevin Phillips PM: Ulrich Skerhut | T-0127 | 2009-05-30 | 2009-05-10 | 138 | 0 | 2 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5005 5435 | Y |  |  | There are no transformers associated with this project
09TPIT0144 | Collin Switch 138 kV capacitors | Install capacitors | Project is taking more time than expected. |  |  |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3081-WACF | 2009-07-01 | 2009-05-15 | 138 | 0 | 0 | 0 | 110.4 | COLLIN |  | Tier 4 |  |  |  | 2370 | Y
09TPIT0139 | Johnson Switch | Add 345 kV circuit breakers | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3070-WACF | 2009-05-01 | 2009-05-18 | 345 | 0 | 0 | 0 | 0 | JOHNSON |  | Tier 4 |  |  |  | 1902 | Y
09TPIT0099 | Villa Cavazos, Convert 69 kV distribution substation to 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE |  |  |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3065 | 2009-06-30 | 2009-05-20 | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  |  | Y
09TPIT0100 | La Palma to Military Highway 138kV line, cut-in Villa Cavazos at 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE |  |  |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3071 | 2009-06-30 | 2009-05-20 | 138 | 0.1 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
09TPIT0088 | East Bernard - Wallis - Sealy - Peters Ckt.65 | Raise conductors and partially rebuild Ckt.65 to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-05-04 | 2009-05-22 | 138 | 0 | 25.28 | 0 | 0 | WHARTON | AUSTIN | Tier 4 |  |  |  | 44190, 44740, 44640, 46220 | Y |  |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added
09TPIT0055 | Skyline to Dresden - 138kV Line Upgrade | Upgrade small section from 556AA to 795ACSS/TW | [5 empty] | CPS | T: Adam Marin | T-0128 | 2009-05-16 | 2009-05-23 | 138 | 0 | 1 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5130 5370 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0232 | Tyler Grande - Tyler S. 138 kV line | Rebuild existing 138 kV line for double-circuit operation |  |  |  |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R387-WA | 2009-05-15 | 2009-05-28 | 138 | 2.32 | 2.32 | 0 | 0 | SMITH | SMITH | Tier 4 | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3196, 3218 | Y
09TPIT0094 | Westover Hills - New 138kV Substation | Install new 138kV substation and connect to VLSI |  |  |  |  | T-0121 | CPS | T: LeeRoy Perez S: Keith Calle | S-0328 | 2009-05-29 | 2009-05-29 | 138 | 1.7 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5467 5488 | Y |  |  | There are no transformers associated with this project
09TPIT0197 | Sacroc terminal equipment | Replace terminal equipment on circuit to Snyder. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R870-WACF | 2009-05-01 | 2009-05-29 | 138 | 0 | 0 | 0 | 0 | SCURRY |  | Tier 4 |  |  |  | 1311 | Y
07TPIT0137 | Abilene Plant to Clyde, Rebuild 69/138 kV Dbld Crkt Capable | Re-build 13 miles Abilene Plant to Clyde Dbl Crkt 69/138 KV line @ 795 ACSR - Energize @ 69 kV | IN-SERVICE |  |  |  | AEP GROUP 341 | AEP/TNC | John Pulay 918-599-2653 | 1697 | 2009-05-31 | 2009-05-31 | 69 | 0 | 13 | 0 | 0 | TAYLOR | CALLAHAN | Tier 4 |  |  |  |  | Y
09TPIT0146 | Chalk terminal equipment | Replace terminal equipment on circuit to Garden City. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R839-E | 2009-05-23 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1352 | Y
09TPIT0149 | Garden City terminal equipment | Replace terminal equipment on circuit to Chalk. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R840-E | 2009-05-01 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | GLASSCOCK |  | Tier 4 |  |  |  | 1218 | Y
09TPIT0166 | Snyder terminal equipment | Replace terminal equipment on circuit to China Grove. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R865-E | 2009-05-01 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | SCURRY |  | Tier 4 |  |  |  | 1305 | Y
09TPIT0167 | Spraberry terminal equipment | Replace terminal equipment on circuit to Big Spring Switch. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R872-E | 2009-05-01 | 2009-06-01 | 69 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  |  | 1330 | Y
09TPIT0109 | Nicole, Four Position Ring | Provide inteconnection at new Nicole substation | IN-SERVICE |  |  |  | AEP GROUP 390 | AEP/ETT | Leo York | 3115 | 2009-06-01 | 2009-06-01 | 138 | 0 | 0 | 0 | 0 | COKE |  | Tier 4 |  |  |  |  | Y
08TPIT0169 | Cut Bluff Creek to Oak Creek into Nicole | Provide inteconnection at new Nicole substation | IN-SERVICE |  |  |  | AEP GROUP 390 | AEP/TNC | Ashley Beasley 918-599-2653 | 3116 | 2009-06-01 | 2009-06-01 | 138 | 0 | 2 | 0 | 0 | COKE | COKE | Tier 4 |  |  |  |  | Y
09TPIT0110 | Cut Red Creek 138 kV line into Nicole | Provide inteconnection at new Nicole substation | IN-SERVICE |  |  |  | AEP GROUP 390 | AEP/TNC | Ashley Beasley 918-599-2653 | 3114 | 2009-06-01 | 2009-06-01 | 138 | 0 | 38 | 0 | 0 | COKE | TOM GREEN | Tier 4 |  |  |  |  | Y
09TPIT0052 | Justin Lane 138/69 kV substation | Establish a new substation at Justin Lane site and install (2) 30MVA transformers. The substation will cut into the existing Ckt 811 (McNeil to Koenig Lane). | COMPLETE |  |  |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3240_117_4855 PLAN_117_P042 PLAN_117_P135 | 2009-05-11 | 2009-06-01 | 138 | 0.5 | 0 | 60 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9225 | Y
07TPIT0092 | Denton West to RD Wells 138kV Transmission Line | Construct 4.6 miles of new 138kV transmission line | On schedule |  |  | Complete | 07TPIT0091, 0094, 0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600129 | 2009-06-01 | 2009-06-02 | 138 | 4.6 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 986, 930 | Y
06TPIT0030 | West Waco - Lorena - Eddy 69 kV line | Upgrade existing 69 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R093-WACF | 2009-05-01 | 2009-06-03 | 69 | 0 | 16.3 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3437, 3577, 3580 | Y |  |  | The Waco West to Lorena section will be reconstructed by 12/31/2008.
07TPIT0094 | RD Wells Substation | Install three 25MVA, 138kV to 13.2kV substation transformers served from the RD Wells 138kV bus | On schedule |  |  | Complete | 07TPIT0091, 0092, 0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600126 | 2009-06-02 | 2009-06-03 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 932 | Y
09TPIT0006 | Lobo, build 138/69 kV substation | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE |  |  |  | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1306 | 2009-12-31 | 2009-06-09 | 138 | 0 | 0 | 93 | 0 | WEBB |  | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
09TPIT0114 | San Angelo Power Station, Reconfigure Station | San Angleo Power Station, Reconfigure Station to separate wind from load circuits | IN-SERVICE |  |  |  | AEP GROUP 429 | AEP/TNC | Brett Madison 918-599-2653 | #N/A | 2009-06-10 | 2009-06-10 | 138 | 0 | 0 | 0 | 0 | TOM GREEN |  | Tier 4 |  |  |  |  | Y
09TPIT0210 | San Angelo Power Station, to Menard 138 kV line improvements | Rebuild part of SAPS to Menard 138 kV line by replacing structures | IN-SERVICE |  |  |  | AEP GROUP 471 | AEP/TNC | Brett Madison 918-599-2653 | 2353 | 2009-06-10 | 2009-06-10 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | MENARD | Tier 4 |  |  |  |  | Y
09TPIT0161 | Moss Switch terminal equipment | Replace terminal equipment on circuit to Odessa EHV. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R846-WACF | 2009-05-01 | 2009-06-12 | 138 | 0 | 0 | 0 | 0 | ECTOR |  | Tier 4 |  |  |  | 1019 | Y
09TPIT0155 | Lake Creek terminal equipment | Replace terminal equipment on circuit to Tradinghouse. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R715-WACF | 2009-06-01 | 2009-06-12 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3409 | Y
09TPIT0082 | Jewett - Big Brown 345 kV circuit #1 | Upgrade circuit breaker and associated equipment at Big Brown to increase emergency rating of line. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R707-E | 2009-05-01 | 2009-06-16 | 345 | 0 | 0 | 0 | 0 | FREESTONE |  | Tier 4 |  |  |  | 3390, 3380 | Y |  |  | 1)_Part of Houston Area Constraint Mitigation Project, Phase II. 2)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0151 | Graham terminal equipment | Replace terminal equipment on circuit to Navy Kickapoo. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R554-WACF | 2009-05-01 | 2009-06-18 | 69 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1602 | Y
09TPIT0145 | Shamburger Switch 138 kV capacitors | Install capacitors | Project is taking more time than expected. |  |  |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R860-WACF | 2009-07-01 | 2009-06-23 | 138 | 0 | 0 | 0 | 110.4 | SMITH |  | Tier 4 |  |  |  | 3104 | Y
09TPIT0131 | Interconnect a new combined cycle plant at Cedar Bayou. | Add a new combined cycle plant at the NRG Cedar Bayou site connected to the Cedar Bayou substation. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-06-30 | 2009-06-24 | 345 | 0 | 0 | 0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 40000, 48583, 48584, 48585, 40001 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0138 | Aransas Pass: Add 1-28.8 MVAR Cap Bank | Aransas Pass: Add 3-69 KV Breakers, Add 1-28.8 MVAR 69 KV Cap Bank |  |  |  |  | AEP GROUP 029 | AEP/TCC | Michael Glueck 918-599-2653 | 1192 | 2009-06-30 | 2009-06-26 | 69 | 0 | 0 | 0 | 28.8 | ARANSAS |  | Tier 4 |  |  |  |  | Y
09TPIT0143 | Anna Switch 138 kV capacitors | Install capacitors | Project is taking more time than expected. |  |  |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3080-WACF | 2009-07-01 | 2009-06-26 | 138 | 0 | 0 | 0 | 110.4 | COLLIN |  | Tier 4 |  |  |  | 2374 | Y
09TPIT0048 | Poage - Temple Taylors Valley - Bell County 69 kV line | Upgrade existing 69 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R472-WACF | 2009-05-01 | 2009-06-29 | 69 | 0 | 3.4 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3635, 3636 | Y
09TPIT0136 | Northern Natural 2 Mvar Capacitor bank | Install 2 Mvar 69 kV Cap Bank at Northern Natural | [5 empty] | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2009-06-30 | 2009-06-30 | 69 | 0 | 0 | 0 | 2 | PECOS | PECOS | Tier 4 |  |  |  | 38440 | Y
07TPIT0151 | Yellowjacket, New 138/69 Station | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2138 | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 90 | 28.8 | MENARD |  | Tier 4 |  |  |  |  | Y
08TPIT0024 | Wilson(7615)-CPS Sutherland Springs(5418) | Construct a new 795 ACSR (220-MVA) 138-kV transmission line between the Wilson(7615) and Floresville Sutherland Springs(5418) substations. | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2009-07-31 | 2009-06-30 | 138 | 10.98 | 0 | 0 | 0 | WILSON | WILSON | Tier 3 |  |  |  | See Project Title | Y
09TPIT0056 | McNeil-Gilleland | Replace under-rated limiting line terminal equipment to increase McNeil (7334)-Gilleland (7336) to the conductor's rating. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0070 | Fayetteville-Willow Springs | Replace under-rated limiting line terminal equipment to increase Fayetteville (7286)-Willow Springs (7273) to the conductor's rating. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 0 | 0 | FAYETTE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0071 | Avery Ranch-Jollyville | Replace under-rated limiting line terminal equipment to increase Avery Ranch (7534)-Jollyville (9223) to the conductor's rating. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-06-30 | 2009-06-30 | 138 | 0 | 0 | 0 | 0 | WILLIAMSON |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0174 | Lufkin Switch - Aspen Power 138 kV line | Construct second 138 kV circuit on an existing line to connect a new power plant. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R850-WAC | 2009-08-01 | 2009-06-30 | 138 | 1.9 | 0 | 0 | 0 | ANGELINA | ANGELINA | Tier 4 |  |  |  | 3118, 3268 | Y
07TPIT0070 | Taylor - Taylor West - Hutto Switch 138 kV line | Upgrade existing 138 kV line | Will attempt accelerating project if construction clearance can be obtained. |  |  |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R457-WACF | 2009-07-01 | 2009-06-30 | 138 | 0 | 10.07 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  | 2007-08-01 | N/A | 3666, 3673, 3658 | Y
09TPIT0123 | Parkdale SVC installation | Install two +300 Mvar/-265 Mvar SVCs | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4056-WACF | 2009-06-15 | 2009-06-30 | 138 | 0 | 0 | 0 | 600 | DALLAS |  | Tier 1 | 2007-02-01 |  | 2007-08-01 | 2440, 12440, 12448, 12449 | Y
09TPIT0065 | Spruce 2 - Power Plant Loop | Install 345kV connection between the Spruce 2 GSU and the existing Spruce 345kV switchyard |  |  |  |  | S-0138 | CPS | T: LeeRoy Perez S: Joe Rodriguez | T-0075 | 2009-06-15 | 2009-06-30 | 345 | 0.07 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5400 | Y |  |  | There are no transformers associated with this project
09TPIT0160 | Morgan Creek terminal equipment | Replace terminal equipment on circuits Odessa EHV and Quail Switch. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R833-WACF, R841-WACF & R842-WACF | 2009-05-01 | 2009-06-30 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1030 | Y
11TPIT0049 | Morgan Creek terminal equipment | Replace terminal equipment on line to Twin Buttes. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C071-E | 2009-05-01 | 2009-06-30 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | CREZ |  |  |  | 1030 | Y |  | IF zero ($) no dates are needed | CREZ default project Existing terminal equipment is adequate.
09TPIT0180 | Barney Davis: Expand substation for Generator interconnects | Barney Davis interconnection of 360 MW of new generation | IN-SERVICE |  |  |  | AEP GROUP 400 | AEP/TCC | Michael Glueck 918-599-2653 |  | 2009-07-01 | 2009-07-01 | 138 | 0 | 0 | 0 | 0 | NUECES |  | Tier 4 | 2009-03-22 | 2009-10-09 | 2009-12-01 |  | Y
05TPIT0118 | Hidden Valley 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Hidden Valley substation. | COMPLETE |  |  |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | 3230_117_1442 | 2009-07-01 | 2009-07-01 | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9207 | Y
10TPIT0057 | Benbrook series reactors | Install a 2-ohm 138 kV series reactor on autotransformer A and B. | ERCOT's approval process for this project took more time than expected which delayed the start of construction. |  |  |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5068-WACF & M5139-WACF | 2009-07-01 | 2009-07-09 | 138 | 0 | 0 | 0 | 0 | TARRANT |  | Tier 4 |  |  |  | 1874,1870, 1869, 1875 | N
06TPIT0166 | MVEC Palmhurst-MVEC Merett | Rebuild 138kV line from Palmhurst to Merett Substations |  |  |  |  | 06TPIT0165 | STEC | Doug Evans 361-485-6459 devans@stec.org | 984501 | 2009-10-09 | 2009-07-09 | 138 | 0 | 4.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8774-8752 | Y
08TPIT8888 | STEC Southmost Substation | Build New 138kV Substation |  |  |  |  | 08TPIT8889 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2009-05-09 | 2009-07-09 | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  | 8789 | Y
09TPIT0206 | Warvue Co-Generation | Interconnect a new co-generation plant at Warvue substation. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-05-31 | 2009-07-14 | 138 | 0 | 0 | 0 | 0 | CHAMBERS |  | Tier 4 |  |  |  | 48940, 41700 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0082 | Live Oak, Add 69/138 kV Auto | Add second Auto 138/69 (LTC) at Live Oak 50 MVA - Expand to a four position ring bus | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2130 | 2009-07-16 | 2009-07-16 | 138 | 0 | 0 | 50 | 0 | SCHLEICHER |  | Tier 4 |  |  |  |  | Y
09TPIT0216 | Lynpol Substation | Disconnect customer owned Lynpol substation from CNP's Ckt. 94 Fairmont - Himont. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-07-31 | 2009-07-31 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 42910 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0202 | Construct Betka 138kV Substation | Serve substation by looping into Ckt.66 Hockley to Freeman. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-06-30 | 2009-07-31 | 138 | 1.74 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 45675 | Y |  |  | No transformer capacity added.
09TPIT0138 | Hillsboro - Alvarado 69 kV line | Rebuild existing 69 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R489-WACF | 2009-09-01 | 2009-08-19 | 69 | 0 | 27.2 | 0 | 0 | HILL | JOHNSON | Tier 4 | 2008-05-01 | 2008-06-10 | N/A | 3523, 3532, 3533, 3537, 2298 | Y
09TPIT0156 | Leon Switch terminal equipment | Replace terminal equipment on circuit to Putnam. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R577-E | 2009-12-01 | 2009-08-19 | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | Tier 4 |  |  |  | 1624 | Y
05TPIT0069 | Waller-Prairie View-Seaway-Macedonia | Upgrade the 22.0-mile Waller(7272)-Macedonia(7671) 138-kV transmission line from 477 ACSR (159-MVA) to 959 ACSS (392-MVA). | [5 empty] | SBEC | Billy Marricle (979) 865-3171 bmarricle@sbec.org | 1004653 | 2009-09-01 | 2009-08-20 | 138 | 0 | 22 | 0 | 0 | WALLER | WALLER | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0204 | Pelican Tap | Pelican 138 kV: Papalote Creek 180 MW Windfarm Direct Interconnect | IN-SERVICE |  |  |  | AEP GROUP 397 | AEP/TCC | Tommy Vannoy 918-599-2653 | 3095 | 2009-09-01 | 2009-09-01 | 138 | 0 | 0 | 0 | 0 | San Patricio |  | Tier 4 |  |  |  |  | N
12TPIT0020 | Kendall CTEC to Kendall | The existing LCRA TSC 138 kV transmission line (approximately 0.23 miles) between the Kendall CTEC (7147) and LCRA TSC Kendall (7152) stations will be rebuilt. The rebuilt transmission line will consist of 1X795 ACSR conductor to provide a thermal rating of 220 MVA. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2012-12-01 | 2009-09-01 | 138 | 0 | 0.23 | 0 | 0 | KENDALL | KENDALL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  |  | CREZ Default project assigned to LCRA TSC
09TPIT0128 | Zorillo: Build 345kV Station | Build 345 kV switching station in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's |  |  |  |  | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2222 | 2009-08-03 | 2009-09-01 | 345 | 0 | 0 | 0 | 0 | KENEDY |  | Tier 4 |  |  |  |  | Y
09TPIT0069 | Rattlesnake Road 345 kV Switching Station | Construct 345 kV switching station to connect a new power plant. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R499-WA | 2009-09-01 | 2009-09-01 | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  | Tier 4 |  |  |  | 3397, 3398, 3399 | Y
09TPIT0212 | SAPS: Reconfigure to double bus, double breaker, reterminate 69/138 kV Auto | Rebuild part of SAPS to Menard 138 kV line by replacing structures and Move SAPS auto and add DCRS at North Brady | IN-SERVICE |  |  |  | AEP GROUP 472 | AEP/TNC | Brett Madison 918-599-2653 | 2356 | 2009-09-30 | 2009-09-15 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | TOM GREEN | Tier 4 |  |  |  |  | Y
10TPIT0094 | Britmore - Addicks Ckt.09 | Upgrade limiting equipment at 138kV Addicks and Britmoore substations to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-09-30 | 2009-09-22 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 44120, 45610 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0106 | Perry Auto | Increase 138/69 autotransformer capacity at Perry | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-11-03 | 2009-09-24 | 138 | 0 | 0 | 100 | 0 | FALLS |  | Tier 4 |  |  |  | 91,92 | Y |  |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
07TPIT0225 | Bennett Road Switching Station | Construct 138 kV switching station |  |  |  |  | R510A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510B-WACF | 2009-12-01 | 2009-10-01 | 138 | 0 | 0 | 0 | 0 | WISE |  | Tier 3 |  |  |  | 1582, 1565, 1566, 1568 | Y
09TPIT0220 | Graham terminal equipment upgrade | Upgrade 345 kV terminal equipment on lines to Long Creek and Parker | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R575-WACF | 2009-12-01 | 2009-10-01 | 345 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1430, 1436, 1435 | Y
09TPIT0218 | Graham Switch terminal equipment | Replace terminal equipment on line to Bowman | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R575-WA | 2009-10-01 | 2009-10-01 | 345 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1430 | Y
09TPIT0219 | Morgan Creek terminal equipment | Replace terminal equipment on line to Twin Buttes. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C071-E | 2009-10-01 | 2009-10-01 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1030 | Y
09TPIT0095 | Cagnon - 138kV Capacitor Bank Addition | 80 MVAR Capacitor Addition at Cagnon | [5 empty] | CPS | S: Ricardo Renteria | S-0362 | 2009-08-17 | 2009-10-07 | 138 | 0 | 0 | 0 | 80 | BEXAR | BEXAR | Tier 4 |  |  |  | 5055 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
09TPIT0191 | Reactor Banks | Install 25 MVAR reactor Banks at Jack County, Rhome, Bowie, and Spring | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-11-02 | 2009-10-08 | 138 | 0 | 0 | 0 | -100 | COOKE, MONTAGUE, JACK, WISE |  | Tier 4 |  |  |  | 579576620684 | N |  |  | Substation Project
07TPIT0152 | Abilene South, 2nd 69/138 kV Auto | Abilene South, add 2nd 69/138 kV 90 MVA Autotransformer | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2134 | 2009-09-30 | 2009-10-10 | 138 | 0 | 0 | 90 | 0 | TAYLOR |  | Tier 4 |  |  |  |  | Y
09TPIT0137 | Hill Country - 138kV Capacitor Bank Addition | Remove one existing back-to-back 50.4MVAR capacitor bank at Harmony Hills and relocate to the 138kV Hill Country bus | [5 empty] | CPS | S: David Riethmeyer | S-0520 | 2009-09-30 | 2009-10-12 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5209 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0153 | Yellowjacket, Add 2nd 69/138 kV Auto | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank, | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2123 | 2009-12-31 | 2009-10-13 | 138 | 0 | 0 | 90 | 0 | MENARD |  | Tier 4 |  |  |  |  | Y
09TPIT0126 | Sonora 69 kV: Mitigation | Open the Friend Ranch to Sonora 69 kV line when the Friend Ranch to Sonora 138 kV line trips to keep the 69 kV line from overloading | IN-SERVICE |  |  |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2265 | 2009-12-31 | 2009-10-15 | 138 | 0 | 0 | 0 | 0 | SUTTON |  | Tier 4 |  |  |  |  | Y
09TPIT0141 | Abilene South, Replace 138/69 kV Auto | Abilene South, add 2nd 69/138 kV 90 MVA Autotransformer | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2134 | 2009-09-30 | 2009-10-23 | 138 | 0 | 0 | 90 | 0 | TAYLOR |  | Tier 4 |  |  |  |  | Y
09TPIT0097 | Hunt Lane - New 138kV substation | Build a new two-terminal 138kV substation to replace Marbach. |  |  |  |  | T-0126 | CPS | PM:Hector Torres | S-0398 | 2009-10-16 | 2009-10-23 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5234 | Y |  |  | There are no transformers associated with this project
09TPIT0171 | Tyler South terminal equipment | Replace terminal equipment | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R835-WA | 2009-12-01 | 2009-10-24 | 138 | 0 | 0 | 0 | 0 | SMITH |  | Tier 4 |  |  |  | 3218 | Y
07TPIT0224 | Decatur - Bennett Rd - Wise County 138 kV line | Rebuild existing 138 kV line |  |  |  |  | R510A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R511-WACF | 2009-11-01 | 2009-10-28 | 138 | 0 | 12.6 | 0 | 0 | WISE | WISE | Tier 3 |  |  |  | 1582, 1566 | Y
08TPIT0049 | Second Whitney 345/138 Autotransformer | Install second 450MVA 345/138KV auto at Whitney | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-09-01 | 2009-10-28 | 345 | 0 | 0 | 450 | 0 | BOSQUE |  | Tier 4 |  |  |  | 240, 241 | Y |  |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
09TPIT0208 | Install an intermediate pole and jumpers to connect Langford to SAPS/ELO 138 kV line | Interconnect Langford Wind Farm at Santiago, upgrade relaying | IN-SERVICE |  |  |  | AEP GROUP 461 | AEP/TNC | Terry Weeks 918-599-2653 | 2335 | 2009-10-01 | 2009-10-29 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | TOM GREEN | Tier 4 |  |  |  |  | Y
09TPIT0209 | Lighthouse Electric Co-Op distribution station | Muleta tap located on the Matador to Turkey 69 kV line | IN-SERVICE |  |  |  | AEP GROUP 470 | AEP/ETT | Dave Goetz 918-599-2653 | 2352 | 2009-11-30 | 2009-10-30 | 69 | 0 | 0 | 0 | 0 | MOTLEY | MOTLEY | Tier 4 |  |  |  |  | Y
09TPIT0096 | Floresville - 138kV Capacitor Bank Addition | Install a new circuit breaker and 18 MVAR capacitor bank at the Elmendorf substation in conjunction with a 21.6 MVAR capacitor bank at Floresville | [5 empty] | CPS | S: David Riethmeyer | S-0364 | 2009-11-30 | 2009-10-30 | 138 | 0 | 0 | 0 | 10 | BEXAR | BEXAR | Tier 4 |  |  |  | 5155 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
09TPIT0199 | Champion Creek Switching Station | Construct a 345 kV switching station to connect a new wind farm. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8000-WACF | 2009-12-01 | 2009-10-30 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  | Tier 4 |  |  |  | 1414 | Y
09TPIT0027 | Fox to Hilltop 138KV Conversion | Convert existing Fox to North Texas 69KV line to 138KV operation. Rebuild Fox to Brock line with double circuit construction | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-30 | 2009-11-03 | 138 | 0 | 3.7 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 501, 495, 498, 487, 478 | Y |  |  | There is no reactive or transformer capability associated with this project
09TPIT0201 | IH20 15 Mvar Capacitor bank | Install 15 Mvar 69 kV Cap Bank at IH20 | [5 empty] | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2009-11-15 | 2009-11-09 | 69 | 0 | 0 | 0 | 15 | REEVES | REEVES | Tier 4 |  |  |  | 38040 | Y
09TPIT0129 | Paducah 69/138 kV Station, Replace the existing 69/138 kV auto | Replace 69/138 kV auto at Paducah with an 90 MVA 69/138 kV with LTC and add 20 MVAR 138 kV shunt reactor | IN-SERVICE |  |  |  | AEP GROUP 289 | AEP/TNC | Brett Madison 918-599-2653 | 1436 | 2009-11-10 | 2009-11-10 | 138 | 0 | 0 | 90 | 0 | COTTLE |  | Tier 4 |  |  |  |  | Y
09TPIT0193 | J.K. Spruce to Pawnee - 345 kV Substation Equipment Upgrade | Replace Substation Equipment at J.K. Spruce in order to remove an existing MLSE | [5 empty] | CPS | S: Cory Kaldacek | S-0543 | 2009-11-01 | 2009-11-15 | 345 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5400 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
09TPIT0192 | Krum | Convert to 138 kV operation | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-11-01 | 2009-11-16 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  |  | 670 | Y
09TPIT0148 | Falcon Seaboard terminal equipment | Replace terminal equipment on circuit to Midland East. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R837-WA | 2009-12-01 | 2009-11-17 | 345 | 0 | 0 | 0 | 0 | HOWARD |  | Tier 4 |  |  |  | 1025 | Y
10TPIT0105 | Parker Switch - Everman 345 kV line | Construct 345 kV line on existing structures. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C035-WA | 2009-11-01 | 2009-11-17 | 345 | 86.3 | 0 | 0 | 0 | PARKER | TARRANT | CREZ |  |  |  | 1436, 1882, 1886, 1430, 1873 | Y |  |  | Project schedule details can be found in PUCT MCPR Docket No. 36146.
09TPIT0222 | Everman Switch | Install 345 kV breakers at Everman. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C035-WA | 2009-11-01 | 2009-11-17 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  |  | Y |  |  | Project schedule details can be found in PUCT MCPR Docket No. 36146.
09TPIT0223 | Parker Switch | Upgrade Parker bus arrangement and connect Graham - Benbrook 345 kV line to Parker. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C035-WA | 2009-11-01 | 2009-11-17 | 345 | 0 | 0 | 0 | 0 | PARKER |  | CREZ |  |  |  |  | Y |  |  | Project schedule details can be found in PUCT MCPR Docket No. 36146. Cost estimated is included in Parker Switch station upgrade project.
09TPIT0007 | Spruce to Skyline - 345kV 2nd Circuit | Build second 345kV line from Spruce to Skyline on existing transmission structures |  |  |  |  | S-0127 | CPS | T: LeeRoy Perez S: Joe Rodriguez | T-0050 | 2009-11-13 | 2009-11-19 | 345 | 20.77 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 | 2007-05-08 | 2007-05-31 | N/A | 5371 5400 | Y |  |  | There are no transformers associated with this project
10TPIT0029 | Robertson to Watson Chapel Rebuild | Rebuild existing Robertson to Watson Chapel 138kv line | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 | 2009-11-23 | 138 | 0 | 21.6 | 0 | 0 | ROBERTSON | LEON | Tier 4 |  |  |  | 32,33 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0120 | Live Oak-Gillespie | Replace under-rated limiting line terminal equipment at Live Oak and Gillespie to increase Live Oak (7412)-Rutherford (7130) to the conductor's rating. | [5 empty] | CTEC | David Peterson 830-992-2250 david.peterson@ctec.coop |  | 2010-06-30 | 2009-11-24 | 69 | 0 | 0 | 0 | 0 | GILLESPIE |  | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
09TPIT0005 | Laredo Plant to Lobo, upgrade 69 kV to 138 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE |  |  |  | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1303 | 2009-11-29 | 2009-11-29 | 138 | 0 | 16.5 | 0 | 0 | WEBB | WEBB | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
09TPIT0134 | York Creek (Galle) - New Substation | Construct a new 138-kV 22.4 MVA substation on the LCRA Zorn-Luling 138-kV transmission line. | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2009-11-30 | 2009-11-30 | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | 7227 | Y
09TPIT0200 | Caterpillar - New Substation | Build a 138-12.5 KV (2) 12-16-20 MVA substation on the existing GVEC 138 KV transmission line between Seguin-West and CMC (SMI) substations. | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2009-11-30 | 2009-11-30 | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  | Tier 4 |  |  |  | See Project Title | N
09TPIT0188 | Tomball - Tomball Tap Ckt.66 | Reconductor Tomball - Tomball Tap Ckt.66 | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-11-30 | 2009-12-01 | 138 | 0 | 0.11 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 46510, 46511 | Y |  |  | No transformer capacity to be added.
10TPIT0136 | Bell County - Salado 138 kV line | Increase the operating temperature of the line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2009-12-01 | 2009-12-01 | 138 | 0 | 7 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3640, 3425 | Y
09TPIT0221 | Eagle Mountain - Alliance - Roanoke Switch terminal equipment | Upgrade 345 kV terminal equipment | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2009-12-01 | 2009-12-01 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | CREZ |  |  |  |  | Y
09TPIT0224 | Jacksboro Switch | Install 345 kV circuit breakers | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C039-WA | 2009-12-01 | 2009-12-01 | 345 | 0 | 0 | 0 | 0 | JACK |  | CREZ |  |  |  | 1429 | Y |  |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
09TPIT0158 | Midland East terminal equipment | Replace terminal equipment on circuit to Moss. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R838-WACF | 2009-12-01 | 2009-12-07 | 345 | 0 | 0 | 0 | 0 | MIDLAND |  | Tier 4 |  |  |  | 1022 | Y
09TPIT0213 | White Baker Station Serve OXY Century Plant | In White Baker Station add 138kV breaker and line position to serve new customer, OXY Century Plant. | [5 empty] | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com |  | 2009-12-09 | 2009-12-09 | 138 | 0 | 0 | 0 | 0 | PECOS |  | Tier 4 |  |  |  | 38431 | Y
07TPIT0253 | West Childress to Henry: Rebuild Dbl Ckt 138/69 kV Line | Rebuild Dbl Crkt 138/69 Line from West Chilldress to Childress 20th Street to connect BEC's Henry Substation (11/09) | IN-SERVICE |  |  |  | AEP GROUP 403 | AEP/BEC | John Pulay 918-599-2653 | 2279 | 2009-12-10 | 2009-12-10 | 69 | 1 | 0 | 0 | 0 | CHILDRESS | CHILDRESS | Tier 4 |  |  |  |  | Y
10TPIT0067 | Holbrook - New 138kV Substation | Loop new 138kV substation into the existing 138kV Coliseum to Kirby line |  |  |  |  | T-0136 | CPS | S: Keith Calle | S-0226 | 2010-01-29 | 2009-12-10 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5218 | Y |  |  | There are no transformers associated with this project
09TPIT0108 | Rio Pecos, Add SVC at Rio Pecos | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto | IN-SERVICE |  |  |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2227 | 2009-12-11 | 2009-12-11 | 69 | 0 | 0 | 0 | 90 | PECOS |  | Tier 4 |  |  |  |  | Y
09TPIT0107 | Rio Pecos, Add 2nd 138/69 kV Auto & reconfig 69 kV bus | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto | IN-SERVICE |  |  |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2232 | 2009-12-11 | 2009-12-11 | 138 | 0 | 0 | 68 | 0 | PECOS |  | Tier 4 |  |  |  |  | Y
09TPIT0195 | Raymond Barker to Verde Creek | The existing LCRA TSC 138 kV transmission line (approximately 1.9 miles) between the LCRA TSC Raymond Barker (7158) and Bandera Electric Cooperative (BEC) Verde Creek (7146) stations will be rebuilt. The rebuilt transmission line will consist of 2X795 ACSR conductor to provide a thermal rating of 440 MVA. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2009-12-16 | 2009-12-11 | 138 | 0 | 1.9 | 0 | 0 | KERR | KERR | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  |  | CREZ Default project assigned to LCRA TSC
10TPIT0055 | Eagle Mountain 345/138 kV autotransformer | Install second 345/138 kV autotransformer | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C001-WA | 2009-12-01 | 2009-12-16 | 345 | 0 | 0 | 517 | 0 | TARRANT |  | CREZ | 2007-12-31 | 2008-02-26 | N/A | 11865, 11864 | Y |  |  | Project schedule details can be found in PUCT MCPR Docket No. 36146.
05TPIT0117 | HiCross to Slaughter Lane 138kV circuit | Establish a new 138kV circuit from HiCross to Slaughter Lane substation | COMPLETE |  |  |  |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P225 PLAN_117_P251 | 2009-11-09 | 2009-12-18 | 138 | 2.2 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 2 | 2008-11-25 | 2008-12-17 | 2009-02-06 | 9147,9292,9267, 9075 | Y
09TPIT0183 | Needle 69kV Substation | Disconnect customer owned Needle 69kV substation from 69kV Ckt.43 Crosby to Mont Belvieu and serve from distribution voltage. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-12-31 | 2009-12-19 | 69 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 41140 | Y |  |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2) Bus #41140 will be removed from the base cases.
06TPIT0014 | LaPalma to Loma Alta, cut-in Los Fresnos at 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE |  |  |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 645 | 2009-12-31 | 2009-12-22 | 138 | 0.1 | 0 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
06TPIT0133 | Los Fresnos, Convert 69 kV distribution substation to 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line | IN-SERVICE |  |  |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 1708 | 2009-12-31 | 2009-12-22 | 138 | 0 | 0 | 0 | 0 | CAMERON |  | Tier 4 |  |  |  |  | Y
07TPIT0238 | Krum - Allison - Decatur 138 kV line | Rebuild and convert 69 kV line to 138 kV operation |  |  |  |  | R510B & R511 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510A-WACF | 2009-11-01 | 2009-12-28 | 138 | 0 | 19 | 0 | 0 | DENTON | WISE | Tier 3 | 2008-01-14 | 2008-05-19 | N/A | 1582, 1568, 1987, 1990, 1986 | Y
09TPIT0038 | Ben Davis Sub: Replace 138 kV Breakers due to interrupting rating | Replace existing circuit breakers due to interrupting rating | [5 empty] | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T07005 | 2009-12-30 | 2009-12-31 | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 968 | Y
08TPIT0200 | Interconnection between TNMP and BP Alternative Energy North America Inc | BP's one 244 MW steam turbine generating unit will be interconnected with TNMP's 138kV system at Greenbelt Switching Station in Texas City, TX | Most of the breakers have been installed. Remaining breakers are scheduled for delivery and installation |  |  |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2009-12-30 | 2009-12-31 | 138 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  |  | N
08TPIT0156 | H.O. Clarke - Brays Ckt.09 | Raise conductors and upgrade limiting equipment at H.O. Clarke and Brays to increase thermal ratings. |  |  |  |  | 07TPIT0263 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2009-12-31 | 2010-01-05 | 138 | 0 | 2.62 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 47150, 47050 | Y |  |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0098 | Replace five poles, Hickory - Locust 69kV Transmission Line | Replace five poles in an existing 69kV transmission line | On Schedule |  |  | Complete | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600774 | 2010-03-31 | 2010-01-10 | 69 | 0 | 0.25 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910, 914 | Y
10TPIT0097 | Salt Creek Reactor | Install 25 MVAR reactor at Salt Creek | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 | 2010-01-19 | 138 | 0 | 0 | 0 | -25 | KENT | KENT | Tier 4 |  |  |  | 743 | N
06TPIT0037 | Carrollton East - Renner 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M448-WA | 2009-12-01 | 2010-01-19 | 138 | 0 | 6.9 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2356, 2611, 2578, 2582 | Y |  |  | Carrollton East - Farmers Branch Gillis Rd section will be completed in 12/2008.
06TPIT0080 | Medina Lake-CPS (Part 1) | Construct a new 138-kV 795 ACSR transmission line (approximately 20 miles in length) from the BEC Medina Lake substation (7432) to the future CPS Energy Talley Road substation (5422), then continuing on to the CPS Energy Texas Research Park substation (5430). | LCRA projected completion date is March 2010. CPS Energy completed on September 23, 2009. |  |  |  | 07TPIT0034 CPS S-0275 | CPS / LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org PM:Hector Torres (210) 353-2404 HVTorres@cpsenergy.com | CPS T-0049 | 2010-01-08 | 2010-01-21 | 138 | 20.7 | 0 | 0 | 0 | BANDERA | BEXAR | Tier 2 | 2007-10-03 | 2007-11-03 |  | 5430 7432 | Y |  |  | CPS and LCRA have filed update letter with ERCOT. BEC is proposing a new load serving substation between Medina Lake and CPS.
09TPIT0175 | Reconfigure Ckt.03 Lynch - Cedar Bayou. | Reconfigure Ckt.03 Lynch - Cedar Bayou substation to create two new circuits Ckt.03 Lynch - EXXON and Ckt.03 Baytown - Cedar Bayou substation per customers request. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-01-31 | 2010-01-22 | 138 | 0.7 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41010, 40011, 40015, 40170, 40570 | Y |  |  | No transformer capacity to be added.
08TPIT0135 | Yellowjacket, Install 150 MVA Phase Shifting Transformer | Yellowjacket, Install 150 MVA 138 kV Phase Shifting Transformer on the SAPS 138 kV line | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2219 | 2010-01-28 | 2010-01-28 | 138 | 0 | 0 | 150 | 0 | MENARD |  | Tier 4 |  |  |  |  | Y
09TPIT0127 | Menard to San Angelo Power Station 138 kV Hairpin into Yellowjacket | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank | IN-SERVICE |  |  |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2154 | 2010-01-28 | 2010-01-28 | 138 | 2 | 0 | 0 | 0 | MENARD | TOM GREEN | Tier 4 |  |  |  |  | Y
09TPIT0211 | San Angelo Power Station to Menard 138 kV line improvements | Rebuild part of SAPS to Menard 138 kV line by replacing structures and Move SAPS auto and add DCRS at North Brady | IN-SERVICE |  |  |  | AEP GROUP 472 | AEP/TNC | Brett Madison 918-599-2653 | 2359 | 2010-01-28 | 2010-01-28 | 138 | 0 | 0 | 0 | 0 | TOM GREEN | MENARD | Tier 4 |  |  |  |  | Y
10TPIT0134 | Gonzales, Build new 69 kV station | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a NaS Battery at Gonzales | IN-SERVICE |  |  |  | AEP GROUP 358 | AEP/ETT | Brett Madison 918-599-2653 | 1182 | 2010-02-01 | 2010-02-01 | 69 | 0 | 0 | 0 | 0 | PRESIDIO |  | Tier 4 |  |  |  |  | Y
10TPIT0153 | Graham terminal equipment | Upgrade terminal equipment on 345 kV line to Bowman | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C070-E | 2010-05-01 | 2010-02-01 | 345 | 0 | 0 | 0 | 0 | YOUNG |  | Tier 4 |  |  |  | 1430 | Y
06TPIT0247 | Salt Dome 69kV Substation | Construct a new Salt Dome substation in the STEC N. Clemville to S. Clemville circut. | Tie is delayed to verify load. Load customer delays and changing load level. Project scope may be reduced before actual construction. Name Changed from "United Brine" to "Salt Dome" |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2009-12-09 | 2010-02-10 | 69 | 0.1 | 0 | 0 | 0 | JACKSON |  | Tier 4 | 2006-03-23 | 2006-04-17 | N/A | 5551 | Y
08TPIT0167 | Friend Ranch, Add 2nd 138 kV 28.8 Mvar Shunt Capacitor | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto (available when needed) | IN-SERVICE |  |  |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2264 | 2010-02-28 | 2010-02-28 | 138 | 0 | 0 | 0 | 28.8 | CROCKETT |  | Tier 4 |  |  |  |  | Y
08TPIT0193 | Sonora to Hamilton 138 kV Line: Apply a dynamic rating with new structures | Raise necessary structures to increase MVA rating of Sonora to Hamilton 138 kV line | IN-SERVICE |  |  |  | AEP GROUP 386 | AEP/TNC/TCC | Brett Madison 918-599-2653 | 2231 | 2010-02-28 | 2010-02-28 | 138 | 0 | 0 | 0 | 0 | SUTTON | VAL VERDE | Tier 4 |  |  |  |  | Y
10TPIT0077 | Hamilton to Pancake Rebuild | Rebuild Hamilton to Pancake with 795ACSR, 138KV | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-08-01 | 2010-03-01 | 69 | 0 | 21.9 | 0 | 0 | HAMILTON | CORYELL | Tier 4 |  |  |  | 158258 | Y
06TPIT0077 | Rim Rock-Jack Furman | Construct a new 336 ACSR 138 kV transmission line (approximately 7.5 miles) between the existing Rim Rock substation (7143) and a new 138 kV switching substation (Jack Furman)(7141). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | 1002912 | 2010-06-30 | 2010-03-01 | 138 | 7.5 | 0 | 0 | 0 | KERR |  | Tier 2 | 2005-09-01 | 2205-09-01 |  | SEE PROJECT DESCRIPTION | Y |  |  | The name of the new substation was changed from Goat Creek to Jack Furman.
09TPIT0178 | Fox to Granbury 138KV Conversion | Convert exisitng Fox to Granbury 69KV line to 138KV operation | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-11-01 | 2010-03-04 | 138 | 3 | 0 | 0 | 0 | PARKER | HOOD | Tier 4 |  |  |  | 306487478 | Y
10TPIT0092 | Crockett Cap Bank | Increase reactive capacity to 107.2 MVAR at 138kV Crockett substation. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-05 | 138 | 0 | 0 | 0 | 100 | HARRIS |  | Tier 4 |  |  |  | 47570, 47571 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
10TPIT0146 | Seward Junction-Leander | Relocate two (2) structures( #84 #85) for Hwy 183A Roadwork | [5 empty] | PEC | Randy Buchanan (830) 868-6058 |  | 2010-03-10 | 2010-03-05 | 138 | 0 | 0 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | N
08TPIT0146 | Firerock, Add Phase Shifting Transformer | Firerock, Build new station and Add Phase Shifting Transformer East of Santa Anna on the Brownwood line | IN-SERVICE |  |  |  | AEP GROUP 391 | AEP/ETT | Ashley Beasley 918-599-2653 | 2269 | 2010-03-18 | 2010-03-07 | 138 | 0 | 0 | 150 | 0 | COLEMAN |  | Tier 4 |  |  |  |  | Y
09TPIT0004 | Laredo Plant to Lobo, rebuild 138 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE |  |  |  | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1304 | 2010-03-07 | 2010-03-07 | 138 | 0 | 15 | 0 | 0 | WEBB | WEBB | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
10TPIT0002 | Lobo, build 345 kV for 675MVA autotransformer | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | IN-SERVICE |  |  |  | AEP GROUP 216 | AEP/ETT | Bill Eakin 918-599-2653 | 1720 | 2010-03-07 | 2010-03-07 | 345 | 0 | 0 | 675 | 0 | WEBB |  | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y
09TPIT0003 | Lobo to San Miguel, build 345 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and con | IN-SERVICE |  |  |  | AEP GROUP 216 | AEP/ETT/TCC | Bill Eakin 918-599-2653 | 633 | 2010-03-07 | 2010-03-07 | 345 | 72 | 0 | 0 | 0 | WEBB | ATASCOSA | Tier 1 | 2003-09-15 | 2004-02-19 | 2004-03-08 |  | Y |  |  | Associated with STEC project 10TPIT0075
07TPIT0248 | San Miguel 345 kV line terminal for San Miguel to Lobo 345 kV line | Breakers, bus, relaying for San Miguel to Lobo 345 kV line termination | Previous 2007 date entry was a typo. Work is planned for 2009. Changed responsibility to STEC and AEP |  |  |  | 09TPIT0003 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-03-01 | 2010-03-10 | 345 | 0 | 0 | 0 | 0 | ATASCOSA |  | Tier 4 |  |  |  | 5901 | Y
10TPIT0075 | San Miguel to Lobo 345 kV line | Construct a 113.8 miles 345 kV line from San Miguel to Lobo. Joint project with AEP. STEC portion 41.8 miles | Previous 2007 date entry was a typo. Work is planned for 2009. Changed responsibility to STEC and AEP |  |  |  | 09TPIT0003 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-03-01 | 2010-03-10 | 345 | 41.8 | 0 | 0 | 0 | ATASCOSA | WEBB | Tier 1 | 2009-10-03 | 2009-02-04 | 2009-03-04 | 5901-80219 | Y
10TPIT0149 | Tomball - Tomball Tap Ckt.66 - Substation Equipment | Upgrade limiting equipment at Tomball substation to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-16 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 46510, 46511 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
09TPIT0104 | Gonzales, add NaS Battery | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a Nas Battery at Gonzales | IN-SERVICE |  |  |  | AEP GROUP 358 | AEP/ETT | Brett Madison 918-599-2653 | 2281 | 2010-03-17 | 2010-03-17 | 69 | 0 | 0 | 0 | 0 | PRESIDIO |  | Tier 1 | 2008-03-21 | 2008-06-10 | 2008-07-15 |  | Y
08TPIT0086 | Exeter - New 138kV Substation | Construct new 138kV substation to replace Terrell Hills substation |  |  |  |  | T-0088 | CPS | PM: Ulrich Skerhut | S-0230 | 2010-03-02 | 2010-03-19 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5143 | Y |  |  | There are no transformers associated with this project
10TPIT0111 | Sandow Switch - Sandow Third 138 kV line | Build new 138 kv line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R732-WACF | 2010-03-01 | 2010-03-20 | 138 | 1 | 0 | 0 | 0 | MILAM | MILAM | Tier 2 |  | 2009-03-01 |  | 13430, 3430, 13434 | Y
10TPIT0112 | Sandow Switch Third 345/138 kV autotransformer | Install third 345/138 kV autotransformer and remove small autotransformer from service. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R736-WACF | 2010-03-01 | 2010-03-20 | 345 | 0 | 0 | 600 | 0 | MILAM |  | Tier 2 |  | 2009-03-01 |  | 3429, 13430 | Y
10TPIT0151 | Benbrook terminal equipment | Upgrade terminal equipment on 345 kV line to Parker | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5154-WACF | 2010-05-01 | 2010-03-21 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | Tier 4 |  |  |  | 1873, 1869, 1870, 1436 | Y
10TPIT0152 | Parker terminal equipment | Upgrade terminal equipment on 345 kV line to Benbrook | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R586-WACF | 2010-05-01 | 2010-03-21 | 345 | 0 | 0 | 0 | 0 | PARKER |  | Tier 4 |  |  |  | 1436, 1873, 1869, 1870 | Y
10TPIT0143 | Childress 20th St to Henry: Rebuild Dbl Ckt 138/69 kV Line | Rebuild Dbl Crkt 138/69 Line from West Chilldress to Childress 20th Street to connect BEC's Henry Substation (11/09) | IN-SERVICE |  |  |  | AEP GROUP 403 | AEP/BEC | John Pulay 918-599-2653 | 2279 | 2010-03-21 | 2010-03-21 | 69 | 1 | 0 | 0 | 0 | CHILDRESS | CHILDRESS | Tier 4 |  |  |  |  | Y
09TPIT0084 | Tomball - Rothwood - Rayford Ckt.66 | Upgrade 138 kV Ckt.66 Tomball - Rothwood to increase thermal ratings | IN-SERVICE |  |  |  | 09TPIT0086 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 13 | 0 | 0 | HARRIS | MONTGOMERY | Tier 3 | 2008-03-26 | 2008-04-14 | 2008-05-20 | 46510, 46295, 46261 | Y |  | “Please see Requested Info in 09tpit0086” | Added as part of 2007 ERCOT 5 year plan projects. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
09TPIT0085 | Convert Rayford 138 kV substation. | Convert Rayford from a double tap substation to a loop tap configuration substation. | IN-SERVICE |  |  |  | 09TPIT0086 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 0 | 0 | 0 | MONTGOMERY |  | Tier 3 | 2008-03-26 | 2008-04-14 | 2008-05-20 | 46261, 46262 | Y |  |  | Added as part of 2007 ERCOT 5 year plan projects. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
10TPIT0071 | Rayford - Westfield Ckt.66 | Upgrade 138 kV Ckt.66 Rayford - Westfield to increase thermal ratings | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 9.14 | 0 | 0 | MONTGOMERY | HARRIS | Tier 4 |  |  |  | 46261, 46051 | Y |  |  | No transformer capacity to be added. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
10TPIT0093 | Tomball - Westfield Ckt.81 | Upgrade 138 kV Ckt.81 Tomball - Westfield to increase thermal ratings | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 138 | 0 | 8.31 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 46510, 46512, 46052 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
09TPIT0086 | Rothwood 345/138 kV substation | Build a new 345/138 kV Rothwood substation. Loop Ckt.74 Kuykendahl to King and 138 kV Ckt.66 Rayford tap section into the new substation. Add one 800 MVA 345/138 kV autotransformer at Rothwood substation. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-03-31 | 2010-03-25 | 345 | 0.4 | 0 | 800 | 0 | HARRIS |  | Tier 3 | 2008-03-27 | 2008-04-14 | 2008-05-20 | 46290, 46295 | Y |  | (Q) I’ve been reviewing the SSWG cases and ERCOT’s 08/01/2008 TPIT to get a better understanding of the projects related to the new Rothwood 345/138 kV substation. In the 2010/2011 SSWG cases, as released, there are still significant overloads on the 138 kV branch from Rothwood to Rayford (46290-46261) for loss of branches 46512-46052 and 46570-45910. (A) Branches 46512-46052 and 46570-45910 do not share a common tower currently and will not share a common tower after the Rothwood project is complete; therefore, they are not included in the ERCOT contingency files posted with the SSWG cases. Furthermore, after the Rothwood project is finished, the circuit segment 46512-46052 will be part of a multi-section line with the circuit designation 46510-46570-&1 (Q) This overload is like the original 2009 overload of the Tomball – Rayford (46510-46261)138 kV line that results in unserved energy that this project is designed to fix. (A) The contingency that caused the unserved energy in the 5 year plan was the loss of the 345 kV double circuit line into Tomball overloading North Belt to Westfield (Q) The latest TPIT lists line upgrade projects on the 138 kV line from Tomball – Rothwood – Rayford going in in 2010. I do not believe that this project is captured in the 2010 or 2011 case. (A) It is captured in the cases; however, the scope of the upgrade had yet to be finalized; therefore, we only modeled bundling the Tomball to Rothwood to Rayford segments with 2-795ACSR. Our own studies on the 08DSB cases from June show a need to upgrade above this capacity because of single contingencies and the soon to be updated TPIT update will reflect these changes. (Q) Can any of you provide the ratings of the lines once the upgrades are complete? The current SSWG case currently has a ratings of 371/455/455 MVA for both 2010 and 2011 (A) The ckt 66 Tomball – Rothwood ratings are expected be 440/526/562. Ckt 66 Rothwood – Rayford ratings are expected to be at least 398/455/893. Final ratings on these segments are still to be determined. (Q) As a side note, the line upgrades associated with the branches from CWESFLD_ 138D – TRSWIG_138A and TRSWIG_138A – Humble__138F are not included in the case. We’ve already included those ratings in our cases though, I have no requests related to those branches. (Q) Additionally, there is an approximately 250% growth in load at Rayford, bus 46261, between 2009 and 2010. I just wanted to verify that this was correct. (A) The reason for the large increase in load is that with the Rothwood project Rayford is being converted from a double tap station to a loop-thru station. The model is adjusted accordingly by eliminating bus 46262 and moving its load (86.2 MW) to bus 46261 for a total of (67.5 + 86.2 MW). | Added as part of 2007 ERCOT 5 year plan projects. Energization dates for projects associated with Rothwood substation have been updated to match the current construction schedule.
08TPIT0079 | Steamboat, new 69 kV switching station | Build new Steamboat 69 kV switch station | IN-SERVICE |  |  |  | AEP GROUP 341 | AEP/TNC | Brett Madison 918-599-2653 | 2074 | 2010-03-31 | 2010-03-31 | 69 | 0 | 0 | 0 | 0 | TAYLOR |  | Tier 4 |  |  |  |  | Y
10TPIT0052 | Big Lake, Add 150 MVA Phase Shifting Transformer | Install a 138 kV Phase Shifting Transformer at Big Lake | IN-SERVICE |  |  |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2228 | 2010-03-31 | 2010-03-31 | 138 | 0 | 0 | 150 | 0 | REAGAN |  | Tier 4 |  |  |  |  | Y
10TPIT0058 | Lytton Springs Autotransformer Addition | Add a new 345-138 kV 478 MVA autotransformer at the Lytton Springs substation (9074). Terminate the Mendoza (7325) - Turnersville (7500) 138 kV transmission line (T-382) into the Lytton Springs substation 138 kV bus (9075), creating the new Turnersville (7500) - Lytton Springs (9075) and Mendoza (7325) - Lytton Springs (9075) 138 kV transmission lines. Upgrade the new Turnersville (7500) - Lytton Springs (9075) 138 kV transmission line from 795 ACSR (220MVA) to 1433 ACSS/TW (507 MVA). Upgrade the new Mendoza (7325) - Lytton Springs (9075) 138 kV transmission line from 795 ACSR (220 MVA) to bundled 795 ACSR (440 MVA). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-05-11 | 2010-04-01 | 345 | 0 | 7 | 478 | 0 | CALDWELL |  | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y
10TPIT0121 | Lolita: Replace Limiting Switches and Jumpers on Formosa to Lolita 138 kV Line | Upgrade generator disturbance monitoring, metering, and communications at the Formosa 138 kV substation. Add generator monitoring, protection, and communications at the Formosa CFB Plant. | In-Service |  |  |  | AEP GROUP 437 | AEP/TCC | Paul Hassink 918-599-2653 | 3336 | 2010-04-09 | 2010-04-09 | 138 | 0 | 11.84 | 0 | 0 | CALHOUN | JACKSON | Tier 4 |  |  |  |  | Y
09TPIT0196 | Pearsall to Moore SS 138 kV Line | Upgrade 12 miles composite core 1020 ACCC-TW 138 kV line conductor from Pearsall to Moore Switching Station. | Upgrade 138 kV line for new generation at Pearsall |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-04-01 | 2010-04-10 | 138 | 0 | 12 | 0 | 0 | FRIO | FRIO | Tier 4 |  |  |  | 5895-5827 | Y
10TPIT0150 | Elgin Switch terminal equipment | Upgrade 138 kV terminal equipment on line to Gilleland | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R734-WACF | 2010-05-01 | 2010-04-17 | 138 | 0 | 0 | 0 | 0 | WILLIAMSON |  | Tier 4 |  |  |  | 3650 | Y
10TPIT0110 | Sandow Switch - Elgin Switch 138 kV line | Rebuild existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R733-WACF | 2010-04-01 | 2010-04-17 | 138 | 0 | 21.8 | 0 | 0 | MILAM | WILLIAMSON | Tier 2 | 2008-07-07 | 2008-08-04 | 2009-03-31 | 13430, 3650 | Y
10TPIT0139 | Salado Switch | Add 345 kV breakers | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C007-WA | 2010-06-01 | 2010-04-17 | 345 | 0 | 0 | 0 | 0 | BELL |  | CREZ |  |  |  | 3699 | Y |  |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
08TPIT0158 | Baytown - Haney Ckt.66 | Reconductor and upgrade limiting equipment at Baytown to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-04-30 | 2010-04-29 | 138 | 0 | 7.1 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40170, 40172, 40790 | Y |  |  | No transformer capacity to be added.
06TPIT0198 | Hickory Substation 69kV Bay Addition | Construct new 69kV bays to allow tie in of the new Iron Horse to Hickory transmission line | On Schedule |  |  | Complete | 07TPIT0095 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600128 | 2010-06-01 | 2010-05-01 | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910 | Y
07TPIT0095 | RD Wells to Hickory 69kV Transmission Line | Construct 1.6 miles of new 138kV transmission line to be operated at 69kV | On schedule |  |  | Complete | 07TPIT0091, 0092, 0094, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600130 | 2010-04-10 | 2010-05-01 | 69 | 1.6 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 932, 910 | Y
07TPIT0097 | Reconstruct 1.2 miles - Hickory to North Lakes 69kV Transmission Line | Reconstruct 1.2 miles of existing 69V transmission line | On schedule |  |  | Complete | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600775 | 2010-03-01 | 2010-05-01 | 69 | 0 | 1.2 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 910, 915 | Y
07TPIT0091 | RD Wells 138kV to 69kV Interchange | Construct a new 138kV to 69 kV 150MVA interchange | On schedule |  |  | Complete | 07TPIT0092, 0094,0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600005 | 2010-04-10 | 2010-05-01 | 138 | 0 | 0 | 168 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 930, 932 | Y
10TPIT0099 | Goldthwaite to Evant | The existing LCRA TSC 138 kV transmission line (approximately 24 miles) between the LCRA TSC Goldthwaite (7070) and Evant (7068) stations will be rebuilt. The rebuilt transmission line will consist of 1X795 ACSR conductor to provide a thermal rating of 220 MVA. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-05-30 | 2010-05-01 | 138 | 0 | 24 | 0 | 0 | MILLS | LAMPASAS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  |  | CREZ Default project assigned to LCRA TSC
10TPIT0131 | Elgin-Gilleland Creek | Upgrade the conductor on the 12.9-mile Elgin (3650)-Gilleland Creek (7336) 138 kV transmission line from 795 ACSR (220 MVA) to 1433 ACSS/TW (507 MVA). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-05-28 | 2010-05-01 | 138 | 0 | 12.9 | 0 | 0 | TRAVIS | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
08TPIT0128 | Stanton East - Big Spring Switch 138 kV line and Stanton East 138/69 kV autotransformer | Rebuild and convert an existing 69 kV line to a 138 kV line and install a 138/69 kV autotransformer at Stanton East | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8002-WACF | 2010-05-01 | 2010-05-01 | 138 | 0 | 21.6 | 60 | 0 | MARTIN | HOWARD | Tier 4 | 2008-12-12 | 2009-03-27 | 2009-07-21 | 1229, 1326, 1322, 1323 | Y
09TPIT0215 | Seadrift 69 kV substation | Construct new 69 kV substation connected to new line from Port O'Connor substation. Will tie to AEP Union Carbide in future. | Acquiring Right-Of-Way Easements |  |  |  | 05TPIT0092 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-04-30 | 2010-05-10 | 69 | 0 | 0 | 0 | 0 | CALHOUN |  | Tier 2 |  | 2001-06-22 | 2001-07-09 | 5598 | Y
10TPIT0124 | Port O'Conner to Seadrift 69 kV line | Construct new 12.4miles 795 MCM ACSR 69 kV line between the new Seadrift station and STEC's Port O'Connor substation. | In construction |  |  |  | 05TPIT0092 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-04-30 | 2010-05-10 | 69 | 12.4 | 0 | 0 | 0 | CALHOUN | CALHOUN | Tier 2 |  | 2001-06-22 | 2001-07-09 | 5596-5598 | Y
08TPIT0116 | CenterPoint Energy/TNMP Alvin interconnection | Build a new 345 kV, 3 breaker ring bus Meadow substation looped into Ckt.99 P.H. Robinson - Oasis. Move 345/138 kV autotransformer from PH Robinson to new Meadow substation for interconnection with TNMP 138 kV North Alvin bus. | IN-SERVICE |  |  |  | 07TPIT0161 | CNP, TNMP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-06-30 | 2010-05-17 | 345 | 0.1 | 0 | 500 | 0 | BRAZORIA |  | Tier 4 | 2006-07-25 | 2006-11-06 | 2007-01-16 | 43030, 42000, 42015 | Y |  |  | 1)_TNMP and CenterPoint Energy jointly studied project. 2)_No transmission circuits to be built, rebuilt or reconductored. 3) See Project #07TPIT0161 for reason for delay. 4) Moving P.H. Robinson Auto #3 (500MVA) to Meadow Substation 5) Meadow substation was formerly known as South Alvin.
09TPIT0013 | Skyline - Install a Third 345kV Autotransformer | Install one 600 MVA autotransformer at Skyline. | [5 empty] | CPS | S: Joe Rodriguez | S-0182 | 2010-05-26 | 2010-05-25 | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | Tier 4 | 2007-03-29 | 2007-04-20 | N/A | 5370 5371 | Y |  |  | There is no transmission line additions associated with this project
05TPIT0040 | Fairview to Aledo | Construct 138kv 795 line from Fairview to Aledo, rebuild Waples to Fairview radial | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-04-26 | 2010-05-27 | 138 | 32 | 5.8 | 0 | 0 | HOOD | PARKER | Tier 2 |  | 2002-09-01 | 2003-01-01 | 467, 470, 527, 526 | Y
10TPIT0130 | Hondo -138 kV Capacitor Bank | Install 18 MVAR Capacitor at the Hondo substation | [5 empty] | CPS | S: Thomas Fryer | S-0569 | 2010-05-28 | 2010-05-27 | 138 | 0 | 0 | 0 | 18 | BEXAR | BEXAR | Tier 4 |  |  |  | 5225 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0161 | Centerpoint Energy/TNMP Alvin Interconnection Project | Install 138 kV switching station on Alvin-Hastings transmission line and interconnect with Centerpoint 345-138 kV auto-transformer near Alvin. | Difficulties in acquistion of land of switching station site has delayed the project. |  |  |  | 08TPIT0116 | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | GCEC 27517, 27519 | 2010-05-01 | 2010-05-31 | 138 | 0 | 0 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 4 | 2006-07-06 | 2006-11-06 | 2007-01-07 | 39015 | Y |  | Autotransformer for this project is being relocated from PH Robinson.
10TPIT0116 | North Brady, Move DRCS from Rio Pecos to N Brady | Rebuild part of SAPS to Menard 138 kV line by replacing structures and Move SAPS auto and add DCRS at North Brady | IN-SERVICE |  |  |  | AEP GROUP 472 | AEP/TNC | Rue Galyean 918-599-2653 | 2358 | 2010-06-01 | 2010-06-01 | 69 | 0 | 0 | 0 | 0 | MCCULLOCH | MCCULLOCH | Tier 4 |  |  |  |  | Y
10TPIT0129 | Merida to Sommers - 138 kV Substation Equipment Upgrade | Replace Substation Equipment at Merida to remove MLSE on the Merida to Sommers 138kV transmission line | [5 empty] | CPS | S: David Riethmeyer | S-0565 | 2010-06-01 | 2010-06-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5310 5395 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
10TPIT0127 | Austin to Tuttle - 138 kV Substation Equipment Upgrade | Replace Substation Equipment at Austin to remove MLSE on the Austin to Tuttle 138kV transmission lines | [5 empty] | CPS | S: Keith Calle | S-0396 | 2010-06-01 | 2010-06-01 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5005 5435 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
10TPIT0107 | McNeil-Marshall Ford | Replace under-rated limiting line terminal equipment to increase McNeil (7334)-Marshall Ford (7356) to the conductor's rating. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-30 | 2010-06-01 | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
10TPIT0072 | Fayetteville-Willow Springs-New Bremen-Bellville South | Rebuild the 28-mile Fayetteville (7286)-Willow Springs (7273)-New Bremen (7271)-Bellville South (7270) 138 kV transmission line (T-216). Upgrade the conductor along the entire line to 1433 ACSS (450 MVA). | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-01 | 2010-06-01 | 138 | 0 | 28.2 | 0 | 0 | FAYETTE | AUSTIN | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y
11TPIT0046 | Twin Buttes (76009) to Coleman/Brown County Line | Add the second 345 kV circuit (approximately 88 miles) to existing transmission line, double circuit capable structures, between the LCRA TSC Twin Buttes station (76009) and the Oncor Brown station (1444). Circuit ownership changes with Oncor at the Coleman/Brown County line. The new circuit will consist of Cumberland conductor to provide a thermal rating of 2988 MVA. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-29 | 2010-06-01 | 345 | 88 | 0 | 0 | 0 | TOM GREEN | COLEMAN | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | N |  |  | CREZ Default project assigned to LCRA TSC
11TPIT0045 | Divide to Twin Buttes | Add the second 345 kV transmission line (approximately 31 miles) to existing double circuit capable structures between the LCRA TSC Divide (76090) and Twin Buttes (76009) stations. The new transmission line will consist of 2x1590 ACSR Falcon ACSS Merrimack conductor to provide a thermal rating of 1678 MVA. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-06-04 | 2010-06-01 | 345 | 31 | 0 | 0 | 0 | COKE | TOM GREEN | Tier 3 |  |  |  | SEE PROJECT DESCRIPTION | Y |  |  | CREZ Default project assigned to LCRA TSC
10TPIT0102 | Bowman - Jacksboro Switch 345 kV line | Rebuild existing 345 kV line. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C041-WA | 2010-06-01 | 2010-06-01 | 345 | 0 | 46.7 | 0 | 0 | ARCHER | JACK | CREZ |  |  |  | 1422, 1429 | Y |  |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
09TPIT0124 | Jacksboro Switch - Willow Creek 345 kV line | Rebuild 345 kV line for double-circuit operation. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C039-WA | 2010-06-01 | 2010-06-01 | 345 | 19.1 | 19.1 | 0 | 0 | JACK | WISE | CREZ |  |  |  | 1429, 1421 | Y |  |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. Cost is included in Willow Creek - Parker project.
10TPIT0156 | NW Carrollton Switch | Add 345 kV breaker. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C0008E | 2010-06-01 | 2010-06-01 | 345 | 0 | 0 | 0 | 0 | DALLAS |  | CREZ |  |  |  | 1730 | Y |  |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0106 | Killeen Switch - Salado Switch 345 kV line | Construct 345 kV line on existing structures | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C036-WA | 2010-03-01 | 2010-06-01 | 345 | 15.7 | 0 | 0 | 0 | BELL | BELL | CREZ |  |  |  | 3422, 3699 | Y |  |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
10TPIT0056 | Renner SVC Phase I | Install one static var compensator (+300 Mvar/-265 Mvar) | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4058-WA | 2010-06-02 | 2010-06-02 | 138 | 0 | 0 | 0 | 600 | DALLAS |  | Tier 1 | 2008-10-16 |  | 2009-02-01 | 12356, 12357 | Y |  |  | The first phase of the project was approved on 8/19/2008, and the second phase was approved on 2/2/2009. Phase I will go into service in May 2010, and Phase II will go into service in May 2011.
10TPIT0068 | Broadview to Fredericksburg Rd - 138kV line upgrade | Upgrade the existing Broadview to Fredericksburg Rd 138kV transmission line | [5 empty] | CPS | PM: Ulrich Skerhut | T-0133 | 2010-06-07 | 2010-06-08 | 138 | 0 | 2.3 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5040 5170 | Y |  |  | There are no transformers associated with this project
11TPIT0025 | Anderson to Westover Hills - New 138kV Transmission Line | Build new 138kV line from Anderson - Westover Hills |  |  |  |  | S-0439 | CPS | T: LeeRoy Perez PM: Bruce Raney | T-0200 | 2010-06-01 | 2010-06-08 | 138 | 1.8 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 2 | 2008-08-01 | 2008-10-01 |  | 5003 5488 | Y |  |  | There are no transformers associated with this project
08TPIT0067 | Fort Worth Substation | Construct new 25MVA, 138kV to 13.2kV substation adjacent to TMPA's 138kV transmission line where it intersects US377 | On schedule |  |  | Complete | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600821 | 2010-06-01 | 2010-06-10 | 138 | 0 | 4 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 919 | Y
06TPIT0010 | W. Levee - Norwood 345 kV line | Construct W. Levee - Norwood 345 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M477-WAC | 2010-06-01 | 2010-06-10 | 345 | 6.5 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 3 | 2003-10-01 | 2004-02-01 | 2004-04-01 | 2398, 2406 | Y
10TPIT0144 | Tombstone: Build new 138 kV Box Bay structure | Interconnect Occidental Petroleum into new Tombstone station | IN-SERVICE |  |  |  | AEP GROUP 473 | AEP/ETT | Brett Madison 918-599-2653 | 2360 | 2010-06-15 | 2010-06-15 | 138 | 0 | 0 | 0 | 0 | PECOS | PECOS | Tier 4 |  |  |  |  | Y
08TPIT0003 | Hutto Switch - Salado Switch 345 kV line | Construct Hutto Switch - Salado Switch 345 kV line and Salado 345 kV Switching Station |  |  |  |  | R456 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R445-WA | 2010-06-01 | 2010-06-15 | 345 | 73.8 | 0 | 0 | 0 | WILLIAMSON | BELL | Tier 1 |  |  | 2004-12-18 | 3699, 3696 | Y
10TPIT0008 | Hutto Switch and 345/138 kV autotransformer | Create 345 kV switching station and install a 345/138 kV autotransformer |  |  |  |  | R445 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R456-WA | 2010-06-01 | 2010-06-15 | 345 | 0 | 0 | 600 | 0 | WILLIAMSON |  | Tier 1 |  |  | 2004-12-18 | 3696, 3666 | Y
10TPIT0098 | Henderson Ranch Switching Station | Construct new switching station to connect a new power plant | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R580-WA | 2010-06-01 | 2010-06-17 | 345 | 0 | 0 | 0 | 0 | JACK |  | Tier 4 |  |  |  | 1443 | Y
10TPIT0042 | Ables Springs 138 kV line and point of interconnection (Oncor Electric Delivery portion only) | Construct 138 kV line and point of interconnection | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3055-WA | 2010-07-01 | 2010-06-21 | 138 | 15.67 | 4.97 | 0 | 0 | KAUFMAN | HUNT | Tier 2 | 2007-01-05 | 2007-05-01 | N/A | 12469, 12470 | Y |  |  | The point of interconnection and eastern line were placed into service in May 2010.
10TPIT0145 | Pelican 138 kV: Add second tap for generation interconnect | Cotton Wind Farm Interconnect Facilities | IN SERVICE |  |  |  | AEP GROUP 397 | AEP/ETT | Tommy Vannoy 918-599-2653 |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | SAN PATRICIO |  | Tier 4 |  |  |  |  | Y
09TPIT0185 | Quanum to Airpro to Shell Ckt.85 | Upgrade limiting equipment at Airpro substation to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 41330, 40070, 41450 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
10TPIT0128 | Sommers to Kirby & Sommers to Beck to Kirby - 138 kV Substation Equipment Upgrade | Replace Substation Equipment at O.W. Sommers, Beck Rd. and Kirby to remove MLSE on the Sommers to Kirby & Sommers to Beck to Kirby 138kV transmission lines | [5 empty] | CPS | S: Ricardo Renteria | S-0561 | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5395 5035 5250 | Y |  |  | There are no transmission line additions associated with this project There are no transformers associated with this project
07TPIT0043 | Wynn Joyce-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  | Switch 9122 at Wynn Joyce | Switch 1420 at Miller | Completed |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 2.81 | 0 | 0 | DALLAS | [5 empty] | 811, 824 | Y | N
07TPIT0044 | Miller 69 kV to 138 kV voltage conversion | Converts voltage for the substation | [5 empty] | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 0 | 0 | 0 | DALLAS | [5 empty] | 824 | Y
07TPIT0046 | Newman-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  | Switch 938 at Newman | Switch 1419 at Miller | Completed |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 2.27 | 0 | 0 | DALLAS | [5 empty] | 814, 824 | Y | N
07TPIT0047 | Centerville-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  | Switch 1376 at Centerville | Switch 1418 at Miller | Completed |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-06-30 | 2010-06-30 | 138 | 0 | 2.68 | 0 | 0 | DALLAS | [5 empty] | 810, 824 | Y | N
10TPIT0137 | Krum Tap 138 kV Switching Station | Construct 138 kV switching station |  |  |  |  | R510D-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510C-WACF | 2010-06-01 | 2010-06-30 | 138 | 0 | 1 | 0 | 0 | DENTON |  | Tier 3 | 2008-01-14 | 2008-05-19 | N/A | 1582, 1568, 1987, 1990, 1986 | Y
10TPIT0138 | Krum Tap 138 kV line | Rebuild existing 138 kV line |  |  |  |  | R510C-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510D-WA | 2010-06-01 | 2010-06-30 | 138 | 0 | 3.3 | 0 | 0 | DENTON | DENTON | Tier 3 | 2008-01-14 | 2008-05-19 | N/A | 1987, 1986 | Y
09TPIT0194 | Taylor Expansion | Close in 138kV ring bus at Taylor Substation | New |  |  |  |  | SU | Dwight Yarbrough, 956-687-5600, dyarbrough@sharylandUtilties.com | PR08.05149.CAP | 2010-07-01 | 2010-07-15 | 138 | 0.2 | 0 | 0 | 0 | HIDALGO |  | Tier 4 |  |  |  | 8821 | Y |  |  | CCN 30192
09TPIT0190 | Spunky to Georges Creek and New Hope Rebuilds | Rebuild Spunky to New Hope and Spunky to Georges Creek with 795 ACSR conductor | [5 empty] | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-09-15 | 2010-07-16 | 69 | 0 | 10.2 | 0 | 0 | JOHNSON | SOMERVELL | Tier 4 |  |  |  | 357384387 | Y
09TPIT0179 | SLU Taylor Road Substation: Loop station into line | Hairpin SLU Taylor Substation into South McAllen to Frontera 138kV Line | IN-SERVICE |  |  |  | AEP GROUP 458 | AEP/TCC/SLU | Rich Haley 918-599-2653 | 3326 | 2010-07-23 | 2010-07-23 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  |  | Y
10TPIT0155 | Cedar Hill Switch 345/138 kV autotransformer | Replace failed autotransformer | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4083A-E | 2010-08-01 | 2010-08-01 | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 |  |  |  | 2420,2422, 2421 | Y
09TPIT0083 | P.H. Robinson - Oasis Ckt.99 | Raise conductors and upgrade in-series equipment at P.H. Robinson to increase thermal rating. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-06-30 | 2010-08-17 | 345 | 0 | 20.45 | 0 | 0 | GALVESTON | BRAZORIA | Tier 4 |  |  |  | 42000, 43035 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
10TPIT0117 | TECO Generation | Interconnect a new generation plant at TECO substation. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-09-30 | 2010-08-24 | 138 | 0 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 48865, 47430 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. Commercial operation scheduled for June 2010
05TPIT0092 | Seadrift to AEP Union Carbide 69 kV line | Construct new 12.4 miles 795 MCM ACSR 69 kV line between the AEP Union Carbide station and STEC's new Seadrift substation. | Construction delays- weather |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-09-01 | 2010-09-01 | 69 | 12.4 | 0 | 0 | 0 | CALHOUN | CALHOUN | Tier 2 |  | 2001-06-22 | 2001-07-09 | 5598-80135 | Y
10TPIT0140 | Second Hasse 138 / 69 Autotransformer | Install 40 MVA 138 / 69 kV autotransformer at Hasse | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-09-23 | 2010-09-22 | 138 | 0 | 0 | 40 | 0 | COMANCHE |  | Tier 4 |  |  |  | 277, 1649 | Y
10TPIT0135 | La Quinta: Temporary Connection into Falfurrias to Lobo 138kV Line | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm | IN SERVICE |  |  |  | AEP GROUP 398 | AEP/ETT | Tommy Vannoy 918-599-2653 | 3353 | 2010-09-27 | 2010-09-27 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y
09TPIT0133 | Jim Christal Substation 138kV Reconstruction | Reconstruct 138kV section of the station installing five 138kV circuit breakers to break the Denton West to Denton North transmission line into two sections | On schedule |  |  | Complete | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602153 | 2010-11-01 | 2010-10-01 | 69 | 0 | 2 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 916 | Y
09TPIT0135 | CSU Dowling Road Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities | [5 empty] | BTU/CSU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2010-09-01 | 2010-10-01 | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
10TPIT0100 | Tippett (76001) to North McCamey (76032) | Add the second 138 kV transmission line (approximately 15 miles) to existing double circuit capable structures between the LCRA TSC North McCamey station (76032) and the new Tippett station (76001). The new transmission line will consist of 2X795 ACSR conductor to provide a thermal rating of 448 MVA. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2010-10-01 | 2010-10-10 | 138 | 15 | 0 | 0 | 0 | UPTON | UPTON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y |  |  | CREZ Default project assigned to LCRA TSC
10TPIT0147 | San Miguel to Pawnee 138 kV reroute | Reroute San Miguel to Pawnee 138 kV circuit to parallel 345 kV circuit per PUCT order | [5 empty] | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2010-11-01 | 2010-10-10 | 138 | 0 | 11 | 0 | 0 | ATASCOSA | KARNES | Tier 4 |  |  |  | 5902-5727 | Y
10TPIT0126 | Galveston Area 138kV Circuit Upgrades Phase One | Reconductor a portion of 138 kV Ckt. 93 PH Robinson - Alta Loma to increase thermal ratings. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 | 2010-10-15 | 138 | 0 | 5.34 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 42015, 42061 | Y |  |  | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan.
10TPIT0113 | Odessa EHV Third 345/138 kV autotransformer | Install 345/138 kV autotransformer and tertiary shunt reactors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8004-WA | 2010-12-15 | 2010-11-01 | 345 | 0 | 0 | 504 | -75 | ECTOR |  | Tier 4 |  |  | 2009-07-21 | 1027, 1028 | Y |  | 2009-R6 | ERCOT BOD approved this project as part of the RMR exit strategy for Permian Basin generation.
09TPIT0170 | Tyler Bullard Road terminal equipment | Replace terminal equipment | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R836-WA | 2010-10-01 | 2010-11-02 | 138 | 0 | 0 | 0 | 0 | SMITH |  | Tier 4 |  |  |  | 3219 | Y |  | 2009-R37
10TPIT0118 | Bandera-Verde Creek Rebuild | Rebuild and upgrade the 15 mile Bandera - Verde Creek 336 ACSR 138kV transmission line to 2- 795 ACSR 138kV. | [5 empty] | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 134142 | 2010-11-10 | 2010-11-10 | 138 | 0 | 15 | 0 | 0 | BANDERA | KENDALL | CREZ |  |  |  |  | N |  |  | The project will now to bundle the 795 conductor per ERCOT recommendation.
10TPIT0119 | Add 2nd Autotransformer at Bandera | Install a second 24/32/40 MVA 138/69kV autotransformer at Bandera Substation. | [5 empty] | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 151272 | 2010-11-10 | 2010-11-10 | 138 | 0 | 0 | 40 | 0 | BANDERA | BANDERA | CREZ |  |  |  |  | N
07TPIT0034 | Medina Lake-Pipe Creek Rebuild (formally (Medina Lake-CPS Cagnon (Part 2)) | Rebuild and upgrade the 7.8 mile Pipe Creek (7437) - Medina Lake (7432) 1/0 ACSR 69kV transmission line to 795 ACSR 138kV. |  |  |  |  | 06TPIT0080 | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 57596 | 2010-11-10 | 2010-11-10 | 138 | 0 | 7.8 | 0 | 0 | BANDERA | BANDERA | Tier 4 | 2003-10-01 | 2003-11-01 |  | See Project Description | Y |  |  | This project was formally known as Medina Lake - CPS Cagnon (Part 2). Submissions to ERCOT RPG for review where concurrent with Medina Lake - CPS Cagnon (Part 1)
09TPIT0018 | Reagor Springs to India Rebuild/Upgrade | Upgrade/rebuild existing Reagor Springs. to India line | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-11-16 | 2010-11-11 | 69 | 0 | 17 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 210, 214, 215 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0142 | Waples Capacitor | Install 36 MVA capacitor bank at Wapels 138 kV bus | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-12-05 | 2010-11-24 | 138 | 0 | 0 | 0 | 36 | HOOD |  | Tier 4 |  |  |  | 467 | Y
10TPIT0132 | Britmore - Addicks Ckt.09 Reconductor | Upgrade 138 kV Ckt.09 Britmore - Addicks to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-12-31 | 2010-11-29 | 138 | 0 | 2.03 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 44120, 45610 | Y |  |  | No transformer capacity to be added.
11TPIT0095 | Renner SVC Phase II | Install one static var compensator (+300 Mvar/-265 Mvar) | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4058B-WA | 2010-12-01 | 2010-12-01 | 138 | 0 | 0 | 0 | 300 | DALLAS |  | Tier 1 | 2008-10-16 |  | 2009-02-01 | 12356, 12357 | Y |  |  | The first phase of the project was approved on 8/19/2008, and the second phase was approved on 2/2/2009. Phase I will go into service in May 2010, and Phase II will go into service in May 2011.
10TPIT0101 | Willow Creek - Parker 345 kV line | Rebuild 345 kV line for double-circuit operation. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C040-WA | 2010-12-01 | 2010-12-01 | 345 | 22.25 | 22.25 | 0 | 0 | WISE | PARKER | CREZ |  |  |  | 1421, 1436 | Y |  |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report. Cost covers entire Jacksboro Switch - Willow Creek - Parker 345 kV line.
10TPIT0154 | Penascal Wind Phases 2 Generation Interconnect | Penascal Wind Phases 2 and 3 Install ERCOT EPS Metering | IN-SERVICE |  |  |  | 038 - 0489 | AEP/ETT/TCC | John Pulay 918-599-2653 | 3381 | 2010-12-13 | 2010-12-13 | 345 | 0 | 0 | 0 | 0 | KENNEDY |  | Tier 4 |  |  |  |  | Y
10TPIT0157 | Relocation of Line 138-S for Road work on FM 524 | Relocate impacted 138kV transmission line segment for Farm to Market Road 524 work | [5 empty] | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE07310 | 2010-12-10 | 2010-12-17 | 138 | 0 | 0.75 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 4 |  |  |  |  | N
12TPIT0077 | Liggett 345/138 kV Autotransformer #1 | Replace 480 MVA Autotransformer | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5107-WAC | 2010-12-01 | 2010-12-17 | 345 | 0 | 0 | 600 | 0 | DALLAS |  | Tier 4 | 2008-06-01 | 2008-07-01 |  | 1923, 1926 | Y |  | 2007-R5
11TPIT0073 | Kirby - Garrott Ckt. 37 | Upgrade 138kV Ckt. 37 Kirby - Garrott to increase thermal ratings. | IN-SERVICE |  |  |  | 11TPIT0072 | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-12-31 | 2010-12-19 | 138 | 0 | 2.32 | 0 | 0 | HARRIS | HARRIS | Tier 3 | 2009-07-01 | 2009-07-01 | N/A | 47320, 47660 | Y |  |  | Part of Garrott - Midtown - Polk Ckt. 90 Upgrade
11TPIT0105 | La Palma to San Benito: Rebuild 0.2 miles | Construct a new 138/69 kV Switching Station near East Harrison substation and reconductor the 69 kV line from La Palma to San Benito | IN-SERVICE |  |  |  | 362 - 0537 | AEP/TCC | Rich Haley 918-599-2653 | 3368 | 2010-12-31 | 2010-12-22 | 138 | 0 | 0.2 | 0 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  |  | Y
08TPIT0009 | Hutto Switch - Round Rock NE - Round Rock 138 kV line | Rebuild existing 138 kV single-circuit line from Hutto Switch to Round Rock with larger conductor and double-circuit structures and add a second circuit to structures to create a Hutto Switch - Round Rock circuit and a Hutto Switch - Gabriel (LCRA) circuit. |  |  |  |  | R456 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R406-WAC | 2010-12-01 | 2010-12-22 | 138 | 8.4 | 8.9 | 0 | 0 | WILLIAMSON | WILLIAMSON | Tier 4 |  |  |  | 3666, 3670, 3667, 3669, 3668 | Y |  |  | Hutto Switch - Round Rock NE section will be completed in June 2010.
09TPIT0173 | Waco West - Waco Woodway - Waco Atco 138 kV line | Rebuild existing line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R409-WAC | 2010-12-01 | 2010-12-29 | 138 | 0 | 5.84 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 | 2008-07-07 |  |  | 3436, 3591, 3592 | Y |  |  | Project submitted to RPG by Luminant.
09TPIT0077 | McCree-Shiloh 138 kV line | Line reconductor |  | Switch 1392 at McCree | Switch 8722 at Shiloh | Completed |  | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2010-12-31 | 2010-12-31 | 138 | 0 | 2.2 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 830, 834 | Y | N
10TPIT0114 | Roanoke Tap to West Denton 345kV CREZ Circuit | Add 345kV circuit to vacant position of TMPA-owned double circuit line from Roanoke Tap over West Denton | Delayed due to coordination with Oncor construction schedule for remainder of line |  |  |  |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T09003 | 2010-12-31 | 2010-12-31 | 345 | 9.8 | 0 | 0 | 0 | DALLAS |  | CREZ |  |  |  | 988, 1730, 2361 | Y
09TPIT0022 | Killeen Switch - S. Harker Heights 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R410-WAC | 2011-01-01 | 2011-01-01 | 138 | 0 | 5.3 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 3633 | Y
06TPIT0167 | MVEC Merett-MVEC Pharr | Rebuild 138kV line from Merett to MVEC Pharr Substations | Clearance extended to 1-14-11 |  |  |  | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 984505 | 2010-12-30 | 2011-01-01 | 138 | 0 | 2.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8752-8762 | Y
11TPIT0127 | Graham 345/138 kV autotransformer | Replace existing autotransformer | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R904A-WAC | 2011-05-01 | 2011-01-01 | 345 | 0 | 0 | 350 | 0 | YOUNG |  | Tier 4 |  |  |  | 1596, 1430 | Y
11TPIT0113 | Oasis - Meadow Ckt.99 | Upgrade 345kV Ckt. 99 Oasis to Meadow to increase thermal ratings. | IN-SERVICE |  |  |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2010-12-31 | 2011-01-07 | 345 | 0 | 3.91 | 0 | 0 | BRAZORIA | BRAZORIA | Tier 4 |  |  |  | 43035, 43030 | Y |  |  | 1) Identified by ERCOT as an Economic Project in 2009 5-Year Plan. Needed by summer peak 2011. 2) No transformer capacity to be added.
10TPIT0108 | Dowling Rd Substation Additions | Build new distibution substation in BTU transmission line from BTU South Switch to TAMU Substation | [5 empty] | COCS/BTU | Tony Michalsky 979- 764-3438 tmichalsky@cstx.gov |  | 2011-01-01 | 2011-01-11 | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
08TPIT0032 | Gilleland 345/138kV autotransformer | Install a 672 MVA 345/138kV autotransformer at the new Gilleland switching substation | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-01-01 | 2011-01-11 | 345 | 0 | 0 | 672 | 0 | TRAVIS |  | Tier 4 |  |  |  | The 345kV bus is 7340 and the 138kV bus is 7336 | Y
08TPIT0042 | Seaton to Barclay Rebuild | Rebuild existing Seaton to Barclay with 1033 ACSR | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2010-12-23 | 2011-01-20 | 69 | 0 | 10.2 | 0 | 0 | BELL | FALLS | Tier 4 |  |  |  | 69131 | Y |  |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0119 | Whitesboro SE - Gordonville 138 kV tap line | Construct 138 kV line and convert existing 69 kV line and substations to 138 kV operation. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R546-WAC | 2011-01-01 | 2011-01-25 | 138 | 0.9 | 7.9 | 0 | 0 | GRAYSON | GRAYSON | Tier 4 |  |  |  | 1744, 1725 | Y
08TPIT0020 | Zorn/Clear Springs-Gilleland Creek-Hutto Switch 345-kV line | Construct a 345 kV double circuit (bundled 959 ACSS) line between Zorn/Clear Springs and Hutto Switch and other ONCOR and AE projects. Upgrade the 7.5-mile McNeil (7334)-Gilleland(7336) 795 ACSR 138-kV transmission line to 1433 ACSS/TW. | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org | Not yet assigned | 2011-02-01 | 2011-02-01 | 345 | 165 | 7.5 | 0 | 0 | WILLIAMSON | GUADALUPE | Tier 1 | 2001-12-01 | 2001-12-01 | 2002-02-01 | 7042, 7050, 7340, 3696 | Y |  |  | Harris Branch substation replaced with Gilleland Creek substation as an in-line termination point for one of the
09TPIT0098 | Dilley, add 138 kV terminal | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to Dilley | IN-SERVICE |  |  |  | 382 - 0559 | AEP/TCC | Brian Johnson 918-599-2653 | 3098 | 2011-02-17 | 2011-02-11 | 138 | 0 | 0 | 0 | 0 | FRIO | FRIO | Tier 1 | 2006-01-01 | 2006-08-01 | 2006-08-01 |  | Y
11TPIT0126 | Cactus tap located on the Ft. Lancaster to West Yates 69 kV line | SouthWest Texas Electric Co-Op distribution station | IN-SERVICE |  |  |  | 491 - 0692 | AEP/TNC | Joe Gilbert 918-599-2653 | 2429 | 2011-02-16 | 2011-02-16 | 69 | 0 | 0 | 0 | 0 | CROCKETT | CROCKETT | Tier 4 |  |  |  |  | Y
07TPIT0055 | Frisco to Kruegerville Rebuild | Rebuild existing Frisco to Kruegerville with1590 or Acss conductor | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-08 | 2011-02-16 | 138 | 0 | 11.7 | 0 | 0 | COLLIN | DENTON | Tier 3 | 2009-10-13 | 2009-11-01 | N/A | 662, 1994, 681 | Y
08TPIT0085 | Palo Duro Switching Station | Construct a new Palo Duro switching substation in the 138 kV transmission line, from Pearsall to Batesville, at the point where the line changes from a north/south direction to an east/west direction, ties-in new 138 kV transmission line to AEP Dilley. | Negotiation of site is in progress. Acquiring Right-Of-Way Easements. |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 | 2011-02-17 | 138 | 0 | 0 | 0 | 0 | FRIO |  | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5866 | Y
08TPIT0094 | Palo Duro to AEP Dilley SS 138 kV Line | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to AEP Dilley. | Changed responsibility to STEC |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 | 2011-02-17 | 138 | 9 | 0 | 0 | 0 | FRIO | FRIO | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5866-8212 | Y
09TPIT0189 | Pearsall to Dilley 69 kV Line | Upgrade 21.8 miles of 69 kV to 795 ACSR conductor from Pearsall to Derby to Dilley. | Upgrade 69 kV line for new generation at Pearsall |  |  |  |  | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-01-01 | 2011-02-25 | 69 | 0 | 21.8 | 0 | 0 | FRIO | FRIO | Tier 4 | 2006-02-01 | 2006-06-29 | 2006-08-01 | 5893-5842--5860 | Y
10TPIT0076 | Stephenville to Granbury 138KV Conversion | Convert exisitng Stephenville to Granbury 69KV line to 138KV operation | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-01-04 | 2011-02-25 | 138 | 0 | 0 | 0 | 0 | HOOD | ERATH | Tier 4 |  |  |  | 306, 307, 309, 306, 305, 304, 303, 299 | Y
10TPIT0050 | Rayburn Substation | Install (3) Breaker ring to include (2) 69 lines and (1) 69/12.5 transformer | [5 empty] | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2011-02-28 | 2011-03-01 | 69 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y
11TPIT0088 | La Quinta: Configure station to 3 breaker ring bus | Construct new 138kV La Quinta Substation to directly interconnect 150MW Cedro Hill Wind Farm | Schedule Update |  |  |  | 398 - 0587 | AEP/ETT | Tommy Vannoy 918-599-2653 | 3351 | 2012-03-31 | 2011-03-01 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB | Tier 4 |  |  |  |  | Y
10TPIT0021 | Krum West Switch - NW Carrollton 345 kV circuit (Oncor Electric Delivery section) | Add second 345 kV circuit on existing structures . |  |  |  |  | C017 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C037-WA | 2011-03-01 | 2011-03-01 | 345 | 37.2 | 0 | 0 | 0 | DENTON | DALLAS | CREZ |  |  |  | 988, 1730, 2361 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
08TPIT0162 | Convert Alta Loma 69/138kV dual voltage substation to a 138kV substation. | Convert Alta Loma 69/138kV dual voltage double tap configuration substation to a 138kVsectionalizing substation looped into Ckt.93 PH Robinson to Hitchcock. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-03-31 | 2011-03-02 | 138 | 0 | 0.1 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 42061, 42062 | Y |  |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
12TPIT0055 | Hill Country to Stonegate - 138 kV 2nd Circuit | Build second 138kV transmission line from Hill Country to Stonegate on existing transmission structures |  |  |  |  | S-0580 | CPS | PM: Hector Torres | T-0163 | 2011-03-17 | 2011-03-08 | 138 | 10.01 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5209 5415 | Y |  |  | There are no transformers associated with this project
11TPIT0141 | Ft. Lancaster to Illinois #4, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE |  |  |  | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2437 | 2011-03-31 | 2011-03-09 | 69 | 0 | 17.21 | 0 | 0 | PECOS | CROCKETT | CREZ Modified |  |  |  |  | Y
11TPIT0119 | Texas Substation Conversion | Convert Texas substation from 69kV to 138kV service. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-04-30 | 2011-03-09 | 138 | 0.76 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 41550, 41540 | Y |  |  | No transformer capacity to be added.
11TPIT0148 | Ayers 138 kV terminal equipment | Upgrade terminal equipment on line from Handley to Hemphill | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5169-WAC | 2011-05-01 | 2011-03-11 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 1950, 2167, 2164 | Y
07TPIT0018 | Lewisville Switch (Brazos) - Highland (TNMP) 138 kV line (Oncor portion) | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5067-WAC | 2011-05-01 | 2011-03-14 | 138 | 0 | 1.6 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | 2010-06-15 | 645, 1970 | Y
10TPIT0123 | Sioux 138 kV substation | Build New 138kV Sioux Substation in the Line from Doedyns-Gandy. | Acquiring Right-Of-Way Easements on Sioux-Gandy T/L |  |  |  | 06TPIT9999 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-03-01 | 2011-03-16 | 138 | 0 | 0 | 0 | 0 | HIDALGO |  | Tier 4 |  |  |  | 8792 | Y
06TPIT9999 | Sioux-Gandy 138kV Line | Build New 138kV Line from Sioux-Gandy Substations | Acquiring Right-Of-Way Easements |  |  |  | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org | 789640 | 2011-03-01 | 2011-03-16 | 138 | 4.5 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 2 | 2005-02-01 | 2005-04-20 |  | 8792-8755 | Y
11TPIT0160 | Bruni auto upgrade | Upgrade the 18 MVA138/69 kV autotransformer. | [5 empty] | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-04-01 | 2011-03-16 | 138 | 0 | 0 | 37 | 0 | WEBB |  | Tier 4 |  |  |  | 5887, 5888 | Y
08TPIT0068 | Collin - Frisco (Brazos) 138 kV line | Upgrade existing 138 kV line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M596-WAC | 2011-05-01 | 2011-03-18 | 138 | 0 | 1.7 | 0 | 0 | COLLIN | DENTON | Tier 4 |  |  | 2010-06-15 | 2370, 681 | Y |  | 2009-R14
11TPIT0137 | Hilltop Lakes Auto | Replace 40 MVA, 138/69 kV auto with 60 MVA auto | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-01 | 2011-03-21 | 138 | 0 | 0 | 60 | 0 | MADISON |  | Tier 4 |  |  |  | 47, 48 | Y
11TPIT0093 | Saginaw Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5160-WAC | 2011-05-01 | 2011-03-29 | 138 | 0 | 0 | 0 | 55.2 | TARRANT |  | Tier 4 |  |  |  | 1957 | Y
11TPIT0116 | FM 237 Yorktown - New Substation | Construct a new 69-13.09x26.18-KV, 7.0 MVA substation | [5 empty] | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-04-11 | 2011-03-31 | 69 | 0 | 0 | 0 | 0 | DEWITT |  | Tier 4 |  |  |  | See Project Title | Y
11TPIT0161 | Pt Lavaca to Pt Oconnor | Upgrade miles of 69 kV from 4/0 to 795 ACSR conductor between Pt Lavaca and Pt Oconnor. | [5 empty] | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-04-01 | 2011-04-01 | 69 | 0 | 20.1 | 0 | 0 | CALHOUN | CALHOUN | Tier 4 |  |  |  | 5592-5596 | Y
11TPIT0053 | Gresham Road 138 kV Switching Station | Construction switching station to connect a new power plant | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6000-WAC | 2011-06-01 | 2011-04-01 | 138 | 0 | 0 | 0 | 0 | NACOGDOCHES |  | Tier 4 |  |  |  | 3301 | Y
11TPIT0121 | Parker - Comanche Peak - Everman 345 kV line | Connect Parker - Everman 345 kV line into Comanche Peak | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com |  | 2011-05-01 | 2011-04-01 | 345 | 0 | 0 | 0 | 0 | SOMERVELL |  | Tier 2 | 2009-07-01 | 2010-03-31 |  | 1900 | Y
09TPIT0105 | Rattlesnake Road Switch - Lake Creek 345 kV line | Upgrade existing 345 kV line |  |  |  |  | R499 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R499A-E | 2011-09-01 | 2011-04-04 | 345 | 0 | 1.5 | 0 | 0 | MCLENNAN | MCLENNAN | Tier 4 |  |  |  | 3399, 3409 | Y
10TPIT0047 | Zenith 345kV Switching Station | Build a new 345 kV Zenith substation. Loop Ckt.99 Singleton - Obrien, Ckt.98 Singleton - T.H. Wharton, Ckt 98 T.H. Wharton - Obrien into the new substation. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 | 2011-04-06 | 345 | 1 | 0 | 0 | 0 | HARRIS |  | Tier 3 | 2007-04-28 | 2007-07-16 | 2007-08-21 | 44900 | Y |  |  | Added to Houston Area Constraint Mitigation Project, Phase II per discussion with ERCOT.
11TPIT0159 | AGRI 69kV Substation | Disconnect customer owned AGRI 69kV substation from CNP service. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-04-30 | 2011-04-20 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 40051 | Y
11TPIT0112 | Hockley - Peters Ckt.58 | Convert Hockley to Peters Ckt. 58 from 69kV to 138kV | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 | 2011-04-20 | 138 | 0 | 28.5 | 0 | 0 | HARRIS | AUSTIN | Tier 4 |  |  |  | 45890, 46250, 46230 | Y |  |  | No transformer capacity to be added. After completion of conversion to 138kV, Ckt. 58 will become Ckt. 65.
10TPIT0044 | Marbach substation removal - Reconfigure 138kV lines at Marbach and Cagnon | Reroute the 138kV lines at Marbach and Cagnon. Due to removal of the Marbach substation. |  |  |  |  | S-0401 | CPS | T: Aaron Finley PM:Hector Torres | T-0129 | 2011-06-01 | 2011-04-21 | 138 | 0.3 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5295 | Y |  |  | There are no transformers associated with this project
11TPIT0051 | Riley, Build 345 kV switch station, cutting in the existing Oklaunion to Bowman 345 kV line | Build new Riley 345 kV switch station, cut in the existing and future 345 kV lines as described in ERCOT CREZ Scenario 2 | IN-SERVICE |  |  |  | 467 - 0668 | AEP/ETT | Tommy Vannoy 918-599-2653 | 2350 | 2011-05-27 | 2011-04-28 | 345 | 0 | 0 | 0 | 0 | WILBARGER | WILBARGER | CREZ Modified |  |  |  |  | Y
11TPIT0149 | Hemphill 138 kV terminal equipment | Upgrade terminal equipment on line to Randol Mill | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5167-WAC, M5167B-WAC & M5167C-WAC | 2011-05-01 | 2011-04-29 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2105 | Y
11TPIT0150 | Hemphill 138 kV terminal equipment | Upgrade terminal equipment on line to Ayers | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5167D-E & M5167E-E | 2011-05-01 | 2011-04-29 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2167 | Y
11TPIT0117 | Leakey | Remove a 15.6 MVAR Capacitor bank from the Bandera substation (7439) and add a 15.6 MVAR capacitor bank at the Leakey substation (7426) | [5 empty] | LCRA TSC | Brad Woods (512) 369-4104 brad.woods@lcra.org |  | 2011-04-01 | 2011-05-01 | 69 | 0 | 0 | 0 | 0 | BANDERA | REAL | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
14TPIT0019 | Orange Grove Switch to Orange Grove Sub upgrade | Upgrade 0.21 miles of 69 kV circuit between Orange Grove Switch and Orange Grove Sub | [5 empty] | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-06-01 | 2011-05-01 | 69 | 0 | 0.21 | 0 | 0 | JIM WELLS | JIM WELLS | Tier 4 |  |  |  | 5658 - 5662 | Y
11TPIT0166 | Alazan to Nelson Sharpe 138 kV line rebuild | Barney Davis to Nelson Sharpe 138 kV line rebuild 1st circuit on a double circuit capable structure | IN-SERVICE |  |  |  | 400 - 0647 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3360 | 2011-06-01 | 2011-05-01 | 138 | 0 | 10.1 | 0 | 0 | NUECES | NUECES | Tier 1 |  |  |  |  | Y
11TPIT0054 | Abilene South - Leon 138 kV line (Oncor Electric Delivery's section) | Rebuild existing 69 kV line for 138 kV operation. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C042-E | 2011-06-01 | 2011-05-01 | 138 | 0 | 8.4 | 0 | 0 | EASTLAND | EASTLAND | CREZ |  |  |  | 1624 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0128 | Leon Switch | Install 138 kV breaker. | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C042-E | 2011-06-01 | 2011-05-01 | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ |  |  |  | 1624 | Y |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0152 | Randol Mill 138 kV terminal equipment | Upgrade terminal equipment on Hemphill - Randol Mill - Handley/Saginaw line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5168-WAC, M5168B-WAC, M5168C-WAC & M5168D-WAC | 2011-05-01 | 2011-05-01 | 138 | 0 | 0 | 0 | 0 | TARRANT | TARRANT | Tier 4 |  |  |  | 2164, 2105, 2103, 2104, 2106 | Y
09TPIT0101 | Oleander, Construct 138/69 kV Substation | Construct a new 138/69 kV Switching Station near East Harrison substation and reconductor the 69 kV line from La Palma to San Benito | IN-SERVICE |  |  |  | 362 - 0537 | AEP/TCC | Rich Haley 918-599-2653 | 3101 | 2011-05-31 | 2011-05-02 | 138 | 0 | 0 | 130 | 0 | CAMERON | CAMERON | Tier 4 |  |  |  | 80023, 80022 | Y
11TPIT0094 | Venus Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3096-WAC | 2011-05-01 | 2011-05-04 | 138 | 0 | 0 | 0 | 110.4 | ELLIS |  | Tier 4 |  |  |  | 1908 | Y
11TPIT0151 | Mesquite 138 kV terminal equipment | Upgrade terminal equipment on the E Mesquite - Mesquite - Seagoville Switch line | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4046-WAC | 2011-05-01 | 2011-05-05 | 138 | 0 | 0 | 0 | 0 | DALLAS | DALLAS | Tier 4 |  |  |  | 2771, 2775, 2776 | Y
11TPIT0056 | Cisco, Convert station to 138 kV | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE |  |  |  | 466 - 0666 | AEP/TNC | Dave Goetz 918-599-2653 | 2341 | 2011-06-30 | 2011-05-06 | 138 | 0 | 0 | 0 | 0 | EASTLAND |  | CREZ Modified |  |  |  |  | Y
07TPIT7777 | MVEC Pharr-Alberta Switch | Rebuild 138kV line from Pharr to Alberta Switch Substations | Delay of Start of Construction to 1-17-11 |  |  |  | 06TPIT0166 | STEC | Doug Evans 361-485-6459 devans@stec.org |  | 2011-05-01 | 2011-05-06 | 138 | 0 | 1.2 | 0 | 0 | HIDALGO | HIDALGO | Tier 4 |  |  |  | 8759-8762 | Y
11TPIT0090 | Benbrook Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5158-WAC | 2011-05-01 | 2011-05-13 | 138 | 0 | 0 | 0 | 220.8 | TARRANT |  | Tier 4 |  |  |  | 1874, 1875 | Y
11TPIT0091 | Elkton Switch capacitors | Install 138 kV capacitors | [5 empty] | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R6003-WA | 2011-05-01 | 2011-05-13 | 138 | 0 | 0 | 0 | 110.4 | SMITH |  | Tier 4 |  |  |  | 3106 | Y
10TPIT0141 | Olney to Rice | Rebuild existin Olney to Rice 138 kV line | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-29 | 2011-05-16 | 138 | 0 | 17.1 | 0 | 0 | YOUNG | YOUNG | Tier 4 |  |  |  | 787, 1477 | Y |  |  | 2009-R10
11TPIT0132 | Olney 2nd Auto | Add 60 MVA, 138/69 kV auto | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-09 | 2011-05-16 | 138 | 0 | 0 | 60 | 0 | YOUNG |  | Tier 4 |  |  |  | 787, 788 | Y
10TPIT0069 | Thomaston: Install 138 kV PST, Add 3-28.8 MVAR Cap Banks, Reterminate 138 kV Line | Upgrade Thomaston substation to 3 breaker ring bus, install 180/200 MVA PST on Thomaston to LCRA Cuero 138 kV line. | IN-SERVICE |  |  |  | 402 - 0653 | AEP/ETT/TCC | Dave Goetz 918-599-2653 | 3264 | 2011-05-31 | 2011-05-19 | 138 | 0 | 0 | 150 | 86.4 | DEWITT |  | Tier 4 |  |  |  |  | Y
11TPIT0124 | Construct Service to Crystal Bay 138kV Substation | Serve substation by looping into Ckt.84 Borden to Dowlap. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-05-31 | 2011-05-20 | 138 | 0.2 | 0 | 0 | 0 | HARRIS |  | Tier 4 |  |  |  | 40290 | Y |  |  | No transformer capacity to be added.
11TPIT0005 | Talley Rd - New 138kV Substation | Loop new 138kV substation into future 138kV Medina Lake to CPS line (06TPIT0080) |  |  |  |  | T-0160 | CPS | PM: Ulrich Skerhut | S-0383 | 2011-06-01 | 2011-05-26 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5422 | Y |  |  | There are no transformers associated with this project
11TPIT0021 | Nassau Bay to Nassau Bay Sw. Rebuild | Rebuild existing 138 kV 4/0 line from Nassau Bay to Nassau Bay Sw. with 1033 double-circuit construction | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-03 | 2011-05-30 | 69 | 0 | 1.21 | 0 | 0 | HOOD | HOOD | Tier 4 |  |  |  | 364373451455 | Y
11TPIT0087 | Putnam, Recofigure Station | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE |  |  |  | 466 - 0666 | AEP/TNC | Dave Goetz 918-599-2653 | 2400 | 2011-05-31 | 2011-05-31 | 138 | 0 | 0 | 0 | 0 | CALLAHAN |  | CREZ Modified |  |  |  |  | Y
11TPIT0102 | Waples to Hood Conversion | Convert existing Waples to Hood line to 138 kV operation | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-05-03 | 2011-05-31 | 138 | 0 | 7.25 | 0 | 0 | HOOD | HOOD | Tier 4 |  |  |  | 466, 373, 455, 451, 364 | Y
11TPIT0135 | Navo Capacitor Bank | Install additional 75 MVAR at Navo sub | [5 empty] | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-04-15 | 2011-05-31 | 138 | 0 | 0 | 0 | 75 | DENTON |  | Tier 4 |  |  |  | 662 | Y
11TPIT0039 | Dresden to LA Heights - 138kV line upgrade | Upgrade the existing Dresden to LA Heights 138kV transmission line |  |  |  |  | S-0308 | CPS | PM: Bruce Raney | T-0156 | 2011-06-01 | 2011-05-31 | 138 | 0 | 3.29 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5130 5285 5286 | Y |  |  | There are no transformers associated with this project
10TPIT0115 | Gibbons Creek Substation Upgrade Project | Install new control houses for both 138kV and 345kV systems. Upgrade all relays and SCADA devices and install new cabling for yard equipment. Install high-side load-break switches for autotransformers 1 and 2. | Revised due to coordination with generation plant outage schedule |  |  |  |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T09002 | 2011-05-01 | 2011-05-31 | 345 | 0 | 0 | 0 | 0 | GRIMES | GRIMES | Tier 4 |  |  |  |  | N
11TPIT0044 | Highway 9 to Valero West 69 kV transmission line upgrades | Upgrade the Upriver to Highway 9 69 kV Loop and add transformation to remove contingency overloads during off-peak maintenance | IN-SERVICE | Highway 9 | Upriver | Under Construction | 399 - 0644 | AEP/ETT/TCC | Michael Glueck 918-599-2653 | 3280 | 2011-06-30 | 2011-06-01 | 69 | 0 | 3.96 | 0 | 0 | NUECES | NUECES | Tier 1 | 2009-03-18 | 2009-10-09 | 2009-12-01 |  | Y | N
11TPIT0035 | McCree 69 kV, install 18.0 MVAR Cap Bank | Install 18 MVAR capacitor bank to support local low voltage problems | [5 empty] | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2011-06-01 | 2011-06-01 | 69 | 0 | 0 | 0 | 18 | DALLAS |  | Tier 4 |  |  |  | 832 | Y
11TPIT0075 | Kirby to Tuttle - 138 kV Circuit | Construct a 138 kV circuit between Kirby and Tuttle using existing ROW and install new substation terminal equipment | [5 empty] | CPS | PM: Bruce Raney | T-0206 | 2011-10-01 | 2011-06-01 | 138 | 6.475 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5250 5435 | Y |  |  | There are no transformers associated with this project
09TPIT0130 | Newman 138 kV, install 24.0 MVAR Cap Bank | Install 24 MVAR capacitor bank to support local low voltage problems | [5 empty] | GARLAND | Danh Huynh, 972-205-3826,Dhuynh@garlandpower-light.org |  | 2011-05-02 | 2011-06-01 | 138 | 0 | 0 | 0 | 24 | DALLAS |  | Tier 4 |  |  |  | 849 | Y
11TPIT0080 | Killeen Switch - Killeen South - Killeen Fort Hood West Tap 138 kV line | Upgrade existing 138 kV line |  | Killeen Switch | Killeen Fort Hood West Tap | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R741-E | 2011-06-01 | 2011-06-01 | 138 | 0 | 7 | 0 | 0 | BELL | BELL | Tier 4 |  |  |  | 3423, 3428 | Y | N | 2009-R32
11TPIT0122 | Cedar Hill Switch 138 kV terminal equipment | Upgrade 138 kV terminal equipment used to connect the 345/138 kV autotransformer |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4083B-WAC | 2011-06-01 | 2011-06-01 | 138 | 0 | 0 | 0 | 0 | DALLAS |  | Tier 4 |  |  |  | 2421, 2422 | Y | N
11TPIT0145 | Goldsmith Tap - Goldsmith 138 kV Line | Rebuild existing 69 kV line as a double-circuit line with a 138 kV circuit and a 69 kV circuit and convert Goldsmith Substation to 138 kV. |  | Goldsmith Tap | Goldsmith | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8021-WAC | 2011-06-01 | 2011-06-01 | 138 | 3.3 | 3.3 | 0 | 0 | ECTOR | ECTOR | Tier 4 |  |  |  | 11256, 11250, 1141, 1145 | Y | N
05TPIT0068 | Marshall Ford-Buttercup | Upgrade the 9.8-mile Marshall Ford(7356)-Buttercup(7531) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). | Complete 6/1/11 |  |  |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2011-06-01 | 2011-06-01 | 138 | 0 | 9.8 | 0 | 0 | TRAVIS | WILLIAMSON | Tier 4 |  |  |  | SEE PROJECT DESCRIPTION | Y
11TPIT0172 | PH Robinson - Center Ckt. 97 | Upgrade substation equipment to increase thermal ratings. | [5 empty] | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 0 | 0 | HARRIS | HARRIS | Tier 4 |  |  |  | 42000, 40240 | Y
11TPIT0067 | Tonkawa Switch | Expand existing switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C859-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 0 | -100 | MITCHELL |  | CREZ |  |  |  | 11048 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0068 | Tonkawa - Sweetwater East 345 kV line | Construct double-circuit 345 kV line |  | Tonkawa | Sweetwater East | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1007-E | 2011-06-01 | 2011-06-01 | 345 | 63.4 | 0 | 0 | 0 | MITCHELL | NOLAN | CREZ |  |  |  | 11048, 11420 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0040 | Scurry County South Switch (Central A) | Construct 345 kV switching station with 345/138 kV autotransformers and shunt reactor |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1004-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 1200 | -150 | SCURRY |  | CREZ |  |  |  | 11318 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0041 | Dermott Switch (Central B) | Construct 345 kV switching station with 345/138 kV autotransformers and shunt reactor |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1003-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 1200 | -150 | SCURRY |  | CREZ |  |  |  | 11305 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
12TPIT0042 | Scurry County South Switch (Central A) - Tonkawa 345 kV line | Construct double-circuit 345 kV line |  | Scurry County South | Tonkawa | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C1008-E | 2011-06-01 | 2011-06-01 | 345 | 30.4 | 0 | 0 | 0 | SCURRY | MITCHELL | CREZ |  |  |  | 11318, 11048 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0069 | Sweetwater East Switch | Construct 345 kV switching station |  |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | C858-E | 2011-06-01 | 2011-06-01 | 345 | 0 | 0 | 0 | -100 | NOLAN |  | CREZ |  |  |  | 11420 | Y | N |  | Project schedule details can be found in PUCT CREZ Oversight Monitor Report.
11TPIT0118 | Cheapside - New Substation | Construct a new 138-13.09KV, 20 MVA x two, redundant backup substation |  | Cheapside | Cuero/Gonzales | Planned |  | GVEC | Rene A. Hernandez rhernandez@gvec.org Barry Kremling bkremling@GVEC.org 830-857-1200 |  | 2011-06-03 | 2011-06-03 | 138 | 0 | 0 | 0 | 0 | GONZALES |  | Tier 4 |  |  |  | See Project Title | Y | N
08TPIT0080 | Abilene South to Tuscola, Rebuild 69 kV line | Re-Build Portions of the Ballinger to Abilene South 69 kV line with 795 ACSR | IN-SERVICE | Abilene South | Tuscola | Under Construction | 499 - 0704 | AEP/ETT | Teresa Trotman 918-599-2653 | 2455 | 2011-06-06 | 2011-06-06 | 69 | 0 | 11.4 | 0 | 0 | TAYLOR | TAYLOR | Tier 1 | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y | N
11TPIT0139 | DUNCAN 138kV Substation | Serve DUNCAN substation by looping into Ckt.86 BENDER - BARHIL. | IN-SERVICE | DUNCAN | BENDER/ BARHIL |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-06 | 138 | 0.3 | 0 | 0 | 0 | CHAMBERS | CHAMBERS | Tier 4 |  |  |  | 40360, 40150, 40155 | Y | N |  | No autotransformer capacity to be added.
10TPIT0087 | Putnam to Leon, Convert 69 kV line to 138 kV | Build new 138 kV circuit from E. Abilene to Leon with 795 ACSS as alternative to CREZ project of upgrading Abilene S. to Leon 138 kV line | IN-SERVICE | Putnam | Leon | Under Construction | 466 - 0666 | AEP/ETT/ONCOR | Larry Roberson 918-599-2653 | 2347 | 2011-06-30 | 2011-06-07 | 138 | 0 | 17.38 | 0 | 0 | NUECES | EASTLAND | CREZ Modified | 2008-06-20 | 2009-03-19 | 2009-08-06 |  | Y | Y
11TPIT0146 | Big Brown 345 kV terminal equipment | Upgrade terminal equipment on line to Venus | Construction taking more time than expected |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R752-WAC | 2011-06-01 | 2011-06-08 | 345 | 0 | 0 | 0 | 0 | FREESTONE | FREESTONE | Tier 4 |  |  |  | 3380, 1906 | Y | N
10TPIT0065 | Dansby Substation | Install (1) Breaker in existing ring bus for a 138 lines to Thompson Creek Substation |  | Dansby | Dansby | completed | 05TPIT0172 11TIPIT0030 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2011-06-11 | 2011-06-11 | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | Tier 4 |  |  |  | 32897 | Y | N
11TPIT0030 | Thompson Creek Substation | Install (3) Breaker ring to include (1) 138 lines, and (1) 138/12.5 transformer |  | Thompson Creek | Thompson Creek | completed | 05TPIT0172 10TIPIT0065 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com |  | 2011-06-11 | 2011-06-11 | 138 | 0 | 0 | 14 | 0 | BRAZOS |  | Tier 4 |  |  |  |  | Y | N
11TPIT0125 | Teasley Substation - Add 28 MVA Transformer | Install an additional 138kV circuit breaker and a new 28 MVA tranformer in the existing Teasley Substation to accommodate additional load growth | On schedule |  |  | Complete | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602766 | 2011-06-11 | 2011-06-11 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON | Tier 4 |  |  | NA | 918 | Y | N
05TPIT0172 | Thompson Creek to Dansby 138, New line construction | Build a 1033 ACSR 138 kV line |  | Thompson Creek | Dansby | completed | 10TPIT0065 11TPIT0030 | BTU | James Tanneberger, 979-821-5763, jtanneberger@btutilities.com Shawndra Green, 979-821-5744, sgreen@btutilities.com | 802 | 2011-06-20 | 2011-06-20 | 138 | 10.2 | 0 | 0 | 0 | BRAZOS | BRAZOS | Tier 4 |  |  |  | 32897, 32863 | Y | N
11TPIT0147 | Venus 345 kV terminal equipment | Upgrade terminal equipment on line to Big Brown | Construction taking more time than expected |  |  | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3103-WAC & M3103B-WAC | 2011-06-01 | 2011-06-20 | 345 | 0 | 0 | 0 | 0 | ELLIS | ELLIS | Tier 4 |  |  |  | 3380, 1906 | Y | N
12TPIT0066 | Laguna Vista 138 kV tap lines | Construct 138 kV tap lines to convert Laguna Vista Substation to 138 kV service. | Construction taking more time than expected | East Tap and West Tap | Laguna Vista | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R587-WAC | 2011-06-01 | 2011-06-23 | 138 | 10.4 | 10.4 | 0 | 0 | PARKER | PARKER | Tier 4 |  |  |  | 528, 1590, 529 | Y | N
11TPIT0120 | Pegasus 138 kV Tap and Point of Interconnection | Convert the tap line to Pegasus and South Pegasus substations to 138 kV and connect to the Odesaa - Crane 138 kV line (Oncor portion) | Construction taking more time than expected | Pleasant Farms | Pagasus and South Pegasus | Completed |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R8010-WAC | 2011-06-01 | 2011-06-23 | 138 | 0 | 11.4 | 0 | 0 | ECTOR | MIDLAND | Tier 4 |  |  |  | 1235, 1234 | Y | N | 2009-R2
11TPIT0074a | Galveston Area 138kV Circuit Upgrades Phase Two | Upgrade 138 kV Ckt. 63 Webster to Stewart to increase thermal ratings. | IN-SERVICE | Webster | Stewart |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-30 | 138 | 0 | 21.85 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 43507, 42861, 43290 | Y | N |  | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan. Construction included in cancelled project 11TPIT0071 is now included in 11TPIT0074.
11TPIT0074b | Galveston Area 138kV Circuit Upgrades Phase Two | Upgrade 138kV Ckt. 93 Alta Loma to Hitchcock to West Galveston to increase thermal ratings. | IN-SERVICE | Alta Loma | West Galveston |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-30 | 138 | 0 | 15.7 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 42061, 42800, 43400 | Y | N | See project 11TPIT0074a for total project cost estimate | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan. Construction included in cancelled project 11TPIT0071 is now included in 11TPIT0074.
11TPIT0074c | Galveston Area 138kV Circuit Upgrades Phase Two | Upgrade 138 kV Ckt. 01 Webster to Tiki Island to Galveston to increase thermal ratings. | IN-SERVICE | Webster | Galveston |  |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2011-06-30 | 2011-06-30 | 138 | 0 | 26.38 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 43500, 42862, 43355, 42670 | Y | N | See project 11TPIT0074a for total project cost estimate | No transformer capacity to be added. Project is part of the 2009 ERCOT 5-Year Plan. Construction included in cancelled project 11TPIT0071 is now included in 11TPIT0074.
07TPIT0026 | Booneville to Hearne Southwest Rebuild | Rebuild existing Booneville - Hearne Southwest with 795 | row issues | Booneville | Hearne Southwest | under construction |  | BRAZOS | Brion Ryan, 254-750-6353, bryan@brazoselectric.com |  | 2011-09-20 | 2011-07-07 | 69 | 0 | 22.2 | 0 | 0 | ROBERTSON | BRAZOS | Tier 4 |  |  |  | 38, 32870 | Y | N |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0086 | Circuit 978 (Seaholm to Warren) Reconductor | Reconductor the last span of the Ckt 978 (Seaholm to Warren) going into Warren substation with bundled 795 ACSR Drake conductor. | COMPLETE | Seaholm Substation | Warren Substation | Planned |  | AUSTIN ENERGY | Ken Chui (512) 322-6745 Ken.chui@austinenergy.com | PLAN_117_P086 | 2011-08-01 | 2011-08-01 | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS | Tier 4 |  |  |  | 9132, 9286 | Y | N
11TPIT0142 | Illinois #4 to Comstock, Rebuild 69 kV as 138 kV, energize at 69 kV | Rebuild 69 kV line from Ft. Lancaster to Hamilton Rd. with 795 ACSS, double circuit capable as alternative to CREZ project of rebuilding Sonora to Hamilton 138 kV line | IN-SERVICE | Illinois #4 | Comstock | Under Construction | 474 - 0676 | AEP/ETT | Larry Roberson 918-599-2653 | 2438 | 2011-08-02 | 2011-08-02 | 69 | 0 | 63.6 | 0 | 0 | CROCKETT | VALVERDE | CREZ Modified |  |  |  |  | Y | Y

## CancelledTPIT09012011NoCost
SEPTEMBER BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) CANCELLED PROJECTS As Of 09/01/2011
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) (Optional) | Terminal "from" Location | Terminal "to" Location | Transmission Status "under construction, planned or conceptual" | Associated Projects (project number) (Optional) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) (only in completed tab) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Autotransformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | County Location for Substation or Starting Point for a Line | County Location of Ending Point for a Line (Optional for Substation projects) | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Part of Interface (Y/N) | Requested Additional Information (Optional) | Other (Optional)
11TPIT0083 | Glen Rose Hills Substation | This project will build a new 138 kV / 12.47 kV substation near Glen Rose Hills subdivision north of Glen Rose |  | Glen Rose Hills | DeCordova | Planned |  | TNMP | Allen Aars, 972-420-4189,Allen.Aars@tnmp.com | NTE02110 | 2012-10-31 |  | 138 | 0 | 0 | 0 | 0 | SOMERVELL |  | Tier 4 |  |  |  | 37705 | Y | N
14TPIT0006 | Mainland-New Substation | This project is to build a new distribution substation to serve the Mainland area for alleviating future loading from Lamarque, TX |  | Freeway Park | Alvin | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE03814 | 2016-05-31 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON |  | Tier 4 |  |  |  | 39040 | Y | N
15TPIT0016 | Rebuild Friendswood-Seminole | This project will rebuild Friendswood to Seminole 138kV transmission line with 795 ACSS wire |  | Freindswood | Seminole | Planned |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | STE08213 | 2015-05-30 |  | 138 | 0 | 2.9 | 0 | 0 | GALVESTON | GALVESTON | Tier 4 |  |  |  | 38980, 39010 | Y | N
16TPIT0008 | Hunt Lane to Pinn Rd. - 138 kV Transmission Line Rebuild | Rebuild 8 circuit miles of 138 kV transmission line from Hunt Lane to Medina and ensure a minimum conductor rating of 578 MVA | This project does not have an effect on the overall ratings of the transmission line |  |  |  |  | CPS | Blake Williams | T-0190 | 2016-12-01 |  | 138 | 0 | 8 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5234 5305 5345 | Y | No |  | There are no transformers associated with this project
13TPIT0097 | Howard to Somerst - 138 kV Substation Equipment Upgrade | Replace Line and Bus Switches at Somerset, change CT settings on both terminals and ensure a 1210 A rating and remove the existing MLSE on the Howard to Somerset 138kV transmission line | This project does not have an effect on the overall ratings of the transmission line |  |  |  |  | CPS | Blake Williams | S-0663 | 2013-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR | Tier 4 |  |  |  | 5230 5390 | Y | No |  | There are no transformers associated with this project
13TPIT0006 | N. Edinburg to Del Sol: Construct 345 kV Line | Construct 345 kV line from Lobo to Rio Bravo to Del Sol to N Edinburg | CANCELLED | North Edinburg | Del Sol | Planned | 065 - 0273 | AEP/ETT/TCC | Paul Hassink 918-599-2653 | 3064 | 2016-10-31 |  | 345 | 15 | 0 | 0 | 0 | HIDALGO | HIDALGO | Tier 1 | 2011-03-10 | On-going |  | 8383, 80355 | N | N |  | DEL SOL - NORTH EDINBURG COMBINED WITH 11TPIT0002
14TPIT0036 | Dynamic Reactive Additions | Install additional dynamic reactive devices to the CNP transmission system at Addicks and Zenith 138 kV | CANCELLED |  |  | Planned |  | CNP | Wayne E. Kemper wayne.kemper@ CenterPoint Energy.com 713 207 2192 |  | 2014-05-31 |  | 138 | 0 | 0 | 0 | 1036 | HARRIS | HARRIS | Tier 1 | 2011-02-08 | On-going |  | 45610, 44910 | N | N

## TPIT5YearPlanProjects
Project Number | Project Name | Proposed in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2010-R1 | El Campo 138/69 kV autotransformer addition | 2013 |  |  |  | Planning Stage
2010-R2 | Victoria – North Victoria 69 kV line upgrade | 2011 |  | 08TPIT0092 |  | In RPG Process
2010-R3 | Texas City Water Treatment Sub – Intercity – LaMarque 69 kV line upgrade | 2011 |  |  |  | Canceled
2010-R5 | Dialville 138/69 kV autotransformer upgrade | 2015 | Planning Stage |  |  | Design Stage
2010-R6 | Troup Switching Station – Walnut Grove POI 138 kV line upgrade | 2013 | Planning Stage | 14TPIT0015 |  | CCN
2010-R7 | Odessa Area 69 kV line upgrades | 2011 | Planning Stage |  |  | In Service
2010-R8 | Odessa Area 138 kV line upgrades | 2011 | Planning Stage
2010-R9 | Pegasus – South Pegasus Tap 138 kV line conversion | 2011 | In Service | 11TPIT0120
2010-R10 | Midland East – Windwood 138 kV line upgrade | 2011 | Planning Stage | 14TPIT0011
2010-R11 | Worsham – Lone Star Tap and Winkler County-6 – Poyote terminal equipment upgrades | 2012
2010-R12 | Denton Area 138 kV line upgrades | 2011
2010-R13 | Forney – Forney West 138 kV line upgrade | 2012 | Planning Stage
2010-R14 & 2010-E4 | Seagoville – Kleberg Tap 138 kV line upgrade | 2014 | Planning Stage |  | This project was identified as Reliability project in 2015 and the economic analysis justified the need for this project earlier in 2014.
2010-R15 | Oran 138/69 kV autotransformer addition | 2012 | Planning Stage
2010-R16 | Hicks 138 kV project | 2014 | Planning Stage
2010-R17 | Kosse Switch – Petteway 69 kV line upgrade | 2013
2010-R18 | Rockwall – Garland 138 kV line – Second Dalrock bus creation | 2015 | Planning Stage
2010-R19 | Parkdale – East Network 138 kV line upgrade | 2014 | Planning Stage
2010-R20 | Apollo – East Richardson 138 kV line upgrade | 2011 | Planning Stage | 09TPIT0044 10TPIT0013
2010-R21 | Lewisville 345/138 kV autotransformer addition | 2012 |  | 07TPIT0042
2010-R22 | Collin 345/138 kV autotransformer addition | 2014 | Planning Stage | 09TPIT0042
2010-R23 | Northaven – Welch Road 138 kV double circuit upgrade | 2011 | Planning Stage
2010-R24 | Jack County Substation 345/138 kV autotransformer addition | 2015
2010-R25a | Lon Hill – Robstown 69 kV line upgrade | 2012
2010-R25b | Robstown - City of Robstown 69 kV line terminal equipment upgrade | 2014
2010-R26 | Lon Hill – Calallen Substation 69 kV line upgrade | 2014
2010-R27 | Upgrade of both Lon Hill 138/69 kV autotransformers | 2014
2010-R28 | Laguna – Naval Base 69 kV line upgrade | 2013
2010-R29 | Orange Grove Switchyard – Orange Grove Distribution Substation 69 kV line upgrade | 2012 | In Service | 14TPIT0019
2010-R30 | Peters – Racoon – Hockley 69 kV line conversion to 138 kV service | 2013 | In Service | 11TPIT0112
2010-R31 | Masterson Road project | 2015 |  | 12TPIT0009
2010-R32 | Ennis Creek 138/69 kV autotransformer upgrade | 2012
2010-R33 | San Angelo Concho 138/69 kV autotransformer upgrade | 2011
2010-R34 | Leakey – Campwood 69 kV line terminal equipment upgrade | 2011
2010-R35 | Morgan Creek 138/69 kV autotransformer upgrade | 2012
2010-R36 | Morgan Creek – Colorado City 69 kV line terminal equipment upgrade | 2013 | Design Stage | 11TPIT0153
2010-R37 | General Motors – Great Southwest #1 circuit upgrade | 2011 | Design Stage | 06TPIT0043
2010-R38 | Handley – Hurst 138 kV line upgrade | 2011 | Design Stage | 07TPIT0017
2010-R39 | Mountain Creek – Norwood 138 kV line upgrade | 2012 | Planning Stage | 14TPIT0012
2010-R40 | Roanoke Switch – Southlake 138 kV line upgrade | 2011 | Design Stage | 12TPIT0079
2010-R41 | Norwood – East Levee 138 kV line upgrade | 2012 | Planning Stage | 14TPIT0013
2010-R42 | Randol Mill – Hemphill 138 kV line terminal equipment upgrade | 2012 | In Service | 11TPIT0149
2010-R44 | Bonham Switch 69 kV capacitor | 2012 | Planning Stage | 12TPIT0018
2010-R45 | Holliday 69 kV capacitor | 2012 | Planning Stage |  | Capacitors are being installed at Seymour instead of Holliday.
2010-R51 | Relocation of load to Granbury 138 kV substation | 2015
2010-R52 | Albany 69 kV capacitor | 2015
2010-E1 | North Brazoria County 138 kV line upgrades | 2011 |  | 13TPIT0079 15TPIT0015
2010-E2a | Tyler Bullard Rd – Elkton 138 kV line terminal equipment upgrade | 2011 | In Service | 09TPIT0170
2010-E2b | Tyler Loop South Tap – Tyler Bullard Rd – Elkton 138 kV line upgrade | 2012 | Planning Stage
2010-E3 | South Lane City – Pledger – West Columbia 138 kV line upgrade | 2012 | Design Stage | 12TPIT0095
2010-E7 | Third Cagnon 345/138 kV autotransformer addition | 2012 |  | 11TPIT0026

## TransmissionOwnerProjContacts
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Bob Healey | bhealey@aep.com | Bob Healey: 918 599 2249 | Glen Reed; David Kidd; Brad Myers; Sugam Patel; Mabel See; Mike Forcum | gareed@aep.com; dekidd@aep.com; rlbentz@aep.com; naward@aep.com; smdsouza@aep.com; camatthes@aep.com; blmyers@aep.com; sgpatel@aep.com; pcbelkin@aep.com ; msee@aep.com; mlforcum@aep.com | David Kidd: 918 599 2637 Glen Reed: 918 599 2664 Brad Myers: 918 599 2690
AUSTIN ENERGY | Primary & Secondary | Ken Chui | ken.chui@austinenergy.com; | Ken: 512 322 6745 | Armke, James; Mathew, Biju; Ebrahimian, Reza; Hunt, Dandy | James.Armke@austinenergy.com; biju.mathew@austinenergy.com; reza.ebrahimian@austinenergy.com; dandy.hunt@austinenergy.com; | James: 512 322 6705 Biju: 512 322 6381 Reza: 512 322 6740 Dandy: 512 322 6748
Bandera Electric | Primary | David Baker | d.baker@banderaelectric.com | David: 830-796-6084 | Brian Bartos | b.bartos@banderaelectric.com | Brian: 830 796 6074
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Brion Ryan | bryan@brazoselectric.com | Brion: 254 750 6353 | David Albers; Dwight Beckman | dalbers@brazoselectric.com; dbeckman@brazoselectric.com | David: 254 750 6358 Dwight: 254 750 6373
BPUB | Primary | Ramon Sanz | rsanz@brownsville-pub.com; | Ramon: 956 983 6203 | James McCann | jmccann@brownsville-pub.com; | James: 956 983 6204
BTU | Primary & Secondary | James Tanneberger | jtanneberger@btutilities.com | James: 979 821 5763 | Shawndra Green | sgreen@btutilities.com | Shawndra: 979 821 5744
CNP | Primary & Secondary | Wayne Kemper | wayne.kemper@centerpointenergy.com | Wayne: 713 207 2192 | Wesley Woitt; Hanson John; Cody Mann; Karolyn Skalany | wesley.woitt@centerpointenergy.com; john.hanson@centerpointenergy.com; cody.mann@centerpointenergy.com; karolyn.skalany@centerpointenergy.com | Wesley Woitt: 713-207-2760 John Hanson: 713-207-2754 Cody Mann: 713-207-3149 Karolyn Skalany: 713-207-3614
COCS | Primary | Tony Michalsky | tmichalsky@cstx.gov; | Tony: 979 764 3438 | Timothy Crabb; David Massey; David Roye | dmassey@cstx.gov; droye@cstx.gov; | Timothy 979 764 3439 David 979 764 3493 David R 979 764 5021
CPS | Primary & Secondary | Basileo Rocha, Mario De La Garza | bdrocha@cpsenergy.com; MADelagarza1@CPSEnergy.com | Basileo: 210 353 4933 | Kenneth Bowen Blake Williams | kbowen@cpsenergy.com; bawilliams@cpsenergy.com; | Kenneth: 210 353 4142 Blake: 210 353 3557
CTT (Cross Texas Transmission) | Primary & Secondary | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310 | Tim Cook | Tcook@LSPower.com | Tim 636 534 3310
DENTON | Primary & Secondary | Chuck Sears | Chuck.Sears@cityofdenton.com; | Chuck: 940 349 7111 | Brent Heath | brent.heath@cityofdenton.com; | Brent: 940 349 7180
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@garlandpower-light.org | Danh: 972 205 3826 | Grubbs, David; Fred Sherman; Steve Zaragoza | Dgrubbs@garlandpower-light.org; FredS@gplops.org; stevez@gplops.org | David: 972 205 2664 Fred: 972 205 3184 Steve: 972-205-3098
Golden Spread EC | Primary & Secondary | Mark Reinart | mreinart@gsec.coop | Mark: 806 349 6562 | Shane McMinn, Chris Koenig | smcminn@gsec.coop; ckoenig@gsec.coop | Shane: 806 379 7766 Chris: 806 349 5201
LCRA TSC; PEC; SBEC; GVEC; City of Georgetown; BBEC,CTEC, NBU | Primary & Secondary | Brad Woods | brad.woods@lcra.org | Brad: 512 369 4104 | Sergio Garza, Christina Doerr, Shirley Mathew | sergio.garza@lcra.org; christina.doerr@lcra.org; smathew@lcra.org | Sergio: 512 369 4149 Christina: 512 369 4514 Shirley: 512 369 4510
Lone Star | Primary & Secondary | Julius Horvath | julius.horvath@lonestar-transmission.com | Julius: 512-236-3135 | JC Culberson | Jc.Culberson@lonestar-transmission.com | JC: 512 236 3144
ONCOR | Primary & Secondary | Mike Juricek | Michael.Juricek@oncor.com; | Mike: 214 743 6671 | Jim Painter | jpainte1@oncor.com | Jim: 214 743 6672
Sharyland Utilities | Primary & Secondary | Mark Caskey | mcaskey@sharylandutilities.com | Mark: 214 978 8243 | Michael Glass, Dwight Yarbrough | mglass@sharylandutilities.com; dyarbrough@sharylandutilities.com | Michael: 956 687 5600, Dwight: 956 687 5600
STEC | Primary & Secondary | Doug Evans | devans@stec.org | Doug: 361 485 6459 | Cory Allen Loretta Gallaga | cory@stec.org; lgallaga@stec.org; | Cory: 866 225 5683 X2531 Loretta: 956 514 1289
TMPA | Primary & Secondary | Eric Schroeder | eschroeder@texasmpa.org; | Eric: 936 873 1124 | Frank Owens | fowens@texasmpa.org; | Frank: 936 873 1120
TNMP | Primary & Secondary | Mohammed Uddin | Mohammad.Uddin@tnmp.com; | Mohammad: 409 948 8451 x232 | Aars, Alton; McDaniel, Rex | Rex.McDaniel@tnmp.com; Alton.Aars@tnmp.com; | Rex:409 948 8451 X238 Alton:972 420 4189
Wind Energy Texas Transmission (WETT) | Primary | Paul Steckley | Paul.Steckley@BrookfieldPower.com | Paul 508 251 7690 | Christina Eckhoff | christina.eckhoff@windenergyoftexas.com | Christina: Christina: 512 279 7371